## Slide 1
ERCOT VRT Study, Phase I
ERCOT ROS Meeting December 10, 2009
Notes: <number>
Suggestion for an animated intro slide – likely to be branding dependant?
Est Cost – say £500?
1.

## Slide 2: Agenda
Phase I Objectives/Deliverables
Phase I
  Study Case Overview
    High Wind High Load (HWHL)
    High Wind Low Load (HWLL)
  Identification of Dynamic Events
    Normal Clearing Events
    Breaker Failure Events
  Dynamic Simulation & Results
    Reliability Metrics
    Normal Clearing Results
    Breaker Failure Results
  Key Observations & Findings
  Key aspects for Phase III
Notes: <number>

## Slide 3: Phase I – Objectives & Deliverables
Objectives
  Perform dynamic simulations on models & dynamic data set provided by ERCOT
  Assess impact of lack of WGR VRT capability on reliability of ERCOT system
Deliverables
    Acceptable wind flat start for HWHL & HWLL in PSS/E Version 30
    Steady state and dynamic data set for both flat starts
    Phase I report documenting
      Methodology for developing wind flat start
      Dynamic simulation process methodology
      Discussion of results associated with dynamic simulations
      Conclusions & Recommendations
Notes: <number>

## Slide 4: ERCOT VRT Study - Phase I
Study Case Overview
  HWHL Case
    58,000 MW of ERCOT System load
    4,800 MW of Wind output for West Texas
    N-1 Secure Dispatch
  HWLL Case
    36,000 MW of ERCOT System load
    4,300 MW of Wind output for West Texas
    N-1 Secure Dispatch
Notes: <number>

## Slide 5: ERCOT VRT Study - Phase I
Definition of Dynamic Events – Steady State Screening Approach
Notes: <number>

## Slide 6: ERCOT VRT Study - Phase I
Voltage Protection Boundaries w/o VRT Capability
Notes: <number>

## Slide 7: ERCOT VRT Study - Phase I
Dynamic Simulation & Results
  Quantities to be monitored
    Electrical Power output and Rotor angles of non-wind generation units
    Voltages at 345kV stations in West Region
    Electrical Power output & Terminal Voltage for all WGRs
    Voltage at all wind farm POI locations or equivalent transmission system locations
    Frequency at 4 representative buses spanning 4 ERCOT zones
Notes: <number>

## Slide 8: ERCOT VRT Study - Phase I
Dynamic Simulation & Results
  Normal Clearing Events
    Fault Clearing Time depends on numerous factors
      Voltage level associated with fault location
      Breaker operation times
      Line associated with clearing the fault
      Relay pick-up time and co-ordination issues
    Based on discussion with ERCOT, 2 fault durations utilized for normal clearing events for Phase I
      6 cycle fault duration
      4 cycle fault duration
Notes: <number>

## Slide 9: ERCOT VRT Study - Phase I
Dynamic Simulation & Results
  Reliability Metrics
    Amount of wind generation (MW) tripped for each dynamic event based on the study case (HWHL/HWLL) generation dispatch vis-à-vis ERCOT responsive reserve level (2300 MW)
    Amount of wind generation (MW) tripped for each dynamic event based on WGR capacity vis-à-vis ERCOT responsive reserve level (2300 MW)
    Amount of wind generation (MW) tripped for each dynamic event based on the study case (HWHL/HWLL) generation dispatch and WGR capacity vis-à-vis ERCOT responsive reserve level not inclusive of LAAR in conjunction with frequency deviations
    System voltage recovery and post-event voltage levels

## Slide 10
Dynamic Simulation Results – HWHL Case, 6 & 4 cycle fault duration
Notes: <number>

## Slide 11
Dynamic Simulation Results – HWHL Case, 6 & 4 cycle fault duration (contd)
Notes: <number>

## Slide 12
Dynamic Simulation Results – HWLL Case, 6 & 4 cycle fault duration
Notes: <number>

## Slide 13
Dynamic Simulation Results – HWLL Case, 6 & 4 cycle fault duration
Notes: <number>

## Slide 14
Dynamic Simulation Results – Breaker Failure events, HWHL & HWLL Cases
Notes: <number>

## Slide 15: ERCOT VRT Study - Phase I
Additional Investigation
  Identify wind farms comprising the clusters identified as “major contributors”
  Identify the updated VRT capability information as submitted by each WGR as part of Phase II data collection process
  Incorporate the updated VRT capability information as obtained via VRT Data Request Forms
    VRT Capability incorporated in the form of altered relay settings in the WGR dynamic model
    No other changes to the model
Notes: <number>

## Slide 16: ERCOT VRT Study - Phase I
Results for critical dynamic events for HWHL study case with and without WGR VRT Capability Information as collected in Phase II
Notes: <number>

## Slide 17: ERCOT VRT Study - Phase I
Key Observations/Inferences
  Dynamic events resulting in potential reliability impacts to ERCOT grid due to lack of WGR VRT capability identified & ranked
    MW trip based on study case dispatch vis-à-vis ERCOT RRS Levels (2300 MW)
    MW trip based on WGR capacity vis-à-vis ERCOT RRS Levels (2300 MW)
    Frequency excursions with potential to initiate LAAR action
    Voltage recovery or unacceptable post-event voltage levels
Notes: <number>

## Slide 18: ERCOT VRT Study - Phase I
Key Observations/Inferences
  Potential impacts of lack of WGR VRT capability (as obtained from ERCOT) for Phase I
    Potential depletion of ERCOT RRS for dynamic events at certain 345kV stations in West under high wind conditions
    Dynamic events associated with CTG#9 & CTG#30 in ERCOT West region present an especially exaggerated reliability risk
      Total wind generation trips as per study case dispatch exceed ERCOT RRS levels
      Frequency deviations close to or beyond 0.3 Hz
      Accompanying frequency excursions seem indicative of initiation of LAAR action
      Exacerbated emergency notification from ERCOT Operations stand-point
Notes: <number>

## Slide 19: ERCOT VRT Study - Phase I
Key Observations/Inferences
  Incorporation of updated VRT capability information for select WGRs significantly alleviates reliability risk
  Other factors deemed to have a positive impact on over-all ERCOT system reliability from VRT standpoint
    Incorporation of VRT capability for the remaining WGRs as collected during the Phase II process
    Incorporation of appropriate collector system equivalent associated with each WGR
    Incorporation of the dynamic/static reactive response capabilities associated with each WGR campus
Notes: <number>

## Slide 20: ERCOT VRT Study - Phase I
Key Observations/Inferences
  Optimistic results in terms of Voltage Recovery
    Lack of dynamic load model representation in ERCOT load conversion file
      AC compressor motor loads
        Stall at low voltages experienced during fault conditions
        Draw 6-7 times more current from the system resulting in elevated reactive power consumption
        Fault Induced Delayed Voltage Recovery (FIDVR)
Notes: <number>

## Slide 21: ERCOT VRT Study - Phase I
Key Observations/Inferences
  Cap Bank trips to be aligned with WGR machine trips
    Provide clear picture on any over-voltage issues
    Ascertain WGR operational philosophy with regards to external cap banks
    Script user-defined models in Phase III
  Breaker failure events around a specific 345kV station in ERCOT West region pose reliability issues
    Total wind generation trips in terms of capacity lost close to ERCOT RRS levels
    No frequency excursion concerns from breaker failure perspective
Notes: <number>

## Slide 22: ERCOT VRT Study - Phase I
Key Aspects for Phase III
  Ascertain exact fault clearing times from TSP
    Normal Clearing Events
    Breaker Failure Events
  Update WGR VRT capability based on Phase II information
  Sensitivity around load model in additional scenarios for Phase III
  Develop and incorporate the effect of collector system impedance associated with each WGR
  Develop link b/w reliability metrics to assess impact on ERCOT system & individual WGR VRT compliance
Notes: <number>

## Slide 23: ERCOT VRT Study - Phase I
Potential Mitigation options to be explored in Phase III in case of reliability risks persisting:
  Strategic location of dynamic voltage support devices
  Under-Voltage Load Shedding (UVLS) Schemes
  Wind turbine retrofitting to posses advanced VRT capability
  Replacement of existing breakers with high speed breakers on stations associated with dynamic events identified as critical
  Re-arrangement of certain critical stations in ERCOT West region
  Potential change to the ERCOT Responsive Reserve Obligation
Notes: <number>

## Slide 24
PB Team
Notes: <number>