## Slide 1: Wind Power Plant Dynamic Reactive Power “Hybrid” Solutions to meet ERCOT Reactive Power Capability Requirements
Presented at ERCOT ROS Meeting, December 10, 2009
Notes: <number>

## Slide 2
Presented by:
  American Superconductor - Narend Reddy
  S&C Electric – Ken Mattern
  Vestas Americas – Steven Saylors
PRR 830, Section 6.5.7.1 (1))
…”The Reactive Power requirements shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAR capable devices.”
The case for engineered wind project “hybrid” reactive power solutions using integrated STATCOM and switched caps/reactors to meet the ERCOT Protocol definition of “dynamic VAR capable devices”
Notes: <number>

## Slide 3: Hybrid Reactive Power Dynamic Solutions
The combination of Statcom augmented by switched static reactive elements of capacitors and/or reactors
  Provides fast-response, robust design that is dynamically capable integrated solutions to meet Voltage Support Services requirements
  Uses Statcom “Overload” capability to ensure VAR output is smooth and linear with voltage over reactive range needed
  Yields a Least-Cost design when compared to Full-Sized Statcoms or SVCs
These solutions have proven as acceptable over the last five years on many previous wind projects to various transmission entities
  AESO
  ISO-NE
  MISO
  BPA
Notes: <number>

## Slide 4: How WPPs can do reactive power control for VSS
Notes: <number>

## Slide 5
Example 1 - STATCOM System for Power Factor Correction and LVRT
PT
600V
600V
600V
34.5 kV
collector
system
115 kV
34.5 kV
Utility
Interconnection
Point
Power Transformer
60/90 MVA
with LTC
16MVAr STATCOM
System Rating for
Regulation
+48 MVAR/-16 MVAR
System Rating for LVRT
+84 MVAR/-48 MVAR
48MVAr STATCOM
Notes: .

## Slide 6: Example 2 – 160MW Wind Farm
Transmission Voltage
33 kV
33 kV
N.O.
Control
Control
CT
Cap Banks
Cap Banks
STATCOM
STATCOM
Reactive Power Control System
PT
Monitoring
CT
CT
Notes: <number>

## Slide 7: Wind Farm Voltage Control
Boosting Output
Bucking Output
1.00
1.01
1.02
1.03
1.04
0.96
0.97
0.98
0.99
Reference Voltage
= 1.00pu
Voltage (
pu
)
1x
2x
3x
1x
2x
3x
Deadband
Buck Droop = 2%
Boost Droop = 2%
Buck Hard Limit = 1.025pu
Boost Hard Limit = 0.975pu
Dynamic and Steady State Regulation Control
Control Setting Options
Independent boost and buck droops
Droop adjustable from 1% to 10%
Adjustable reference or target voltages
Optional dead band and D-VAR output limits
Can provide power factor control

## Slide 8: AMSC STATCOM System Installations for Wind Farms
Over 40 wind farms worldwide use AMSC D-VAR Systems (majority includes static shunt switched devices to provide dynamic support)
Control systems allow seamless integration and switching of static shunt devices
Static shunt devices also configured to address transient grid conditions to complement short term overload capability of D-VAR STATCOM.
Notes: <number>

## Slide 9: “Hybrid” STATCOM and Static Shunt Solutions Fully Accepted in:
United Kingdom
  +/-0.95 dynamic power factor (pf) at PCC with system response time of 1 second (See following chart)
Alberta (AESO)
  -0.95/0.90 pf overall with -0.985/0.95 pf “dynamic”
Ontario (IESO)
  +0.35/-0.33pu with dynamic capability
South Australia
  +/-0.93pf with 50% dynamic (STATCOM)
Notes: <number>

## Slide 10
United Kingdom – Power Factor Capability
20%
50%
100%
MW Output
Leading
(Inductive)
Lagging
(Capacitive)
MVAR
0.33x MW
Full leading
at 50% gen
Full lagging
at 20% gen
38% of leading
at 20% gen
15% of leading and
lagging at zero gen
0.33x MW
Notes: <number>

## Slide 11
Alberta Electric System Operator
Notes: <number>

## Slide 12: WPP MW, Inverter VArs and Net VArs at POI
WPP MW
INVERTER MVAr
WPP Net MVAr
Cap bank ON
Cap bank OFF

## Slide 13: DSTATCOM Windfarm Installations
±12 MVAr, 3x22 MVAC
Oregon
±6.25 MVAr, 5 x 7.5 MVAC
New Mexico
±6.25 MVAr, 1x8MVAR, 2x8MVAC
Scotland
±12 MVAr, 1x13, 3x26
New Mexico
±7.5 MVAr, 9 MVAR, 12 MVAC
Ireland

## Slide 16
Scottish Windfarm

## Slide 17: Thank you for your attention
Copyright Notice
The documents are created by Vestas Wind Systems A/S and contain copyrighted material, trademarks, and other proprietary information. All rights reserved. No part of the documents may be reproduced or copied in any form or by any means—such as graphic, electronic, or mechanical, including photocopying, taping, or information storage and retrieval systems without the prior written permission of Vestas Wind Systems A/S. The use of these documents by you, or anyone else authorized by you, is prohibited unless specifically permitted by Vestas Wind Systems A/S. You may not alter or remove any trademark, copyright or other notice from the documents. The documents are provided “as is” and Vestas Wind Systems A/S shall not have any responsibility or liability whatsoever for the results of use of the documents by you.
Notes: <number>