| PRR Number | 833 | PRR Title | Primary Frequency Response Requirement from Existing WGRs |
| --- | --- | --- | --- |
| Date |  | January 5, 2010 |  |
| Submitter’s Information |  |  |  |
| Name |  | Todd Kimbrough |  |
| E-mail Address |  | Todd.kimbrough@fpl.com |  |
| Company |  | NextEra Energy Resources |  |
| Phone Number |  | 512.466.3190 |  |
| Cell Number |  | 512.466.3190 |  |
| Market Segment |  | Independent Generator |  |

Comments

NextEra Energy Resources appreciates the time extended by TAC to work with Wind-powered Generation Resources (WGRs) vendors to assess the availability of technical solutions for the provision of Primary Frequency Response from existing WGRs.  A survey of manufacturers and technical support vendors leads NextEra to believe retrofitted automated Primary Frequency Response capability is available for some WGRs and WGR control systems but not for others.  NextEra proposes the language below to clarify the definition of “technically infeasible” consistent with our experience and research on this issue.

NextEra also acknowledges the recent comments by E.ON, which offer an alternative methodology for providing some Primary Frequency Response and believes the E.ON concept is worthy of further consideration.  NextEra surmises some combination of the language below along with the addition of E.ON’s tiered frequency response concept may provide the most complete and most cost-effective solution for the market and the most benefit to the ERCOT System.

NextEra proposes the two key pieces of this Protocol Revision Request (PRR) – technical feasibility from an automated control system perspective and tiered curtailment-based response to high frequency excursions be further explored and refined by the QSE Managers Working Group (QMWG) and Performance, Disturbance, Compliance Working Group (PDCWG), respectively.

Revised Proposed Protocol Language

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Standard Generation Interconnection Agreements (SGIAs) signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional steam generators.  For WGRs with SGIA executed on or prior to January 1, 2010, those not already equipped with Primary Frequency Response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with Primary Frequency Response capability shall submit an attestation to ERCOT by May 1, 2010 explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for which Primary Frequency Response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within one hundred eighty (180) days of receipt of the attestation.  For purposes of this Section, “technically infeasible” shall mean that a commercially available upgrade to the existing WGR control system that would enable compliance with this Section does not exist at the time that the WGR submits its one-time attestation to ERCOT pursuant to this Section.  If ERCOT does not grant  a permanent exemption, the WGR shall acquire the capability to provide Primary Frequency Response within twenty-four (24) months of being notified of that determination.