| PRR Number | 833 | PRR Title | Primary Frequency Response Requirement from Existing WGRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | January 6, 2010 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Protocol Section Requiring Revision |  | 5.9.1.3, Wind-powered Generation Resource (WGR) Primary Frequency Response (new) |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) places a Primary Frequency Response requirement on WGRs that are not covered by PRR824, Primary Frequency Response from WGRs. |  |  |
| Reason for Revision |  | To require all WGRs to provide Primary Frequency Response. |  |  |
| Overall Market Benefit |  | Possible added reliability and similar treatment for existing WGRs as that given to prospective wind farms. Maintain system frequency better with additional wind generation in the ERCOT Region, which shall allow greater utilization of wind generation. |  |  |
| Overall Market Impact |  | Greater requirements are placed on existing WGRs. |  |  |
| Consumer Impact |  | Greater reliability but also possibly greater cost. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed PRR833 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Relevance to Nodal Market |  | May require similar changes to Nodal Protocols. |  |  |
| Nodal Protocol Section Requiring Revision |  | 8.5.3, Wind-powered Generation Resource (WGR) Primary Frequency Response |  |  |
| Procedural History |  | - On 9/22/09, PRR833 was posted. - On 9/25/09, Calpine comments were posted. - On 10/12/09, Wind Coalition comments were posted. - On 10/19/09, ROS comments were posted. - On 10/22/09, PRS considered PRR833. - On 11/12/09, ERCOT comments were posted. - On 11/12/09, the CEO Revision Request Review and an Impact Analysis were posted. - On 11/19/09, PRS considered the 10/22/09 PRS Recommendation Report and Impact Analysis for PRR833. - On 12/2/09, Horizon Wind Energy LLC comments were posted. - On 12/3/09, TAC considered PRR833. - On 1/4/10, a second set of Calpine comments were posted. - On 1/5/10, E.ON comments were posted. - On 1/5/10, NextEra Energy comments were posted. - On 01/06/10, TAC again considered PRR833. |  |  |
| PRS Decision |  | On 10/22/09, PRS voted to recommend approval of PRR833 as revised by PRS via roll call vote. All Market Segments were present for the vote. On 11/19/09, voted to endorse and forward the 10/22/09 PRS Recommendation Report as amended by the 11/12/09 ERCOT comments, and the Impact Analysis to TAC. The motion passed via roll call vote. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 10/22/09, there was discussion regarding retrofitting WGRs with Primary Frequency Response capability and ERCOT’s interpretation of the retrofitting being “technically infeasible.” There was concern expressed by some Market Participants regarding the cost-benefit of PRR833. On 11/19/09, ERCOT Staff reviewed the proposed language “technically infeasible” and noted that with no clear definition, ERCOT will base their decision on whether or not a turbine is technically infeasible of meeting the Primary Frequency Response requirement by whether the turbine is capable of pitching its blades without taking into consideration the cost to do so. Some Market Participants suggested tabling the PRR to allow time to consult with vendors as to what is or is not technically infeasible while others suggested comments could be filed to TAC to add more specific language if desired. |  |  |
| TAC Decision |  | On 12/3/09, TAC voted to table PRR833 for one month to provide the wind community with the opportunity to address the definition of “technically infeasible.” There were four opposing votes from the Investor Owned Utility (IOU) (3) and Municipal Market Segments and four abstentions from the Independent Power Marketer (IPM) (3) and Cooperative Market Segments. All Market Segments were present for the vote. On 01/06/10, TAC voted to table PRR833 with instructions for WMS to review the 1/5/10 NextEra comments and ROS to review the 1/5/10 E.ON comments. There were two abstentions from the Independent Power Marketer (IPM) Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 12/3/09, there was discussion regarding the need for clarification of the proposed language “technically infeasible.” Some Market Participants stated that although some older units could respond there is still a need to determine how. It was also noted that ERCOT could base its determination regarding technical feasibility on the WGR’s attestation. ERCOT Staff noted that the guidance to develop language to clearly define “technically infeasible” would need to come from the wind community. On 01/06/10, the 1/5/10 NextEra and E.ON comments were discussed. It was suggested that additional review of E.ON comments be reviewed by the Performance, Disturbance, Compliance Working Group to assess the technical feasibility concerns from an automated control system perspective while the QSE Managers Working Group (QMWG) should review the 1/5/10 NextEra comments to review the tiered frequency response concept. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | WGRs would need to install Governor response. | Less than $500,000 per WGR. |
|  | 2 | Lost production due to high frequency. | Depends on the price of power. |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provides automatic response to frequency, primarily to high frequency excursions, in addition to the response from conventional generation units. Should help avoid excessive frequency excursions. | Difficult to quantify. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Kenan Ögelman |
| E-mail Address | kogelman@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | 512 542-7594 |
| Cell Number | 512 423-3570 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Calpine 092209 | Supported approval of PRR833. |
| Wind Coalition 101209 | Recommended rejection of PRR833. |
| ROS 101909 | Recommended approval of PRR833 as submitted. |
| ERCOT 111209 | Proposed administrative and clarifying language revisions. |
| Horizon Wind Energy LLC 120209 | Recommended rejection of PRR833. |
| Calpine 010410 | Proposed language changes to remove the contentious language surrounding what is or is not technically feasible. |
| E.ON 010510 | Proposed language changes would require all existing WGRs not already equipped to provide Primary Frequency Response to install over-frequency relays that would interrupt the WGR at set frequency levels. |
| NextEra Energy 010510 | Proposed two key pieces of PRR833, technical feasibility from an automated control system perspective and tiered curtailment-based response to high frequency excursions, be further explored and refined by the QSE Managers Working Group (QMWG) and Performance, Disturbance, Compliance Working Group (PDCWG), respectively. |

Proposed Protocol Language Revision

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Standard Generation Interconnection Agreements (SGIAs) signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional steam generators.  For WGRs with SGIA executed on or prior to January 1, 2010, those not already equipped with Primary Frequency Response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with Primary Frequency Response capability shall submit an attestation to ERCOT by May 1, 2010 explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for which Primary Frequency Response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within one hundred eighty (180) days of receipt of the attestation.  If ERCOT does not grant an exemption, the WGR shall acquire the capability to provide Primary Frequency Response within twenty-four (24) months of being notified of that determination.