## Slide 1: Why is CREZ Unique?
15 GW of intermittent generation when ERCOT load is less than 30 GW
5000 miles of 345 kV circuits with power flow swings from less than 10% to over 50%
10 GVars of reactive power imbalance swings from min to max export
9 cycle clearing to avoid tripping up to 5 GW of Panhandle wind generation
8 TSPs coordinating operationally

## Slide 2: What are the Challenges?
Until we learn to manage these extraordinary demands on the grid,
  in one year, the cost of spilled wind energy (1% of curtailment ~$20M) could pay for
  the total cost of the advanced systems (2000 miles of OPGW ~$20M) that would maximize delivered production
Without the application of Smart-grid technology such as Synchrophasor, it will not be possible to actively and instantaneously manage reactive and real power flow
Loss of CREZ wind hubs due to a disturbance during high wind periods may push ERCOT into under-frequency load shed

## Slide 3: What are the Opportunities?
Fiber Optic backbone via Optical Ground Wire (OPGW) can provide communication that is:
  High-speed / high-bandwidth – allows for multiple protocols to reside on same infrastructure
  Self-healing / looped – allows for the configuration of primary and secondary communications on the same infrastructure
Enables real-time high-speed control via Wide Area Networks
  Enhancing management of voltage profile / power flow
  Responding to sub-synchronous interactions / small signal power swings
Enables current differential protection, which is immune to the effects of mutual coupling, series capacitors, and power swings

## Slide 4: Potential Communication Loops

## Slide 5: What has to Happen?
Operating Guide Revision Request (OGRR) seeks to set minimum requirement for CREZ system design
  Redundancy as it relates to NERC Standards
  Protection standard for EHV transmission
Rationale for high speed/bandwidth communications
  TSP specific evaluation of cost / benefit
  ERCOT evaluation of potential reduction in spilled wind energy
  ERCOT Reactive Study to determine clearing time requirement
Develop comparison of production cost savings and other benefits verses the incremental cost of OPGW
  Benefit quantification of instantaneous system observability, and high speed remedial action systems
  Identification of ancillary benefits from high speed/bandwidth communications