###### ERCOT STEADY STATE WORKING GROUP

###### PROCEDURE MANUAL

January 08, 2010

ERCOT STEADY-STATE WORKING GROUP’S SCOPE

The ERCOT Steady-State Working Group (SSWG) operates under the direction of the Reliability and Operations Subcommittee (ROS). The SSWG’s main objectives are to produce seasonal and future load-flow base cases, coordinate tie-line data, update the Most Limiting Series Element Database, maintain the ERCOT Data Dictionary, update the SSWG Procedural Manual, prepare data for and review seasonal transmission loss factor calculation, and provide requested transmission system data and power-flow support documents to market participants. The SSWG usually meets in June and November to accomplish these tasks, and at other times during the year as needed to resolve any impending load-flow modeling issues or to provide technical support to the ROS. Some of the above responsibilities are further described as follows:

- Develop and maintain load-flow base cases for the spring, summer, fall, and winter seasons of the upcoming year. The cases, collectively known as Data Set A, are produced by the SSWG by approximately July 1st on an annual basis. These seasonal cases consist of one on peak and one off-peak case for each of the four seasons.

- Develop and maintain load-flow base cases for the five future years following the upcoming year. The cases, collectively known as Data Set B, are produced by the SSWG by approximately November 15th on an annual basis. These future cases consist of five summer on-peak cases, and one minimum case.  Data Set B will contain economically dispatched generation (ECO)

- Maintain and update the ERCOT Data Dictionary to reflect new bus information and SCADA names. This task is performed during the Data Set B work.

- Maintain and update the SSWG Procedural Manual to reflect current planning practices and the latest load-flow base case modeling methodologies.

- Prepare data for and review seasonal transmission loss factor calculation on an annual basis. This task is to be done by approximately January 1st.

Each TDSP shall maintain an MLSE database and will make the data available to ERCOT upon request.

- Assist in development of ERCOT processes for compliance with NERC Reliability Standards for both entity and region-wide requirements.

- Coordinate tie-line data submission to ERCOT with neighboring companies.

- Provide Transmission Project Information Tracking (TPIT) report to ERCOT quarterly.

- Maintain and update the contingencies files.

- Address issues identified by ERCOT Reliability Assessment

- Perform studies as directed by the ROS.

Table of Contents

###### SECTION 1.0 – Data Requirements	4

1.1 	General

4

1.2	Bus Data

5

1.3	Load Data

6

1.4	Generator Data

7

1.5	Line Data

11

1.6	Transformer Data

19

1.7	Static Reactive Devices

22

1.8	Dynamic Control Devices

24

###### HVDC Devices

###### 27

###### SECTION 2.0 – Load-flow Procedures and Schedules

###### 30

2.1	Data Set A Considerations

30

2.2	Data Set B Considerations

32

2.3	Error Screening and Case Updates

34

###### SECTION 3.0 – Other SSWG Activities

###### 37

3.1	Transmission Loss Factor Calculation …

37

3.2

Contingency Database……………………………….........................................38

###### APPENDICES

###### 41

A	Owner ID, TSP, Bus/Zone Range and Tables

41

B	Glossary of Terms

53

C	TSP Impedance and Line Ratings Assumptions

54

D	MLSE

68

E	TPIT

69

F	Treatment of Mothballed Units in Planning

70

G	Load Forecasting Methodology

72

H	Transmission Element Naming Convention

80

I	Method for Calculating Wind Generation Levels in SSWG Cases………….

81

J	Mexico’s Transmission System in ERCOT SSWG Cases.…………….……..82

###### SECTION 1.0 – Data Requirements

1.1 GENERAL

The principal function of the SSWG is to provide analytical support of the ERCOT electrical transmission network from a steady state perspective.  To accomplish this, the Working Group performs three principal charges: load-flow, voltage control and reactive planning, and transmission loss factor calculation tasks.

    - Coordination with ERCOT

- Load-flow base cases provide detailed representation of the electric system for planning and evaluating the current and future high voltage electrical system and the effects of new loads, generating stations, interconnections, and transmission lines.

    - Model

- The model represents the high voltage system, branches, buses, bus components, impedances, loads, multi-section lines, ownership, switched shunts, transformers, generators, DC lines and zones. The network model submitted by the TSP shall be in a format compatible with the latest approved PSS/E and rawd ASCII data format based on a 100 MVA base. The model should reflect expected system operation.

    - Data

The SSWG will based upon the load data on the ERCOT Annual Load Data Request (ALDR) and build two sets of cases, Data Set A and Data Set B (see Sections 2.1 and 2.2).  Reference appendix G.

Data Set A consists of seasonal cases for the following year.  The SSWG must finalize Data Set A by early July to meet ERCOT schedule to perform the commercially significant constraint studies. Data Set B, which is finalized in mid-October, is used for planning purposes and consists of the following:

- Future summer peak planning cases

- A future minimum load planning case

- ERCOT Data Dictionary

- Updated Contingency List

Load-flow Case Uses

- The cases being created each year are listed in Sections 2.1 and 2.2.  ERCOT SYSTEM PLANNING (ESP) and Transmission Service Providers (TSPs) test the interconnected systems modeled in the cases against the ERCOT Planning Criteria to assess system reliability in the coming year and into the future. ROS Working Groups and ERCOT System Operations use SSWG cases as the basis for other types of calculations and studies:

- Internal planning studies and generation interconnection studies

- Voltage control and reactive planning studies

- Dynamics Working Group stability studies

- ERCOT transmission loss factor calculation

- Basis for ERCOT operating cases and FERC 715 filing

- Commercially significant constraints studies

1.2 BUS DATA

    - Areas defined by TSP

Each TSP is assigned a unique area name and number denoted in the TSP Bus/Zone Range Table in Appendix A.

    - Bus Data Records

All in-service transmission (60kV and above) and generator terminals shall be modeled in load-flow cases. Each bus record has a bus number, name, base kV, bus type code, real component of shunt admittance, reactive component of shunt admittance, area number, zone number, per-unit bus nominal voltage magnitude, bus voltage phase angle, and owner id. Fixed reactive resources shall be modeled as a fixed component in the switchable shunt data record and not be part of the bus record.

    - Bus Ranges

Presently, ERCOT is modeled within a 100,000-bus range. The Chairman of the SSWG allocates bus ranges, new or amended, with confirmation from the SSWG members.  Bus ranges are based on high-side bus ownership. (Refer to TSP Bus/Zone Range Table in Appendix A)

Bus numbers from within the TSP’s designated bus range are assigned by the TSP and are to remain in the assigned ranges until the equipment or condition that it represents in the ERCOT load-flow cases changes or is removed.

    - Zone Ranges

Presently the Chairman of the SSWG allocates zone ranges, new or amended, with confirmation from SSWG members. Each TSP represents their network in the ERCOT load-flow cases using allocated zone ranges. Zone numbers that have been assigned by the TSP, within the TSP’s designated zone range, may be changed by the TSP as needed to represent their network in the ERCOT load-flow cases. Every zone number assigned must be from the TSP’s designated zone range. Zone identifiers are specified in zone data records.  Each data record has a zone number and a zone name identifier. (Refer to TSP Bus/Zone Range Table in Appendix A).

    - Owner IDs

All TSPs may provide owner IDs for buses. This data is maintained in the Owner ID, TSP Bus/Zone Range Table shown in Appendix A.  The generation owner ID’s are not in the cases due to the difficulty in tracking the continuously changing ownership.

    - Bus Name

Electrical Bus names shall not identify the customers or owners of loads or generation at new buses unless requested by customers.  The twelve characters Electrical Bus Name representing individual transmission element in the planning model shall be unique and follow certain technical criteria as stated in the ERCOT Nodal Protocol Section 3.10. (Refer to Transmission Element Naming Convention in Appendix H)

1.3 LOAD DATA

Each bus modeling a load must contain at least one load data record.  Each load data record contains a bus number, load identifier, load status, area, zone, real and reactive power components of constant MVA load, real and reactive power components of constant current load, and real and reactive power components of constant admittance load.  All loads (MW and MVAR) should be modeled on the high side of transformers serving load at less than 60 kV.

Guidelines:

    - The bus number in the load data record must be a bus that exists in the base case. As of 2001 owner IDs shall not be associated with any entity in cases. The load identifier is a two-character alphanumeric identifier used to differentiate between loads at a bus. All self-serve loads must be identified by “SS”. If there are multiple self-serve loads at the same bus, then the self-serve loads will be identified by S1, S2, S3, etc.  See Section 1.4.1.  Partial self-serve load should be modeled as a multiple load with “SS” identifying the self-serve portion. Distributed generation must be identified by “DG” and modeled as negative load.

    - The load data record zone number must be in the zone range of the TSP serving the load.  It does not have to be the same zone that the bus is assigned to.

1.3.3	Generator auxiliary load should not be modeled at generating station buses. Refer to section 1.4.1.

1.3.4	In conformance to NERC Planning Requirements and the ERCOT Operating Guides Section 5.1.2, which states “ Each ERCOT DSP directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual load forecasts to ERCOT as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures.  For each substation not owned by either a TSP or a DSP, the owner shall provide a substation load forecast to the directly connected TDSP sufficient to allow it to adequately include that substation in its ALDR response.”  Entities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TDSP has agreed to be the agent on SSWG for that entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the load flow cases during DataSetA and DataSetB annual updates.

    - Multiple loads from different TSPs at a bus may be used. At this time, each TSP can define a load however it wishes with a load ID of its choice though careful coordination is required between TSP representatives to ensure that the loads at the bus get modeled correctly. n

1.4 GENERATOR DATA

    - Acquisition of Generator Data

- Only net real and reactive generator outputs and ratings should be modeled in load-flow cases. Net generation is equal to the gross generation minus station auxiliaries and other internal power requirements.  All non-self-serve generation connected at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled. A generator explicitly modeled must include generator step-up transformer and actual no-load tap position. Generation of less than 10 MW is still required to be modeled, but not explicitly.

- Unit reactive limits (leading and lagging) for existing units should be obtained from the most recent generator reactive unit test data provided by ERCOT. For units that have not been tested, limits will be obtained from the generator owner. Unit reactive limits (leading and lagging) are tested at least once every two years (ERCOT Protocols, Section 6.10.3.5 and ERCOT Operating Guides, Section 6.2.3). If the test does not meet these requirements, reference the ERCOT Operating Guides for further explanation or actions.. Note that the CURL MVAr values are gross values at the generator terminals. Limited ERCOT RARF data shall be made available to SSWG upon request.

- Generator reactive limits should be modeled by one value for Qmax and one value for Qmin as described below:

- Qmax

- Qmax is the maximum net lagging MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability. Qmax is calculated from the lagging CURL value by subtracting any auxiliary MVAr loads and any Load Host MVAr (Self Serve) load served from the low side of the generator step up transformer.

- Example:

- Lagging CURL value is 85 MVAr

- Lagging test value is 	80 MVAr

- Auxiliary Load is       	5 MVAr

- Qmax is 85 – 5 = 80 MVAr (Use the CURL value here if the test value is equal to or greater than 90% of the CURL. Use the test value here if the test value is less than 90% of the CURL.)

- Qmin

- Qmin is the maximum leading MVAr observed at the low side of the generator step up transformer when the unit is operating at its maximum net dependable MW capability. Qmin is calculated from the leading CURL value by adding any auxiliary MVAr loads and any Load Host MVAr (Self Serve) load served from the low side of the generator step up transformer.

- Example:

- Leading CURL value is -55 MVAr

- Auxiliary Load is	 5 MVAr

- Qmin is -55 – 5 = -60 MVAr

      - Self-Serve Generation

- Self-serve generators serve local load that does not flow through the ERCOT transmission system. Generation data should be submitted for self-serve facilities serving self-serve load modeled in the base case. Total self serve generation MWs shall match total self-serve load MWs.

- Any generating unit or plant with gross real power output of at least 50 MW.

- Any self-serve loads with a contract of at least 50 MW of backup power.

      - Coordination with Power Generating Companies

- ERCOT shall request Power Generating Companies to provide the following information, in electronic format:

- Data forms from the ERCOT Generation Interconnection Procedure.  See Appendix F.

- One-line electrical system drawing of the generator’s network and tie to TSP (or equivalent) in readable electronic format (AutoCAD compatible)

- Modeling information of the generator’s transmission system in PTI or GE format

- Units to be retired or taken out for maintenance

      - Coordination with other ERCOT Working Groups

- All generator data should be coordinated with the Dynamics Working Group, OWG, Network Data Support Working Group and System Protection Working Group members to assure that it is correct before submitting the cases. This will insure that all of the cases have the most current steady state and dynamics information.  The following are items from the fall peak SSWG case that should be provided to these working groups for annual coordination by the end of the year:

- Unit bus number

- Unit ID Wind units will use W1 (discussion needed)

- Unit maximum and minimum real power capabilities

- Unit maximum and minimum reactive power capabilities

- Unit MVA base

- Resistive and reactive machine impedances

- Resistive and reactive generator step-up transformer impedances

    - Review Expected Load for Area to Serve

Before the generation schedule can be determined, the expected area load and losses (demand) must be determined. Each MW of demand needs to be accounted for by a MW of generation.

    - Generation Dispatch Methodology

In order to simulate the future market, the following methodology for generation dispatch has been adopted for building the Data Set A and Data Set B load flow cases.

Existing and planned units owned by the Non-Opt-In Entities (NOIE) are dispatched according to the NOIE's planning departments; unless a NOIE requests that their units are to be dispatched according to the order that is described below.

Private network generation is also dispatched independently. The plants are dispatched to meet their load modeled in the case. DC Ties are modeled as load levels or at generation levels based on historical data.  Likewise, wind plants are modeled at generation levels based on historical data.

See Appendix I on Method for Calculating Wind Generation Levels in SSWG Cases.

Units that are solely for black start purposes are to be modeled in the base cases; however, these units should not be dispatched.  Black start units are designated with a unit ID that begins with the letter ‘B’ which can be followed by an alphanumeric character (for example, ‘B1’, ‘B2’, etc.).

All other units are dispatched by performing a system simulation using the UPLAN software package.  The UPLAN simulation will dispatch units in order to minimize production costs taking into account unit start-up times and cost and heat rates while adhering to the following guidelines for each set of cases:

Data set A cases are dispatched to maintain CSC and CRE loading below their limits.  The uplan software simulates the system load for the two weeks leading up to the peak hour for each season.

Data set B economically constrained cases are dispatched in the most economical way for a given load level with no consideration for overloads.  The uplan software  simulates the system load for the two weeks leading up to the peak hour for each summer peak case and the two weeks leading up to the minimum load hour for the minimum case.

In all cases spinning reserve is maintained according to ERCOT guides.  Mothballed units are treated as described in Appendix F.  The dispatch may be modified for data set A cases if necessary to maintain voltages at acceptable levels.

Once ERCOT receives an executed interconnection agreement or public, financially-binding agreement between the generator and TSP under which generation interconnection facilities would be constructed or a commitment letter from a municipal electric provider or an electric cooperative building a generation project, the project will be included in the base cases beyond its expected in-service year.

SSWG shall be able to review and modify the generation dispatch based on historical information.

Extraordinary Dispatch Conditions

ERCOT power flow cases typically model load at individual TSP peaks instead of at the ERCOT system peak.  Additionally, some of the generation reserve modeled in the cases is actually made up from LaaR (Load Acting as a Resource) in system operations. Since LaaR is not modeled in powerflow cases it must be made up from generation resources. For these, and other reasons such as how mothballed generation is counted, the load and generation modeled in powerflow cases usually does not match the load and generation resources estimated in the ERCOT CDR.

These differences can result in future cases without sufficient dispatchable generation resources to match load.  When such a condition is encountered in future cases, ERCOT may increase generation resources by taking the indicated action, or adding generation, in the following order:

- DC ties dispatched to increase transfers into ERCOT to the full capacity of the DC ties.

- Mothballed units that have not announced their return to service.

- Ignore spinning reserve.

- Increase NOIE generation with prior NOIE consent

- Add publicly announced plants without interconnect agreements.

- Black start Units

- Add generation resources at the sites of retired units.

    - Voltage Profile Adjustments

      - Schedule Voltage for Generator Units

- After generation has been determined, the next step is to set the proper voltage profile for the system. The scheduled voltages should reflect actual voltage set points used by the generator operators.

      - Voltage Control

- Check the voltages at several key locations within the system when modifying generation voltage and control VARS.  When these voltages are not within acceptable parameters, changes in the system VARS are needed. VAR changes can be accomplished by turning on/turning off capacitors or reactors, and by changing the operations of generators (turning on/turning off/redispatching for Var control).

- 1.5 LINE DATA

    - Use of Load-flow Data Fields

      - Bus Specifications

The end points of each branch in the ERCOT load-flow case are specified by “from” and “to” bus numbers.  In most cases the end point buses are in the same TSP area.  However, when the “from” and “to” buses used to specify a branch are in different TSP areas, the branch is considered to be a tie line (See Section 1.5.3, Coordination of Tie Lines). Branch data includes exactly two buses. The end points of Multi-Section Lines (MSL) are defined by two buses specified in a branch data record.  (See 1.5.2.) There are other components that are modeled with more than two buses, such as transformers with tertiary that may be represented by three-bus models.

      - Circuit (Branch) Identifier

Circuit identifiers are limited to two alphanumeric characters.  Each TSP will determine its own naming convention. These identifiers are typically numeric values (e.g. 1 or 2) that indicate the number of branches between two common buses, but many exceptions exist.

      - Impedance Data

The resistive and reactive impedance data contained in the load-flow cases are both expressed in per-unit quantities that are calculated from a base impedance. The base impedance for transmission lines is calculated from the system base MVA and the base voltage of the transmission branch of interest.  The system base MVA used in the ERCOT load-flow cases is 100 MVA (S = 100 MVA).  The base voltage for a transmission line branch is the nominal line-to-line voltage of that particular transmission branch.  (See Transformer Data for Calculation of Transformer Impedances.) Therefore the base impedance used for calculating transmission branch impedances is:

Ohms

This base impedance is then used to convert the physical quantities of the transmission line into per-unit values to be used in the load-flow cases.

        - Resistance

Once the total transmission line resistance is known and expressed in ohms, then this value is simply divided by the base impedance to obtain the per-unit resistance to be entered in the load-flow case.  This calculation is as follows:

        - Reactance

Once the total transmission line reactance is known and expressed in ohms, then this value is divided by the base impedance to obtain the per-unit reactance and entered into the load-flow case.  This calculation is as follows:

        - Charging

Line charging is expressed as total branch charging susceptance in per unit on the 100 MVA system base.  The total branch charging is expressed in MVARs and divided by the system base MVA to get per unit charging.  The equation used to accomplish this depends on the starting point. Typically the charging of a transmission line is known in KVARs.  Given the total transmission line charging expressed in KVARs, the equation to calculate the total branch charging susceptance in per unit on the system base is as follows:

Or, given the total capacitive reactance to neutral expressed in ohms , the equation to calculate the total branch charging susceptance in per unit on the system base is as follows:

      - Facility Ratings

ERCOT load-flow cases contain fields for three ratings for each branch record.  The ratings associated with these three fields are commonly referred to as Rate A, Rate B and Rate C.  Methodology used by each TSP shall be kept current in Appendix C. Following are the ERCOT facility ratings definitions:

        - Ratings Definitions

Rate A  – Normal Rating

Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.   The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

Rate B  – Emergency Rating

Emergency Rating:  Represents the two (2) hour MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer (MLSE) at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

Rate C  – Conductor/Transformer Rating

Emergency Rating of the Conductor or Transformer:  Represents the two (2) hour MVA rating of the conductor or transformer only, excluding substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The conductor or transformer can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

I.e. Rate C ≥ Rate B ≥ Rate A

When performing security studies, ESP will default to Rate B, unless the TSP has previously indicated in writing that other ratings (e.g., Rate A) should be used.  If problems exist using Rate B and Rate B is significantly different from Rate C, then ESP will contact the TSP.

        - NERC Reliability Standards

Compliance with the NERC Reliability Standards for facility ratings is required in the ERCOT load-flow cases.

        - Most Limiting Series Element Database

MLSE database contains ratings of all existing elements in series (switches, current transformers, conductors, etc.) between the two end terminals of a transmission line and provides the maximum rating of the transmission line..

      - Complex Admittance

Branch Data records include four fields for complex admittance for line shunts.  These records are rarely used in ERCOT.

      - Status

Branch data records include a field for branch status.  Entities are allowed to submit branch data with an out-of-service status for equipment normally out of service.  This information will be kept throughout the load-flow data preparation process and returned to all entities with the final ERCOT load-flow cases.

      - Line Length and Ownership

The line length will be submitted by the TSP’s during the DSA and DSB case creation and TPIT updates and ownership may be submitted at their discretion.

        - Line Length

This data will be provided in miles

        - Ownership

The load-flow database allows users to specify up to four owners for each branch including percent ownership. The percent ownership of each line should sum up to 100%. See Appendix A.

Facilities owned by Generators will be assigned non-TSP ownership id in the cases.

        - Practices for Verification

Transmission line length for existing lines should be verified from field data before values are entered into the load-flow data.  The following equation is an approximation that applies to transmission lines that are completely overhead:

or assuming   MVA then

    - Multi-Section Line Grouping

A multi-section line is defined as a grouping of several previously defined branches into one long circuit having several sub-sections or segments.

Example: Two circuits exist (Figure 1) which originate at the same substation (4001) and terminate at the same substation (4742).  Each circuit has a tap to Substation A and a tap to Substation B.  If a fault occurs or maintenance requires an outage of Circuit 09, the circuit would be out-of-service between bus 4001 and bus 4742 including the taps to buses 4099 and 4672.  The loads normally served by these taps would be served by means of low-side rollover to buses 4100 and 4671 on Circuit 21.  This is the type of situation for which multi-section lines are used to accurately model load flows.

Figure 1.  Example of circuits needing to use multi-section line modeling.

Figure 2 represents a load-flow data model of the circuits in Figure 1.  Branch data record would have included the following:

4001,4099,09,…

4099,4672,09,…

4672,4742,09,…

4001,4100,21,…

4100,4671,21,…

4671,4742,21,…

along with the necessary bus, load, and shunt data.  To identify these two circuits as multi-section lines, entries must be made in the raw data input file.  The multi-section line data record format is as follows:

I,J,ID,DUM1,DUM2, … DUM9  where :

I	“From bus” number.

J	“To bus” number.

ID	Two characters multi-section line grouping identifier. The first character must be an ampersand (“&”).  ID = ‘&1’ by default.

DUMi	Bus numbers, or extended bus name enclosed in single quotes, of the “dummy buses” connected by the branches that comprise this multi-section line grouping. No defaults allowed.

Up to 10 line sections (and 9 dummy buses) may be defined in each multi-section line grouping.  A branch may be a line section of at most one multi-section line grouping.

Each dummy bus must have exactly two branches connected to it, both of which must be members of the same multi-section line grouping.

The status of line sections and type codes of dummy buses are set such that the multi-section line is treated as a single element.

Figure 2. Load-flow model of example circuits.

For our example, the following would be entered as multi-section line data records:

4001, 4742, &1, 4099, 4672

4001, 4742, &2, 4100, 4671

Multi-section lines give a great amount of flexibility in performing contingency studies on load-flow base cases.  When set up correctly, hundreds of contingencies where the automatic low-side load rollover occurs can be analyzed and reported within minutes.

    - Coordination of Tie Lines

A tie line is a branch that connects two TSP areas in the load-flow case. In a tie line, the bus at one end is in one TSP area and the bus at the other end is in another TSP area. Each of the interconnected TSPs owns some terminal equipment or line sections associated with the tie line.  The branch may be a transmission line, transformer, bus section or another electrical component connecting systems together.

Careful coordination and discussion is required among SSWG members to verify all modeled tie-line data. Even in load-flow cases where no new tie lines were installed, there could be many tie-line changes. Construction timings of future points of interconnection can change. As an example, a tie line may need to be deleted from a spring case and added to a summer case. Another example is, if a new substation is installed in the middle of an existing tie line, it redefines the tie-line bus numbers, mileages, impedances and possibly ratings and ownership.

Tie branch models also affect a number of important ERCOT calculations and therefore must accurately reflect real-world conditions. Also missing or erroneous ties can produce unrealistic indications of stability and/or voltage limits. Inaccurate metering points, impedances, ratings, transformer adjustment data, status information, mileages, or ownership data can all have a profound effect on system studies; therefore it is imperative that neighboring entities exercise care in coordinating tie branch data.

    - Metering Point

Each tie line or branch must have a designated metering point and this designation should also be coordinated between neighboring TSP areas.  The location of the metering point determines which TSP area will account for losses on the tie branch.  The PSS/e load-flow program allocates branch losses to the TSP area of the un-metered bus.  For example, if the metering point is located at the “to” bus then branch losses will be allocated to the TSP area of the “from” bus.

The first bus specified in the branch record is the default location of the metering point unless the second bus is entered as a negative number. These are the first and second data fields in the branch record.

    - Coordination of Tie-Line Data Submission

Ratings for tie lines should be mutually agreed upon by all involved entities and should comply with NERC Reliability Standards.

It is imperative for neighboring entities to coordinate tie data in order to allow Data Set A and Data Set B work activities to proceed unimpeded. Entities should exchange tie-line data at least two weeks before the data is due to ESP. Coordination of tie data includes timely agreement between entities on the following for each tie line:

- In-service/ out-service dates for ties

- Metering point bus number

- From bus number

- To bus number

- Circuit identifier

- Impedance and charging data

- Ratings

- Transformer adjustment (LTC) data

- Status of branch

- Circuit miles

- Ownership (up to four owners)

- Entity responsible for submitting data

1.6 TRANSFORMER DATA

    - Transformer Data

Every transformer is to be represented in the transformer data record block.  The transformer data block specifies all the data necessary to model transformers in power flow calculations.  Both two winding transformers and three winding transformers can be specified in the transformer data record block. Three-winding transformer should be represented by its three-winding model and not by its equivalent two-winding models.

      - Bus Numbers

The end points of each transformer branch in the ERCOT load-flow case are specified by “from” and “to” bus numbers.  The “from” bus is the bus connected to the tapped side of the transformer and the “to” bus is connected to the impedance side of the transformer being modeled. In some cases, the “from” and “to” buses used to specify a branch are in two different TSP areas, making the branch a tie line (See Section 1.5.3, Coordination of Tie Lines). The “from” bus is the metered side of the transformer by default, but can be assigned to the other bus by assigning a negative number to the second bus. The metered side determines which TSP area losses due to the transformer are assigned to (TSP area of the un-metered bus).  Three winding transformers (transformers with tertiary winding) can be represented by utilizing the “from” and “to” bus numbers and in addition the “last” bus number in the data block to represent the tertiary winding.

      - Transformer Circuit Identifier

Circuit identifiers are limited to two alphanumeric characters. Actual transformer identifiers may be used for circuit identifiers for transformers, however, typically, circuit identifiers are used to indicate which transformer is being defined when more than one transformer is modeled between two common buses. Where practical, TO’s should identify autotransformers with the letter A as the first character of the ID field.  Generator Step-Up transformers should be identified with the letter G.  Phase-shifting transformers should be identified with the letter P.

      - Impedance Data

The resistance and reactance data for transformers in the load flow database are specified: (1) in per-unit on 100 MVA system base (default), (2) in per-unit on winding base MVA and winding bus base voltage, (3) in transformer load loss in watts and impedance magnitude in per-unit on winding base MVA and winding bus base voltage.

        - Resistance

Transformer test records should be used to calculate the resistance associated with a transformer branch record. Where transformer test records are unavailable, the resistance should be entered as zero.

        - Reactance

Transformer test records or transformer nameplate impedance should be used to calculate the reactance associated with a transformer branch record. Where the transformer resistance component is known, the transformer impedance is calculated on the same base using the known data and the reactance component is determined using the Pythagorean Theorem. Where the transformer resistance is assumed to be zero, the calculated transformer impedance can be assumed to be equal to the transformer reactance.

        - Susceptance

For load-flow modeling purposes, the transformer susceptance is always assumed to be zero.

      - Transformer Ratings

The ratings used for transformer branches are defined the same as in Section 1.5.1.4, Facility Ratings.

      - Tap Ratios

The ratio is defined as the transformer off nominal turns ratio and is entered as a non-zero value in per unit. Where the base kV contained in the bus data records for the buses connected to transformer terminals are equal to the rated voltage of the transformer windings connected to those terminals, the transformer off-nominal ratio is equal to 1.00. When the transformer has no-load taps, the transformer off-nominal ratio will be something other than 1 and usually in the range of 0.95 to 1.05. The effects of load tap changing (LTC) transformer taps are also handled in the transformer data record. Actual no-load tap settings will be periodically requested by ERCOT.

      - Angle

The transformer phase shift angle is measured in degrees from the untapped to the tapped side of the transformer. The angle is entered as a positive value for a positive phase shift.

      - Complex Admittance

Complex admittance data is not required for ERCOT load-flow cases and the values for each of these four fields should be zeros.

      - Length

Circuit mileage has no meaning in a transformer branch record and should be entered as zero.

      - Status

This field indicates the status of the transformer. A value of 1 indicates the transformer is in-service and a value of zero indicates the transformer is out-of-service.

      - Ownership

The load-flow case allows users to specify up to four owners for each branch including percent ownership. Ownership and owner IDs should be included for all non-transformer branches. The sum of all percent ownerships should equal 100% for every line.

      - Controlled Bus

The bus number of the bus whose voltage is controlled by the transformer LTC and the transformer turns ratio adjustment option of the load-flow solution activities. This record should be non-zero only for voltage controlling transformers.

      - Transformer Adjustment Limits

These two fields specify the upper and lower limits of the transformer turns ratio adjustment or phase shifter adjustment.  For transformers with automatic adjustment, they are typically in the range 0.80 to 1.20.

        - Upper Limit

This field defines the maximum upper limit of the off-nominal ratio for voltage or reactive controlling transformers and is entered as a per-unit value. The limit should take into account the no-load tap setting of the transformer, if applicable. For a phase shifting transformer, the value is entered in degrees.

        - Lower Limit

Similar to the upper limit, this field defines the lower limit of the off-nominal ratio or phase shift angle for the transformer defined.

      - Voltage or Load-Flow Limits

These two fields specify the upper and lower voltage limits at the controlled bus or for the real or reactive load flow through the transformer at the tapped side bus before automatic LTC adjustment will be initiated by the load-flow program. As long as bus voltage is between the two limits, no LTC adjustment will take place.

        - Upper Limit

This field specifies the upper limit for bus voltage in per unit at the controlled bus or for the reactive load flow in MVAR at the tapped side bus. For a phase shifting transformer, this field specifies the upper limit for the real load flow in MW at the tapped side bus.

        - Lower Limit

Similar to the upper limit, this field specifies the lower limit for the bus voltage or the real or reactive load flow for the transformer defined.

      - Step

Transformer turns ratio step increment for LTC is defined by this field and entered in per unit. Most LTC transformers have 5/8% or 0.00625 per unit tap steps.

      - Table

The number of a transformer impedance correction table is specified by this field if the transformer's impedance is to be a function of either the off-nominal turns ratio or phase shift angle. ERCOT load-flow cases normally don’t use these tables and this field is set to zero by default.

      - Control Enable

This field enables or disables automatic transformer tap adjustment. Setting this field to one enables automatic adjustment of the LTC or phase shifter as specified by the adjustment data values during load-flow solution activities. Setting this field to zero prohibits automatic adjustment of this transformer during these activities.

      - Load Drop Compensation

These two fields define the real and reactive impedance compensation components for voltage controlling transformers. They are ignored for MW and MVAR flow controlling transformers. ERCOT load-flow cases normally don’t use these fields and they are set to zero by default.

      - Resistive Component

The resistive component of load drop compensation entered in per unit is based on the resistance between the location of the LTC and the point in the system at which voltage is to be regulated.

      - Reactive Component

Similar to the resistive component of load drop compensation, this value is entered in per unit and is based on the reactance between the location of the LTC and the point in the system at which voltage is to be regulated.

1.7 STATIC REACTIVE DEVICES

Presently all shunt reactors and capacitors that are used to control voltage at the transmission level are to be modeled in the ERCOT load-flow cases to simulate actual transmission operation. There are two distinct static reactive devices currently represented in the ERCOT load-flow cases: bus shunts and series compensated capacitors.  For ease of identifying all capacitive shunt devices in the ERCOT load-flow cases shunt devices are modeled as switched shunts. or fixed shunts

    - Switched Shunt Devices

      - Bus Shunt

A shunt capacitor or reactor connected to the high side or low side of a substation transformer in a substation should be represented in the ERCOT load-flow case as a switched or fixed shunt device to accurately simulate operating conditions.  Care should be exercised when specifying the size of cap banks. Be sure that the rated size of the bank is for 1.0 per unit voltage.  Care should be taken to ensure that distribution level capacitors are not modeled in such a way as to be counted twice.

When a switched capacitor or reactor is submitted as the switched shunt data record, there are three modes that it can operate in: fixed, discrete, or continuous.  Switched capacitors are to be modeled in the discrete mode.

A switched shunt can be represented as up to eight blocks of admittance, each one consisting of up to nine steps of the specified block admittance. The switched shunt device can be a mixture of reactors and capacitors.  The reactor blocks are specified first in the data record (in the order in which they are switched on), followed by the capacitor blocks (in the order in which they are switched on). The complex admittance (p.u.), the desired upper limit voltage (p.u.), desired lower limit voltage (p.u.), and the bus number of the bus whose voltage is regulated must be defined to accurately simulate the switched shunt device.

A positive reactive component of admittance represents a shunt capacitor and a negative reactive component represents a shunt reactor.

      - Dummy Bus Switched Shunt

If a switchable capacitor or reactor were connected to a transmission line instead of a bus, an outage of the transmission line would also cause the capacitor or reactor to be taken out of service (see Figure 3).  For these instances, the most accurate model is the switched shunt modeled at a dummy bus connected by a zero impedance branch to the real bus.  This dummy bus must have exactly two branches connected to it, both of which must be members of the same multi-section line grouping.  The status of the line section is that the multi-section line is treated as a single element.  A capacitor or reactor connected to a line but modeled, as a bus shunt will result in load-flow calculations for contingencies that differ from real operating conditions.

Figure 3. Example one-line of line connected capacitor bank

    - Series Compensated Capacitor Banks

Series compensated capacitor banks will be modeled as a series branch with Negative reactance, zero charging, and Zero Resistance with a parallel by-pass.

    - Fixed Shunt Capacitor Banks

A shunt capacitor or reactor connected to the high side or low side of a substation transformer in a substation can be represented in the ERCOT load-flow case as a fixed shunt device to accurately simulate operating conditions.  Care should be exercised when specifying the size of cap banks. Be sure that the rated size of the bank is for 1.0 per unit voltage.  A fixed bus shunt can be modeled as a fixed shunt for easy identification in the ERCOT load-flow cases.  Care should be taken to ensure that distribution level capacitors are not modeled in such a way as to be counted twice.

Multiple fixed shunts can be modeled at a bus, each with a unique ID.  These fixed shunts have a status that can set to on or off.

A positive reactive component of admittance represents a shunt capacitor and a negative reactive component represents a shunt reactor.

1.8 DYNAMIC CONTROL DEVICES

There is a multiplicity of FACTS (Flexible ac Transmission System) devices currently available comprising shunt devices, such as Static Compensator (STATCOM), series devices such as the Static Synchronous Series Compensator (SSSC), combined devices such as the Unified Power Flow Controller (UPFC) and the Interline Power Flow Controllers (IPFC). These devices are being studied and installed for their fast and accurate control of the transmission system voltages, currents, impedance and power flow. They are intended to improve power system performance without the need for generator rescheduling or topology changes. These devices are available because of the fast development of power electronic devices specifically gate-turn-off semiconductors.

    - Basic Model

Figure 4.  Basics FACTS Control Device Model

Each FACTS device data record shall have the following information:

| N | FACTS control device number |
| --- | --- |
| I | Sending end bus number |
| J | Terminal end bus number (0 for a STATCOM) |
| MODE | Control mode |
| PDES | Desired real power flow arriving at the terminal end bus in MW (default 0.0) |
| QDES | Desired reactive power flow arriving at the terminal end bus in MVAR (default 0.0) |
| VSET | Voltage set point at the sending end bus in pu (default 1.0) |
| SHMX | Maximum shunt current at sending end bus in MVA at unity voltage (default 9999.) |
| TRMX | Maximum bridge real power transfer in MW (default 9999.) |
| VTMN | Minimum voltage at the terminal end bus in pu (default 0.9) |
| VTMX | Maximum voltage at the terminal end bus in pu (default 1.1) |
| VSMX | Maximum series voltage in pu (default 2.0) |
| IMX | Maximum series current in MVA at unity voltage (default 0.0) |
| LINX | Reactance of dummy series element used in certain solution states in pu (default 0.05) |

The FACTS model figure has a series element that is connected between two buses and a shunt element that is connected between the sending end bus and ground. The shunt element at the sending end bus is used to hold the sending end bus voltage magnitude to VSET subject to the sending end shunt current limit SHMX.  This is handled in power flow solutions in a manner similar to that of locally controlling synchronous condensers and continuous switched shunts.  One or both of these elements may be used depending upon the type of device.

A unified power flow controller (UPFC) has both the series and shunt elements active, and allows for the exchange of active power between the two elements. (I.e. TRMX is positive)

A static series synchronous condenser (SSSC) is modeled by setting both the maximum shunt current limit (SHMX) and the maximum bridge active power transfer limit (TRMX) to zero. (I.e. the shunt element is disabled).

A static synchronous condenser (STATCON) or static compensator (STATCOM) is modeled by a FACTS device for which the terminal end bus is specified as zero. (I.e. the series element is disabled).

An Interline Power Flow Controller (IPFC) is modeled by using two consecutively numbered series FACTS devices.  By setting the control mode, one device will be assigned, as the IPFC master device while the other becomes the slave device.  Both devices have a series element but no shunt element.  Conditions at the master device define the active power exchange between the devices.

    - Power Flow Handling of FACTS Devices

For an in-service FACTS device to be modeled during power flow solutions, it must satisfy the following conditions:

1.	The sending end bus must be either a type 1 or type 2 buses.

2.	The sending end bus must not be connected by a zero impedance line to a type 3 bus.

3.	If it is specified, the terminal end bus must be a type 1 bus with exactly one in-service AC branch connected to it; this branch must not be a zero impedance line and it must not be in parallel with the FACTS device.

4.	If it is specified, the terminal end bus must not have a switched shunt connected to it.

5.	If it is specified, the terminal end bus must not be a converter bus of a DC line.

6.	A bus, which is specified as the terminal end bus of an in-service FACTS device, may have no other in-service FACTS device connected to it. However, multiple FACTS device sending ends on the same bus are permitted.

7.	A bus, which is specified as the terminal end bus of an in-service FACTS device, may not have its voltage controlled by any remote generating plant, switched shunt, or VSC DC line converter.

1.9 HVDC DEVICES

HVDC Devices allow a specified real power flow to be imposed on the DC link.  For base case operation, this should be set to the desired interchange across the DC tie.  Capacitors, filter banks and reactors should be modeled explicitly and switched in or out of service based on normal DC tie operation.  The HVDC model itself normally calculates reactive power consumption.

HVDC ties with external interconnections may be modeled by the use of either the Two Terminal DC Transmission Line Data or Voltage Source Converter DC Line Data.

    - Two Terminal DC Transmission Line Data

Conventional HVDC ties should be modeled using Two Terminal DC Transmission Line Data.  The Two Terminal DC Transmission Line Data model represents the HVDC terminal equipment, including any converter transformers, thyristers, and the DC link.  The model will calculate voltages, converter transformer taps, losses, and VA requirements, based upon the power transfer over the HVDC facility, and the terminal AC bus voltages.

    - Basic Two-Terminal HVDC Model

Figure 5.  Basic Two-Terminal HVDC Model

A type 3 swing bus must be modeled on the bus external to ERCOT.  Filters and capacitors, and reactors on the AC terminals should be explicitly modeled, and set to minimize the VAr interchange to the AC system.

1.9.3	Relevant parameter values for Two-Terminal HVDC Model

| I | The DC line number. |
| --- | --- |
| MDC | Control mode: 0 for blocked, 1 for power, 2 for current. |
| RDC | DC line resistance, entered in ohms. |
| SETVL | Current (amps) or power (MW) demand. The sign of SETVL indicates desired power at the rectifier when positive, and desired power at the inverter when negative. |
| VSCHD | Scheduled DC voltage in kV |
| METER | Metered end code of either ‘R’ (for rectifier) or ‘I’ (for inverter). |
| IPR | Rectifier converter bus number |
| EBASR | Rectifier primary base AC voltage in kV. |
| TAPR | Rectifier tap setting |
| IPI | Inverter converter bus number |
| EBASI | Inverter primary base AC voltage in kV. |
| TAPI | Inverter tap setting |

Notes:

- The DC line number, I, must be unique, and should be assigned by the ERCOT SSWG, such that new DC lines do not overlay existing DC lines in the ERCOT cases.

- SETVL may be varied to dispatch the amount of flow over the DC.

- To reverse the flow over the DC, it is necessary to reverse the Rectifier converter bus number, IPR, and the Inverter converter bus number, IPI.

1.9.4	Voltage Source Converter (VSC) DC Line Data

Voltage Source Converter DC line data can be used to model DC ties that use the voltage source converter technology, for PSS/e Rev. 30 and above.

1.9.4	VSC DC Line Basic Model

Figure 6.  Basic VSC DC Line Model

1.9.5	Relevant parameter values for VSC DC Line Data

| NAME | VSC Lines are designated by a NAME, rather than a number |
| --- | --- |
| MDC | Control mode: 0 for out-of-service, 1 for in-service. |
| RDC | DC line resistance, entered in ohms. |
| IBUS | Converter bus number |
| TYPE | Type code: 0 for converter out-of-service, 1 for DC voltage control, 2 for MW control. |
| MODE | Converter AC control mode 1 for AC voltage control, 2 for fixed AC power factor. |
| DCSET | If Type=1, the scheduled DC voltage; if Type=2, the power demand, with the sign indicating direction of flow. |
| ACSET | For Mode=1, the regulated AC voltage set point; for Mode=2, the power factor set point. |
| SMAX | Converter MVA rating |
| IMAX | Converter AC current rating |

Notes:

- The VSC Name, must be unique, and should be assigned by the ERCOT SSWG, to prevent overlaying existing VSC DC lines in the ERCOT cases.

- DCSET may be varied to dispatch the amount of flow over the VSC DC, with the sign indicating the direction of flow.  (It is not necessary with VSC DC line data to reverse the rectifier and inverter bus numbers).

- A type 3 swing bus must be modeled on a bus in the system external to ERCOT.

- Filters and capacitors, and reactors on the AC terminals should be explicitly modeled, and set to minimize the VAR interchange to the AC system.

###### SECTION 2.0 – Load-Flow Procedures and Schedules

2.1 DATA SET A CONSIDERATIONS

The detailed data requirements for the production of the load-flow cases by ESP are described in other sections of these guidelines.  This section presents a general overview of the items that should be considered when preparing ERCOT load-flow data.

    - Data Set A Uses

The ‘Data Set A’ cases are used for short-term planning studies, system operations analysis, commercially significant constraint determination, and transmission loss factor calculations. Data Set A cases are submitted by the ERCOT region in response to FERC 715 requirements and are posted on ERCOT web site for general use.

    - Data Set A Case Definitions

Load-flow cases produced by ESP are to be divided into two groups.  The first group, “Data Set A,” models expected conditions for the following year’s four seasons (eight cases).  The second group, “Data Set B,” models cases for the five-year planning horizon.

Data Set A seasons are as follows:

SPG		March, April, May

SUM		June, July, August, September

FAL		October, November

WIN		December, January, February

ERCOT DATA SET A BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR) SPG1 | 2 | April 1, (YR) |
| (YR) SPG2 | 3 | April 1, (YR) |
| (YR) SUM1 | 1 | July 1, (YR) |
| (YR) SUM2 | 3 | July 1, (YR) |
| (YR) FAL1 | 2 | October 1, (YR) |
| (YR) FAL2 | 3 | October 1, (YR) |
| (YR+1) WIN1 | 1 | January 1, (YR+1) |
| (YR+1) WIN2 | 3 | January 1, (YR+1) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent maximum expected load during month of transmission in-service date.

- Cases to represent lowest load on same day as the corresponding seasonal case (not a minimum case). For example, (YR) FAL2 case represents the lowest load on the same day as the (YR) FAL1 case.

    - Entity Responsibilities

The Data Set A load-flow cases are assembled and produced by ESP.  The responsibilities for providing this data are divided among the various market participants. These data provision responsibilities may overlap among the various market participants because participants may designate their representative or a participant may be a member of more than one market participant group.  The market participants can generally be divided into four groups: TSPs, Load Serving Entities, Power Generating Companies, and Marketing Entities.  The data responsibilities of each group are as follows:

      - TSPs

It is the responsibility of the TSPs to provide all the data required to model the transmission system (line impedances, ratings, transformers, reactive sources, etc.) This will include data for all generator step-up transformers physically tied to the system of the TSP.  Transmission providers shall model the load or generation data if they are the designated representatives for load entities or power generating companies.

      - Load Serving Entities

Each ERCOT DSP directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual load forecasts to the ERCOT as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures.  For each substation not owned by either a TSP or a DSP, the owner shall provide a substation load forecast to the directly connected TDSP sufficient to allow it to adequately include that substation in its ALDR response.  Entities not having representation on SSWG shall submit the data to ERCOT or if the directly connected TDSP has agreed to be the agent on SSWG for that entity, to that TSP.  If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the load flow cases during DataSetA and DataSetB annual updates.

      - Power Generating Companies

It is the responsibility of the generation entities to provide all data required to model the generators in all the cases. See Section 1.4. This data should be coordinated with ERCOT and should include but is not limited to unit capabilities.

      - Marketing Entities

It is the responsibility of marketers to supply the load and/or generation data if they are the designated representatives for either a load or generating entity or both.

    - Schedule

ESP shall post all data and information. As an example:

Mar	1	ALDR due to ESP

April 	3	ALDR due to SSWG

April 	21	NOIEs send generation dispatch data to ESP

May 	5	Raw data files due to ESP

May 	12	Pass 1 cases due to SSWG  (w/UPLAN economic dispatch)

May 	19 	Pass 1 changes due to ESP

May 	26	Pass 2 cases due to SSWG  (w/UPLAN economic dispatch)

June 	2	Pass 2 changes due to ESP

June 	7	Pass 3 cases due to SSWG  (w/UPLAN economic dispatch)

June 	13-15	SSWG meeting at ESP office to finalize cases

June 	30	Cases posted on the ERCOT web site by ESP

2.2 DATA SET B CONSIDERATIONS

    - Data Set Uses

Data Set B cases are generally used by TSPs to perform long-range planning studies.

    - Data Set B Case Definitions

ERCOT DATA SET B BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR+1) SUM1 | 1 | JULY 1, (YR+1) |
| (YR+2) SUM1 | 1 | JULY 1, (YR+2) |
| (YR+3) MIN | 2 | JANUARY 1, (YR+3) |
| (YR+3) SUM1 | 1 | JULY 1, (YR+3) |
| (YR+4) SUM1 | 1 | JULY 1, (YR+4) |
| (YR+5) SUM1 | 1 | JULY 1, (YR+5) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent the absolute minimum load expected for (YR+3).

    - Data Set B Dispatching

Data Set B will contain economically dispatched generation (ECO).

    - ERCOT Data Dictionary

Each SSWG member will submit a data file listing all buses that exist in any case from either Data Set A or B 30 days after completion of Data Set B cases.  This file is called the ERCOT Data Dictionary.   The data dictionary is used by ESP to show correlation between base case bus numbers and TSP area SCADA names.  Also, the data dictionary without the SCADA names is included as part of ERCOT’s FERC 715 filing.  The format will be as follows:

| Notes | Column | Description | Who's Responsible |
| --- | --- | --- | --- |
| TDSP | A | NM fill in |  |
| Planning Bus Date In | J | Should be added by a member of SSWG. This is a required field for all the buses which are going in service in the future. | SSWG |
| Planning Bus Date Out | K | Should be added by a member of SSWG. This is a required field for all the buses which are going out of service either in current year or in the future. | SSWG |
| Planning Bus No | L | Planning - Up to 5 digit number used in planning models. Will be added by a member of the SSWG. Is required by FERC for FERC 715 pt. 2 report. | SSWG |
| Planning Base kV | M | Planning Base kV - Will be added or corrected by a member of SSWG. Is required by FERC for FERC 715 pt. 2 report. | SSWG |
| Planning Bus Name | N | Planning - 12 character name used in planning models. Will be added by a member of the SSWG. Is required by FERC for FERC 715 pt. 2 report. | SSWG |
| Planning Full Bus Name | O | Planning Full Bus Name that has been used in planning. Will be added by a member of the SSWG. Is required by FERC for FERC 715 pt. 2 report. | SSWG |
| Planning Comments | P | This Field is optional and should be used by SSWG members to input some comments like bus name changed, bus number changed etc... | SSWG |
| County of Bus | Q | Planning - Self explanatory - geography. Is required by FERC for FERC 715 pt. 2 report. | SSWG |

There are several naming conventions that should not be used because it creates problems when the data dictionary is used for ESP’s operations load-flow model. The following special characters should not be used: ‘$’, ‘%’, ‘:’, ‘!’, ‘@’, ‘&’, ‘(’, ‘)’ or ‘’’. No field should begin with an underscore or a # sign. SCADA names should be a maximum of eight characters long, and there should be no duplicate SCADA names at the same voltage level in the ERCOT Data Dictionary. SCADA names are not required for future substations.

    - Schedule

ESP shall post all data and information. As an example:

Sept	8	NOIEs send generation dispatch data to ESP

Sept	15	Raw data files due to ESP

Sept	22	Pass 1 cases due to SSWG

Sept	29	Pass 1 changes due to ESP

Oct	6	Pass 2 cases due to SSWG

Oct	13	Pass 2 changes due to ESP

Oct	20	Pass 3 cases due to SSWG

Oct	27	Pass 3 changes due to ESP

Nov	1-3	SSWG meeting at ESP office to finalize cases

Nov	17	Cases posted on the ERCOT web site by ESP

2.3 ERROR SCREENING AND CASE UPDATES

SSWG members are responsible for assembling all of the information for the sub-systems they are responsible for and, through a systematic process, creating the load-flow base cases.  This requires many steps, each of which may introduce errors.  To minimize the potential for errors in the cases, there are many data screens and error checks that should be employed.  These can be local or global in nature.

The creation of the load-flow base cases consists of two distinct phases. Therefore, the screening for and correction of errors will be divided into two different processes.  These two phases are:

- Producing the application for load serving entities’ Annual Load Data Request

- Creating the cases for Data Set A and Data Set B

    - Review of ALDR

The ALDR provides the detailed load data for each customer that is requesting transmission service.  Because of the vastness of the data in the ALDRs, it is critical that they be reviewed and screened with the utmost diligence before their submittal to ESP.

- Load shall be consistent with ALDR.

- Load serving entities’ total load plus losses in cases shall be consistent with coincident system load in the ALDR, excluding self-serve load.

- Bus numbers should be within TSP designated SSWG bus range

After ESP reviews each ALDR, they are sent to all SSWG members who should review them closely before they are used to create load-flow case data. If ALDR problems are found, SSWG members should contact the entities submitting the data.  Proper communication between TSP should minimize these problems.  Some checks that should be performed (by spreadsheet format) include but are not limited to the following:

- The bus number in column D must be included. No duplicate IDs, bus numbers or bus names.

- The coincidence factors in columns K and Q must be less than or equal to 100%.

- The Minimum/Peak value in column T must be less than or equal to 100%.

- All power factors must be less than or equal to 1.

- There should be a continuity of power factors for loads that have changed from one TSP to another.

- The county name should be spelled correctly.

- NA, N/A, or other alphabetic characters should not appear in a numerical field (leave field blank if not sure). Also #DIV/0! and #VALUE! should be deleted.

- There should be only one voltage level for each delivery point.

- In some places the workbook asks for kW or KWH and in some places MW or MWH.  The values must be in the correct measure.

- The calculated diversity factor in row 33 should be greater than or equal to 100%.

- Correct TSP code.

- No missing loads (i.e. loads that have changed from one TSP to another have not been dropped.)

- No duplicate loads.

    - Review of Load-Flow Base Case Data

Checks should include but are not limited to the following:

- Bus numbers should be within that TSP’s designated SSWG bus range

- Zone numbers should be within that TSP’s designated SSWG zone range

- No disconnected buses and swingless islands.

- No buses with blank nominal voltage.

- No radial distribution buses will be allowed in cases.

- No transformers serving non-network distribution buses.

- Should not be any topology differences between on-peak seasonal cases and corresponding off-peak seasonal cases (e.g. 98SPG1 vs. 98SPG2)

- Branch data checks:

- Every branch should have mileage

- Mileage comparison to impedance is reasonable

- Percentage ownerships total 100% for all lines

- No inordinately small impedances (less than 0.0001 p.u.)

- No inordinately large impedance (greater than 3.000 p.u.)

- No inordinately high R/X ratio (absolute value of R greater than 2 times absolute value of X)

- Generally no negative reactances (with the exception of 3 winding transformers)

- No inordinately high charging (greater than 5.000 or negative)

- Zero impedance branches connected to generation buses

- Zero impedance loops (X<0.0001 p.u. on 100 MVA base).  Cases will not solve with mismatches within the zero impedance loops.

- Transformer data checks:

- No transformer RMAX < RMIN

- No transformer VMAX < VMIN

- Difference between VMAX and VMIN should be 0.0125 or greater

- No inordinately high tap ratios (greater than 1.200)

- No inordinately low tap ratios (less than 0.800)

- No non-transformer branches between voltages levels

- No tap positions bigger than 33 unless verified

- Generator data checks:

- No zero generator source impedance (CONG)

- No maximum generation (PMAX) less than minimum generation (PMIN).

- No maximum reactive generation (QMAX) less than minimum reactive generation (QMIN).

- Offline generators should be Type 2 with status 0.

- No plant specified as remotely regulating itself (remote bus must be zero if self-regulating).

- Generators controlling the same remote bus shall have its remote var dispatch factor (RMPCT) proportional to the generator capability.

    - Solved Case Checks

A case is considered solved when a power-flow program reaches a solution using the following method:  a Fully Coupled Newton-Rhapson iterative algorithm with a tolerance of the largest bus mismatch of .5 MW or MVAR on a 100 MVA base (.005 per unit) or less.  Other solution techniques may be applied prior to executing this solution method to converge the case.

A case shall also meet the following conditions:

- Solve in less than 20 iterations (preferably in less than 12 iterations)

- Transformer tap stepping enabled.

- Switched shunts  enabled

- Phase shifters enabled

- DC transformer tap stepping enabled

- Generator var limits enforced immediately

- The system swing generation real output should be within normal operating parameters of the unit.

- Generally for Data Set A cases all line and equipment loading and voltage levels should be within applicable rating limits.

- No branches loaded above any of Rate A, Rate B or Rate C

- No buses with solved voltage above 1.050 p.u.

- No buses with solved voltage below 0.950 p.u.

- Data Set B cases may contain overloaded branches and voltage levels outside of applicable limits.

- There should be no voltage control conflicts (for example, PTI’s CNTB ALL).

- Before finalizing cases each TSP will verify and acknowledge with email the error checking output produced by ESP.

# Review of Tie-Line Listing

Coordination between TSPs is critical in maintaining the tie-line listing. Some potential problems that need to be reviewed include:

- Correct add/remove years

- Correct from/to bus numbers

- Correct metering location

- Correct conductor description

- Correct ownership

- Correct mileage and impedance/rating

- TSPs should agree on all ratings

Once the discrepancies are identified, TSPs need to correct the differences and make appropriate updates both to load-flow cases and the tie-line listing.

    - Case Updates

When necessary the TSP will document updates, which will be posted by ESP. The file name should have a clear description, which will include provider’s acronym and the specific case to be updated.

ERCOT will include a tracking sheet with each pass of TPIT, case building, and contingencies.

SECTION 3.0 – Other SSWG Activities

3.1 TRANSMISSION LOSS FACTOR CALCULATIONS

Transmission Loss Factors

The transmission loss factors must be calculated according to Protocol Section 13. The loss factors are calculated using SSWG DSA base cases. The values are entered in the ERCOT settlements system to account for losses on the transmission system. Separate calculations are performed for the eight Data Set A cases: spring, summer, fall, and winter with an on and off peak for each season.

The Non Opt In Entities (NOIE) that provide metering of their system load to the ERCOT settlement system by a set of ERCOT Polled Settlements Meters (EPS) that ‘ring’ their transmission system as defined in Protocol 13.4.1 have additional calculations performed for their transmission loss factors.

The NOIE that send extra data to ERCOT for the loss calculations have EPS settlement meters on all of their transmission lines that connect or “tie” their system to the rest of the ERCOT transmission network. For the ERCOT settlement process ERCOT calculates their load as the net of inflows minus the outflows from these EPS meters. However calculations must be performed to subtract out the losses on the transmission lines that are ‘inside’ their EPS meters. If this was not done then these NOIE loads would be too high relative to the other loads where EPS meters are at each delivery point. Other NOIE send EPS metering data from each delivery point so their load can be calculated by summing the individual points. Therefore the extra calculations are not necessary.

The process with approximate timelines for creating the loss factors is below.

- Send out a request to SSWG for any case updates, changes to NOIE bus ranges, and latest self serve data. NOIE’s that have a ‘ring’ of EPS meters must validate the PSS/E Metered End data in each of the cases. The PSS/E Metered End for a transmission facility that is not inside the ‘ring’ of EPS meters should be Metered ‘to’ the remote bus, and not Metered ‘to’ bus where the EPS meter is located.

- Verify self-serve data with the ERCOT planning staff that performs the congestion management functions (CSC &TCR). The CSC process tries to verify with ERCOT operations where the self-serve is located.

- Update base cases. (1 week)

- Update the transmission loss factor spreadsheet. (1/4 day)

- Perform the calculations. (1 day)

- Fill in the yellow shaded squares on the loss factor spreadsheet. (1/4 day)

- Create the DIFF spreadsheet between this year and last year. (1/4 day)

- Send to SSWG for review and approval. (1 week)

- Send to ERCOT settlements (Settlement Metering Manager) to be put into the ERCOT settlement system and post at http://www.ercot.com/mktinfo/data_agg/index.html

- .  (1/4 day)

3.2	Contingency Database

Contingency Procedure:

- All the TO’s either submit the contingencies individually or will updated the existing database.

- The duplicate contingencies are included only once and are attributed to the TO which comes first in alphabetical order.

- All contingencies need to be categorized based on NERC categories.

- Contingency database is updated every year a month after building DSB cases.

- Current contingency database is sent to all TSP’s for reviewing.

- Once reviewed, updates are made as necessary (Delete, Update or Add contingencies).

- ERCOT will update the contingency database when a TSP submits the contingency changes related to a major Topology change ( - incremental change).Every time the database changes, files in MUST, PSS/E, Powerworld, UPLAN and VSAT formats are posted online.

- Database is sent in either spread sheet or Access mdB format.

### Below are the description of each of the columns in the spreadsheet, and the expectation of updates from TO’s.

- Items

  - Line number of the table, this has no relation to the contingency database.

  - TO’s are requested not to change any data in this column.

- DataBaseID

  - This is the database ID generated automatically when the contingency is extracted from the contingency database.  DataBaseID 2 means this is the 2nd contingency in the database, and it has 5 elements.  Please note that the number is not sequential because some contingency records have been deleted from the database.

  - TO’s are requested not to change any data in this column.

- ERCOTID

  - The column is blank intentionally, this is reserved by ERCOT for future contingency database implementation

  - This column is reserved for ERCOT.

- TOContingencyID

  - This is the ID used internally by TO to identify the contingency.  It is TO specific.

  - TO must use this column to submit new contingencies. This column will be the key identifier for the database to group elements of new contingencies.

  - Once a unique ERCOTID is established this column is optional for all contingencies.

- FromBusNumber_i

  - This is the From Bus Number of elements in contingencies

  - TO’s are requested to verify if the FromBusNumber is correct with respect to a specific contingency.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- ToBusNumber_j

  - This is the To Bus Number of elements in contingencies

  - TO’s are requested to verify if the ToBusNumber is correct with respect to a specific contingency.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- ToBusNumber_k

  - This is the 3rd winding information; it will have data only if it is a 3-winding transformer

  - TO’s are requested to verify if the ToBusNumber is correct with respect to a specific contingency.  If not, please provide correct information.

  - This column is mandatory for all 3 phase transformer contingencies.

- CircuitID

  - This is the Circuit ID of a Branch or transformer

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

- This column is mandatory for all contingencies. Element Identifier

  - This is to specify the type of the element.

  - Example: Bus, Transformer, Branch etc.

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- Submitter

  - This is the abbreviation of TO’s who submit the contingency definition

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- StartDate

  - This is the start date of a specific contingency, defined by month and year

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- StopDate

  - This is the stop date of a specific contingency, defined by month and year

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- DateCreated

  - This is the date a specific contingency is created.  It is intended to be date first imported into the database.

  - There is no action from TO’s.

- UpdatedDate

  - This is the date a specific contingency is being updated.

  - There is no action from TO’s.

- Multi-SectionLine

  - This is to check if the element is a multi-section line.

  - TO’s are requested to verify if the information is correct.  If not, please provide correct information.

  - This column is mandatory for all contingencies.

- NERCCategory

  - This is the information showing which category a specific contingency is in.

  - TO’s are requested to classify contingencies based using NERC contingency definition from the NERC documentation.  It is expected to enter B, C, or D for every contingency.

  - This column is mandatory for all contingencies.

- ERCOTCategory

  - This is the information showing which category a specific contingency is in.

  - TO’s are requested to classify contingencies using definitions from the ERCOT operating guide section 5.1.4.  It is expected to enter ERCOT1 for 5.1.4.1 and, ERCOT2 for 5.1.4.2, for any applicable contingencies.  If it is not applicable, please enter “N/A”.

- TDSPComments

  - This is the comments TDSP would put in for a specific contingency.

  - TO’s are encouraged to enter any comments that are relating to a specific contingency.

  - This column is optional

- ERCOTComment

  - This is the comments ERCOT would put in for a specific contingency.

  - This column is reserved for ERCOT.

- ContingencyName

  - This name is straight from the database.

  - TO’s are encouraged to replace this name with a more meaningful name of a specific contingency.

  - This column is mandatory for all contingencies

APPENDICES

Appendix A

Owner ID, TSP, Bus/Zone Range Table

| BUS RANGE | TSP | ACRONYM | TRAN OWNER (ID) | TSP | PSSE AREA NO | # OF BUS ALLOCATED | ZONE RANGE |  | # OF ZONES ALLOCATED | NERC TP Yes/No | NERC DP Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 - 799 | BRAZOS ELECTRIC POWER COOP. | BEPC | 101 | TMPPA | 11 | 4799 | 7 | 99 | 93 | Yes |  |
| 33000 - 36999 |  |  |  |  |  |  |  |  |  |  |  |
| 860 - 899 | BRYAN, CITY OF | BRYN | 102 | BRYN | 22 | 990 | 2 | 2 | 1 | Yes |  |
| 32050 - 32999 |  |  |  |  |  |  |  |  |  |  |  |
| 900 - 934 | DENTON MUNICIPAL UTILITIES, CITY OF | CODX | 108 | CODX | 19 | 35 | 3 | 3 | 1 | No | Yes |
| 800 - 859 | GARLAND, CITY OF | COGX | 110 | COGX | 20 | 60 | 4 | 4 | 1 | Yes |  |
| 935 - 955 | GREENVILLE ELECTRIC UTILITY SYSTEM | GEUS | 113 | GEUS | 21 | 21 | 5 | 5 | 1 | No | Yes |
| 956 - 999 | TEXAS MUNICIPAL POWER AGENCY | TMPA | 127 | TMPA | 12 | 44 | 6 | 6 | 1 | Yes |  |
| 1000 - 4999 | ONCOR | ONCOR | 130 | ONCOR | 1 | 26000 | 100 | 198 | 99 | Yes |  |
| 10000 - 31999 |  |  |  |  |  |  |  |  |  |  |  |
| 32000 - 32049 | COLLEGE STATION, CITY OF | COCS | 104 | COCS | 23 | 50 | 199 | 199 | 1 | Yes |  |
| 37000 - 39999 | TEXAS NEW MEXICO POWER CO. | TNMP | 128 | TNMP | 17 | 3000 | 220 | 249 | 30 | Yes |  |
| In TNMP | TNMP CUSTOMER | TNMPC | 228 | TNMP |  |  |  |  |  | No TNMP |  |
| 40000 - 49999 | CENTERPOINT | CNPT | 114 | CNPTA | 4 | 10000 | 260 | 319 | 60 | Yes |  |
| 5000 - 5499 | CPS ENERGY | CPST | 107 | CPSTA | 5 | 5500 | 340 | 369 | 30 | Yes |  |
| 50000 - 54999 |  |  |  |  |  |  |  |  |  |  |  |
| 5500 - 5899 | SOUTH TEXAS ELECTRIC COOP. | STEC | 422 | STECA | 13 | 4400 | 869 | 898 | 30 | Yes |  |
| 55000 - 58999 |  |  |  |  |  |  |  |  |  |  |  |
| 5910 - 5919 | SOUTH TEXAS POWER PLANT | STP | 114 | HLPTA | 4 | 10 | 260 | 319 | 60 | No CNPT |  |

Owner ID, TSP, Bus/Zone Range Table (continue)

| BUS RANGE | TSP | ACRONYM | TRAN OWNER (ID) | TSP | PSSE AREA NO | # OF BUS ALLOCATED | ZONE RANGE |  | # OF ZONES ALLOCATED | NERC TP Yes/No | NERC DP Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 5920 - 5929 | EAST HIGH VOLTAGE DC TIE |  |  | AEP | 16 | 10 | 200 | 200 | 1 | No AEPSC | n/a |
| 5930 - 5989 | PUBLIC UTILITY BOARD OF BROWNSVILLE | PUBX | 119 | PUBXA | 15 | 660 | 800 | 829 | 30 | Yes |  |
| 59300 - 59899 |  |  |  |  |  |  |  |  |  |  |  |
| 59900 - 59999 | WIND ENERGY TRANSMISSION TEXAS | WETT | 149 | WETT | 29 | 100 | 590 | 609 | 20 | Yes |  |
| 6000 - 6699 | AMERICAN ELECTRIC POWER- TNC | AEP-TNC | 131 | AEP | 6 | 8700 | 402 | 479 | 78 | No | n/a |
| 60000 - 67999 |  |  |  |  |  |  |  |  |  | AEPSC |  |
| 69000 - 69999 |  |  |  |  |  |  |  |  |  |  |  |
| In AEN-TNC | COLEMAN COUNTY ELECTRIC COOP. | CCEC | 103 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | CONCHO VALLEY ELECTRIC COOP. | CVEC | 105 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | MIDWEST ELECTRIC COOP. | MWEC | 118 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | RIO GRANDE ELECTRIC COOP. | RGEC | 120 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | SOUTHWEST TEXAS ELECTRIC COOP. | SWTE | 123 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | STAMFORD ELECTRIC COOP. | SECX | 124 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | TAYLOR ELECTRIC COOP. | TECX | 125 | AEP |  |  |  |  |  | No AEPSC | n/a |
| 6096 - 6096 | NORTH HIGH VOLTAGE DC |  |  | AEP | 14 | 1 | 394 | 394 | 1 | No AEPSC | n/a |
| 6700 - 6749 | TEX-LA ELECTRIC COOP. | TXLA | 130 | TUETA | 3 | 50 | 177 | 177 | 1 | No | Yes |
| 6800 - 6949 | RAYBURN COUNTRY ELECTRIC COOP. | RCEC | 130 | RCEC | 2 | 150 | 178 | 178 | 1 | No | Yes |

| BUS RANGE | TSP | ACRONYM | TRAN OWNER (ID) | TSP | PSSE AREA NO | # OF BUS ALLOCATED | ZONE RANGE |  | # OF ZONES ALLOCATED | NERC TP Yes/No | NERC DP Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| In RCEC | GRAYSON COUNTY ELECTRIC COOP. | GCEC | 112 | RCEC | 2 | 11 | 178 | 178 | 1 | No | No RCEC |
| In RCEC | LAMAR ELECTRIC COOP. | LCEC | 194 | RCEC | 2 | 39 | 178 | 178 | 1 | No | No RCEC |
| In RCEC | FARMERS ELECTRIC COOP. | FECX | 109 | RCEC | 2 | 40 | 178 | 178 | 1 | No | No RCEC |
| In RCEC | TRINITY VALLEY ELECTRIC COOP. | TVEC | 129 | RCEC | 2 | 10 | 178 | 178 | 1 | No | No RCEC |
| In RCEC | FANNIN COUNTY ELECTRIC COOPERATIVE | FCEC | 148 | RCEC | 2 |  | 178 | 178 | 1 | No | No RCEC |
| 68000 - 69999 | LONE STAR TRANSMISSION | LST | 147 | LST | 27 | 1000 | 670 | 689 | 20 | Yes |  |
| In AEP-TNC | CONCHO VALLEY ELECTRIC COOP. | CVEC | 105 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | MIDWEST ELECTRIC COOP. | MWEC | 118 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | RIO GRANDE ELECTRIC COOP. | RGEC | 120 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | SOUTHWEST TEXAS ELECTRIC COOP. | SWTE | 123 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | STAMFORD ELECTRIC COOP. | SECX | 124 | AEP |  |  |  |  |  | No AEPSC | n/a |
| In AEP-TNC | TAYLOR ELECTRIC COOP. | TECX | 125 | AEP |  |  |  |  |  | No AEPSC | n/a |
| 6096 - 6096 | NORTH HIGH VOLTAGE DC |  |  | AEP | 14 | 1 | 394 | 394 | 1 | No AEPSC | n/a |
| 6700 - 6749 | TEX-LA ELECTRIC COOP. | TXLA | 130 | TUETA | 3 | 50 | 177 | 177 | 1 | No | Yes |

| BUS RANGE | TSP | ACRONYM | TRAN OWNER (ID) | TSP | PSSE AREA NO | # OF BUS ALLOCATED | ZONE RANGE |  | # OF ZONES ALLOCATED | NERC TP Yes/No | NERC DP Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 68000 - 69999 | LONE STAR TRANSMISSION | LST | 147 | LST | 27 | 1000 | 670 | 689 | 20 | Yes |  |
| 7000 – 7899 70000 - 78999 | LOWER COLORADO RIVER AUTHORITY TSC | LCRA TSC | 116 | LCRAA | 7 | 9900 | 500 | 589 | 90 | Yes |  |
| In LCRA TSC | BANDERA ELECTRIC COOP. | BEC | 140 | LCRAA |  |  |  |  |  | Yes |  |
| In LCRA TSC | BLUEBONNET ELECTRIC COOP. | BBEC | 141 | LCRAA |  |  |  |  |  | Yes |  |
| In LCRA TSC | CENTRAL TEXAS ELECTRIC COOP. | CTEC | 142 | LCRAA |  |  |  |  |  | No | Yes LCRA |
| In LCRA TSC | GUADALUPE VALLEY ELECTRIC COOP. | GVEC | 143 | LCRAA |  |  |  |  |  | Yes |  |
| In LCRA TSC | NEW BRAUNFELS UTILITIES | NBU | 144 | LCRAA |  |  |  |  |  | Yes |  |
| In LCRA TSC | PEDERNALES ELECTRIC COOP. | PEC | 145 | LCRAA |  |  |  |  |  | Yes |  |
| In LCRA TSC | SAN BERNARD ELECTRIC COOP. | SBEC | 146 | LCRAA |  |  |  |  |  | Yes |  |
| 7000 - 7899 | SOUTHWESTERN ELECTRIC SERVICE CO. | SESC | 121 | LCRAA | 7 |  | 100 | 199 |  | No LCRA | NO |
| 79000-79100 | CROSS TEXAS TRANSMISSION | CTT | 150 | CTT | 30 | 101 | 790 | 799 | 10 | Yes |  |
| 8000 – 8999 80000 - 89999 | AMERICAN ELECTRIC POWER - TCC | AEP-TCC | 106 | AEP | 8 | 11000 | 610 | 669 | 60 | Yes |  |
| 79500-79599 | SHARYLAND | SHRY | 191 | SHRY | 18 | 100 | 820 | 829 | 10 | Yes |  |
| 9000 – 9399 90000 - 93999 | AUSTIN ENERGY | AENX | 100 | AENXA | 9 | 4400 | 690 | 719 | 30 | Yes |  |

| BUS RANGE | TSP | ACRONYM | TRAN OWNER (ID) | TSP | PSSE AREA NO | # OF BUS ALLOCATED | ZONE RANGE |  | # OF ZONES ALLOCATED | NERC TP Yes/No | NERC DP Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9400-9450 | LYNTEGAR ELECTRIC COOP (Goldenspread) | LYECO | 132 | LYECO | 25 | 50 | 179 | 179 | 1 | No | Yes |
| 9451-9470 | TAYLOR ELECTRIC COOP | TAYECO | 133 | TAYECO | 25 | 19 | 179 | 179 | 1 | No | Yes |
| 9471-9490 | BIG COUNTRY ELECTRIC COOP | BCECO | 135 | BCECO | 25 | 19 | 179 | 179 | 1 | No | Yes |
| 9491-9499 | CITY OF GOLDSMITH | CGECO | 136 | CGECO | 26 | 8 | 180 | 180 | 1 | No | Yes |
| 9500 – 9999 94000 - 99999 | ERCOT SYSTEM PLANNING | ESP |  | ESP |  | 6600 | 900 | 999 | 100 | No N/A |  |
| 5824,5864, 5870,5872 | RIO GRANDE ELECTRIC COOP | RGEC | 126 | RGEC |  |  |  |  |  | No AEPSC |  |
| 600-601 | BRIDGEPORT ELECTRIC | BRPTEC | 195 | BRYN |  | 2 |  |  |  | No BRYN |  |

FACTS Device ID Range Table

| FACTS Device ID# | Ownership claimed by TSP |
| --- | --- |
| 1 - 15 | American Electric Power |
| 16 - 18 | Austin Energy |
| 19 |  |
| 20 - 30 | ONCOR |
| 30 - 34 |  |
| 35 - 39 | Texas New Mexico Power |
| 40 - 50 | Centerpoint Energy |

Description of Zones in base cases

The number of buses and loads come from the 2006 summer peak base case as a reference.

| Zone # | Zone Name | # buses in zone | # loads in zone | Zone Description |
| --- | --- | --- | --- | --- |
| 2 | BRYAN | 39 | 23 | City of Bryan |
| 3 | DENTON | 12 | 12 | Denton Municipal Electric |
| 4 | GARLAND | 45 | 26 | Garland Power and Light |
| 5 | GRNVILLE | 12 | 7 | Greenville Electric Utility System |
| 6 | TMPA | 28 | 3 | Texas Municipal Power Agency |
| 11 | BEPC | 407 | 325 | Brazos Electric Power Coop. |
| 120 | W FALLS | 71 | 41 | ONCOR |
| 121 | EASTLAND | 36 | 20 | ONCOR |
| 124 | COMANCHE | 21 | 9 | ONCOR |
| 125 | MINERL W | 41 | 25 | ONCOR |
| 130 | FT WORTH | 140 | 70 | ONCOR |
| 131 | DFW CENT | 65 | 38 | ONCOR |
| 132 | DALLAS | 332 | 179 | ONCOR |
| 133 | ROANOKE | 70 | 35 | ONCOR |
| 134 | VENUS | 94 | 42 | ONCOR |
| 135 | DAL SUBS | 194 | 101 | ONCOR |
| 140 | GAINESVL | 47 | 24 | ONCOR |
| 141 | PARIS | 64 | 15 | ONCOR |
| 142 | SULPHR S | 32 | 14 | ONCOR |
| 143 | WILLS PT | 19 | 5 | ONCOR |
| 144 | TYLER | 49 | 25 | ONCOR |
| 145 | ATHENS | 32 | 10 | ONCOR |
| 146 | LUFKIN | 36 | 19 | ONCOR |
| 147 | PALESTIN | 51 | 26 | ONCOR |
| 148 | CORSICAN | 53 | 22 | ONCOR |
| 149 | LIMESTON | 21 | 8 | ONCOR |
| 150 | RND ROCK | 38 | 25 | ONCOR |
| 151 | TEMPLE | 23 | 12 | ONCOR |
| 152 | KILLEEN | 16 | 11 | ONCOR |
| 153 | WACO | 74 | 34 | ONCOR |
| 154 | HILLSBOR | 19 | 13 | ONCOR |
| 160 | ODESSA | 123 | 65 | ONCOR |
| 161 | MIDLAND | 45 | 28 | ONCOR |
| 162 | BIG SPRG | 45 | 31 | ONCOR |
| 163 | SWEETWTR | 72 | 34 | ONCOR |
| 177 | TEX-LA | 18 | 18 | TEX-LA Electric Coop |
| 178 | RAYBURN | 89 | 88 | Rayburn Country Electric Coop |
| 199 | COCS | 4 | 4 | City of College Station |
| 200 | EHVDC | 2 | 0 | East High Voltage DC |
| 220 | TNP/CLIF | 16 | 16 | Texas New Mexico Power Co. |
| 221 | TNP/WLSP | 8 | 10 | Texas New Mexico Power Co. |
| 222 | TNP/VROG | 6 | 8 | Texas New Mexico Power Co. |
| 224 | TNP/LEW | 7 | 12 | Texas New Mexico Power Co. |
| 225 | TNP/KTRC | 9 | 12 | Texas New Mexico Power Co. |
| 226 | TNP/BELS | 5 | 4 | Texas New Mexico Power Co. |

Description of Zones in base cases

The number of buses and loads come from the 2006 summer peak base case as a reference.

| Zone # | Zone Name | # buses in zone | # loads in zone | Zone Description |
| --- | --- | --- | --- | --- |
| 227 | TNP/CLMX | 5 | 6 | Texas New Mexico Power Co. |
| 229 | TNP/PMWK | 20 | 22 | Texas New Mexico Power Co. |
| 230 | TNP/TC | 41 | 41 | Texas New Mexico Power Co. |
| 233 | TNP/COGN | 32 | 6 | Texas New Mexico Power Co. |
| 234 | TNP/WC | 11 | 13 | Texas New Mexico Power Co. |
| 235 | TNP/HC-F | 1 | 0 | Texas New Mexico Power Co. |
| 238 | TNP/GEN | 3 | 0 | Texas New Mexico Power Co. |
| 240 | TNP/FS | 17 | 11 | Texas New Mexico Power Co. |
| 260 | CNP/DNTN | 6 | 4 | CenterPoint Energy - Dist Buses in Downtown |
| 261 | CNP/INNR | 5 | 4 | CenterPoint Energy - Dist Buses in Inner City |
| 300 | CNPEXNSS | 38 | 22 | CenterPoint Energy - Exxon Facility self serve |
| 301 | CNP/INDS | 122 | 117 | CenterPoint Energy - Industrial Customers |
| 302 | CNP/COGN | 63 | 15 | CenterPoint Energy - Cogeneration |
| 303 | CNP/SS | 2 | 17 | CenterPoint Energy - Self Serve |
| 304 | CNP/DIST | 360 | 318 | CenterPoint Energy - Distribution |
| 305 | CNP/TGN | 59 | 1 | CenterPoint Energy |
| 306 | CNP/IPP | 37 | 0 | CenterPoint Energy |
| 308 | CNP/GALV | 14 | 7 | CenterPoint Energy |
| 310 | STP | 3 | 0 | South Texas Project |
| 318 | CNP TERTIARY | 2 | 0 | CenterPoint Energy- AUTO TERTIARIES |
| 319 | CNP/LCAP | 24 | 0 | CenterPoint Energy - In Line Capacitor Banks |
| 320 | CNPDOWSS | 37 | 9 | CenterPoint Energy |
| 350 | CPS | 122 | 77 | CPS Energy |
| 391 | WEATHFRD | 0 | 6 | American Electric Power - TNC |
| 393 | TNC/LCRA | 13 | 12 | American Electric Power - TNC |
| 394 | NHVDC | 1 | 0 | North High Voltage DC Tie |
| 402 | WHEARNE | 0 | 1 | American Electric Power - TNC |
| 424 | TRENT | 6 | 4 | American Electric Power - TNC |
| 428 | PUTNAM | 25 | 17 | American Electric Power - TNC |
| 432 | ABILENE | 78 | 38 | American Electric Power - TNC |
| 434 | PECOS | 15 | 9 | American Electric Power - TNC |
| 438 | MCCAMEY | 95 | 50 | American Electric Power - TNC |
| 442 | W CHLDRS | 8 | 5 | American Electric Power - TNC |
| 444 | TUSCOLA | 9 | 10 | American Electric Power - TNC |
| 446 | PADUCAH | 15 | 12 | American Electric Power - TNC |
| 456 | ASPR MNT | 37 | 37 | American Electric Power - TNC |
| 458 | SOUTHERN | 4 | 5 | American Electric Power - TNC |
| 460 | E MUNDAY | 30 | 16 | American Electric Power - TNC |
| 462 | SONORA | 21 | 16 | American Electric Power - TNC |
| 466 | MASON | 25 | 15 | American Electric Power - TNC |
| 472 | PRESIDIO | 18 | 18 | American Electric Power - TNC |
| 474 | SAN ANG | 40 | 23 | American Electric Power - TNC |
| 477 | OKLUNION | 20 | 9 | American Electric Power - TNC |
| 478 | CEDR HIL | 31 | 19 | American Electric Power - TNC |
| 479 | BALLINGR | 30 | 28 | American Electric Power - TNC |

Description of Zones in base cases

The number of buses and loads come from the 2006 summer peak base case as a reference.

| Zone # |  | Zone Name |  | # buses in zone |  | # loads in zone |  |  | Zone Description |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 500 |  | AUSTIN |  | 9 |  | 5 |  |  | Lower Colorado River Authority |  |
| 502 |  | BANDERA |  | 9 |  | 8 |  |  | Lower Colorado River Authority |  |
| 504 |  | BASTROP |  | 30 |  | 15 |  |  | Lower Colorado River Authority |  |
| 506 |  | BLANCO |  | 8 |  | 3 |  |  | Lower Colorado River Authority |  |
| 507 |  | BROWN |  | 1 |  | 1 |  |  | Lower Colorado River Authority |  |
| 508 |  | BURLESON |  | 2 |  | 2 |  |  | Lower Colorado River Authority |  |
| 510 |  | BURNET |  | 20 |  | 11 |  |  | Lower Colorado River Authority |  |
| 512 |  | CALDWELL |  | 12 |  | 12 |  |  | Lower Colorado River Authority |  |
| 514 |  | COLORADO |  | 15 |  | 10 |  |  | Lower Colorado River Authority |  |
| 516 |  | COMAL |  | 21 |  | 16 |  |  | Lower Colorado River Authority |  |
| 522 |  | CULBRSON |  | 2 |  | 0 |  |  | Lower Colorado River Authority |  |
| 525 |  | DEWITT |  | 5 |  | 6 |  |  | Lower Colorado River Authority |  |
| 528 |  | FAYETTE |  | 23 |  | 16 |  |  | Lower Colorado River Authority |  |
| 531 |  | GILESPIE |  | 12 |  | 8 |  |  | Lower Colorado River Authority |  |
| 534 |  | GOLIAD |  | 1 |  | 1 |  |  | Lower Colorado River Authority |  |
| 537 |  | GONZALES |  | 14 |  | 11 |  |  | Lower Colorado River Authority |  |
| 540 |  | GUADLUPE |  | 37 |  | 17 |  |  | Lower Colorado River Authority |  |
| 543 |  | HAYS |  | 30 |  | 22 |  |  | Lower Colorado River Authority |  |
| 546 |  | KENDALL |  | 12 |  | 9 |  |  | Lower Colorado River Authority |  |
| 549 |  | KERR |  | 13 |  | 13 |  |  | Lower Colorado River Authority |  |
| 555 |  | LAMPASAS |  | 7 |  | 7 |  |  | Lower Colorado River Authority |  |
| 558 |  | LAVACA |  | 7 |  | 7 |  |  | Lower Colorado River Authority |  |
| 561 |  | LEE |  | 2 |  | 4 |  |  | Lower Colorado River Authority |  |
| 564 |  | LLANO |  | 22 |  | 10 |  |  | Lower Colorado River Authority |  |
| 575 |  | MILLS |  | 2 |  | 2 |  |  | Lower Colorado River Authority |  |
| 577 |  | REAL |  | 1 |  | 3 |  |  | Lower Colorado River Authority |  |
| 579 |  | SAN SABA |  | 4 |  | 3 |  |  | Lower Colorado River Authority |  |
| 581 |  | TRAVIS |  | 31 |  | 12 |  |  | Lower Colorado River Authority |  |
| 583 |  | WALLER |  | 6 |  | 6 |  |  | Lower Colorado River Authority |  |
| 585 |  | WSHNGTON |  | 12 |  | 7 |  |  | Lower Colorado River Authority |  |
| 587 |  | WILLMSON |  | 16 |  | 16 |  |  | Lower Colorado River Authority |  |
| 589 |  | WILSON |  | 2 |  | 2 |  |  | Lower Colorado River Authority |  |
| 590 |  | BORDEN |  | 1 |  | 0 |  |  | Wind Energy Transmission Texas |  |
| 591 |  | MARTIN |  | 1 |  | 0 |  |  | Wind Energy Transmission Texas |  |
| 592 |  | STERLING |  | 1 |  | 0 |  |  | Wind Energy Transmission Texas |  |
| 593 |  | GLASSCOCK |  | 1 |  | 0 |  |  | Wind Energy Transmission Texas |  |
| 594 |  | DICKENS |  | 1 |  | 0 |  |  | Wind Energy Transmission Texas |  |
| 610 |  | E VALLEY |  | 39 |  | 33 |  |  | American Electric Power - TCC |  |
| 611 |  | TCCSWIND |  |  |  |  |  |  | American Electric Power - TCC |  |
| 615 |  | W VALLEY |  | 66 |  | 54 |  |  | American Electric Power - TCC |  |
| 620 |  | N REGION |  | 113 |  | 91 |  |  | American Electric Power - TCC |  |
| 621 |  | TCCNWIND |  |  |  |  |  |  | American Electric Power - TCC |  |
| 625 |  | C REGION |  | 104 |  | 85 |  |  | American Electric Power - TCC |  |
| 626 |  | TCCCWIND |  |  |  |  |  |  | American Electric Power - TCC |  |
| 630 |  | W REGION |  | 54 |  | 49 |  |  | American Electric Power - TCC |  |
| 631 |  | TCCWWIND |  |  |  |  |  |  | American Electric Power - TCC |  |
| 635 |  | LAREDO |  | 27 |  | 21 |  |  | American Electric Power - TCC |  |
| 636 |  | TRIANGLE |  | 20 |  | 14 |  |  | American Electric Power - TCC |  |
| 640 |  | NORTH LI |  | 25 |  | 19 |  |  | American Electric Power - TCC |  |
| 645 |  | CENT LI |  | 27 |  | 22 |  |  | American Electric Power - TCC |  |
| 650 |  | NR COGEN |  | 15 |  | 10 |  |  | American Electric Power - TCC |  |
| 651 |  | CR COGEN |  | 8 |  | 0 |  |  | American Electric Power - TCC |  |
| 656 |  | TCC/RGEC |  | 2 |  | 2 |  |  | American Electric Power - TCC |  |

Description of Zones in base cases

The number of buses and loads come from the 2006 summer peak base case as a reference.

| Zone # | Zone Name | # buses in zone | # loads in zone | Zone Description |
| --- | --- | --- | --- | --- |
| 658 | TCC/LCRA | 2 | 3 | American Electric Power - TCC |
| 659 | TCC/MEC | 2 | 3 | American Electric Power - TCC |
| 660 | DAV#1GEN | 1 | 0 | American Electric Power - TCC |
| 661 | ROBSTOWN | 0 | 2 | American Electric Power - TCC |
| 662 | KIMBLE | 1 | 1 | American Electric Power - TCC |
| 670 | SHACKELFORD | 1 | 0 | Lone Star Transmission |
| 672 | EAST_LAND | 4 | 0 | Lone Star Transmission |
| 675 | BOSQUE | 4 | 0 | Lone Star Transmission |
| 688 | HILL | 1 | 0 | Lone Star Transmission |
| 689 | NAVARRO | 1 | 0 | Lone Star Transmission |
| 691 | BAST-AEU | 1 | 0 | Austin Energy |
| 692 | CALD-AEU | 2 | 0 | Austin Energy |
| 695 | FAYE-AEU | 1 | 0 | Austin Energy |
| 709 | TRAV-AEU | 93 | 58 | Austin Energy |
| 712 | WILL-AEU | 2 | 2 | Austin Energy |
| 790 | GRAY | 1 | 0 | Cross Texas Transmission |
| 791 | SCOMP | 2 | 0 | Cross Texas Transmission |
| 800 | BPUB | 22 | 13 | Public Utility Board of Brownsville |
| 870 | MEC | 51 | 29 | Medina Electric Coop |
| 875 | MVEC/E | 12 | 12 | South Texas Electric Coop - Eastern Magic Valley |
| 876 | MVEC/W | 19 | 19 | South Texas Electric Coop - Western Magic Valley |

| 890 | STEC | 132 | 78 | South Texas Electric Coop except Magic Valley and Medina |
| --- | --- | --- | --- | --- |

Appendix B

Glossary of Terms

ALDR	Annual Load Data Request

BUS	A node representing point of electrical connection, such as substation or radial tap point.

CSC	Commercially Significant Constraint

ECO	Economically Dispatched

ERCOT	Electric Reliability Council of Texas

ESP	ERCOT System Planning

IPP	Independent power producer

LSE	Load serving entity

LTC	Load tap changing transformer

MLSE	Most limiting series element

MSL	Multi-section line

NERC	North American Electric Reliability Corporation

NESC	National Electric Safety Code

NOIE	Non-opt-in Entity

NUG	Non Utility Generator

PUCT	Public Utility Commission of Texas

QSE	Qualified Scheduling Entity

REP	Retail Electric Provider

SSWG	Steady State Working Group

TPIT	Transmission Project Information Tracking

TSP	Transmission Service Provider

VCRP	Voltage control and reactive planning

Zone	A predefined sub-system within a load-flow case.

MOD 	Model on Demand

IMM	Information Model Manager

Appendix C

TSP Impedance and Line Ratings Assumptions

Each TDSP has their own set of

design parameters and assumptions, if the TSP is

not

listed here, then  contact them for their methodology.

Texas-New Mexico Power Company

Conductor Ratings

Conductor thermal ratings for existing transmission lines are calculated by the IEEE method detailed in ANSI/IEEE Standard 738 with the following input parameters:

Latitude  = 30 N

Wind Velocity  = 2 feet per second

Wind Angle = 90° to conductor

Emissivity Coefficient  = 0.5

Solar Absorption Coefficient  = 0.5

Line Elevation  = 600 feet AMSL

Line Orientation  = East – West

Time of Day   = 2 P.M.

Atmospheric Condition  = Clear

Air Temperature  = 25 C

Conductor Temperature  = 75 C

New transmission lines will be designed using the above parameters to calculate load capacity, except that Ambient Temperature will be 38C, and Conductor Temperature will be 100C. In cases where ACSS conductor is installed, Ambient Temperature of 38C and Conductor Temperature of 200C will be used.

The 2-hour rating of the conductor of an existing line is the conductor thermal rating based on a conductor temperature of 75C unless it has been determined that the conductor can operate at a higher temperature and maintain adequate clearance. No allowance is made for design or operational thermal limits such as conductor sag or for circuit elements other than the transmission line conductor.

Line Ratings

Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the rating of a transmission line is the conductor rating. Where such equipment has a manufacturer's continuous current rating less than the conductor rating, then that equipment continuous rating shall be used for the rating of the transmission line.

Transformer Ratings

The continuous rating of a transformer is the manufacturer’s highest continuous FA rating at 55C rise.

The 2-hour rating of a transformer is the manufacturer’s highest continuous FA rating at 65C rise.

Line Constants

Line impedance constants are calculated in a TNMP developed Transmission Line Impedance Calculation spreadsheet-using formulas detailed in the Electrical Transmission and Distribution Reference Book by Westinghouse (T&D Reference Book).  Factors used in the calculations are:

- Conductor characteristic data from T&D Reference Book, Electrical Conductor Handbook, or manufacturer's data sheets

- Tower or pole and conductor configuration information

- Actual length of line with no allowance for sag

- Earth resistivity = 100 ohm-meters

- Frequency = 60 Hz

- Ground wires are included in zero sequence impedance calculations

Transformer Constants

Transformer impedance is calculated using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer's test results data to resistance and reactance values on the required per-unit base.

CPS Energy

Transmission line impedance and facility rating assumptions and methodology are specified in internal CPS Energy documentation.  This documentation is available upon request.

Lower Colorado River Authority TSC

LCRA TSC’s impedance and ratings methodology for its transmission facilities are available upon request.

Austin Energy

Line Constants

Austin Energy uses PTI’s Transmission Line Characteristics program (TMLC) to calculate the line constants. TMLC accepts input data either interactively or from an ASCII text file. The program requires (1) conductor sag and tower configuration data, (2) conductor characteristic data, (3) the phase location on the tower.

Assumptions used to make the line constant calculations:

Earth resistivity is 100 ohm-meters.

#### Frequency is 60 Hz

The conductor names follow the standard convention such as Drake, Rail or Puffin, as described in the Aluminum Association Electrical Conductor Handbook.

#### Conductor temperature used for calculating impedance: 50C

Typical conductor data used:

Resistance (Rac and Rdc), inductive reactance, capacitive reactance and conductor rating.

Data comes from the Electrical Conductor Handbook and Electrical T&D Reference Book.

The calculation includes ground wires in the calculations.

The actual tower configuration is used in the calculations.

The actual length of line is used in the calculations.

The conductor sag is included in calculation and it is determined graphically.

Transformer Constants Austin Energy uses either the transformer test report data or the manufacturer specification sheets data.

Assumptions used to make the calculations:

### Frequency is 60 Hz

Temperature used for calculating impedance: 75-85C

### Typical transformer data: resistance, reactance are used in the calculations

Data comes from transformer test reports

Ratings Calculation

Line Branches

Austin Energy utilizes the ampacity table developed by the Southwire Company Overhead Conductor Manual 2nd ed for the transmission line ratings. For the equipment at the substation termination, Austin Energy uses the nameplate ratings for the circuit breakers and the new re-rated ratings for other equipment such as switches, jumpers, and wave traps.

Assumptions used for normal and emergency ratings.

# For ACSR conductors: Emergency rating at 100C, normal rating set at 90% of emergency rating.

For ACSS conductors: Emergency rating at 200C, normal rating set at 90% of emergency rating.

Normal line ratings are calculated using 40C ambient temperature.

Wind speed = 2 feet/second with sun.

Frequency of operation = 60 Hz.

Solar absorption/emissivity = 0.5

Wave traps, current transformers and load switches can be loaded to the normal rating under normal conditions and can be loaded to the emergency rating under contingency conditions.

The normal rating of the most limiting series element (Rate A) is applied under normal condition, and the emergency rating of the most limiting series element (Rate B) is applied under contingency condition.

## Transformers Branches

Emergency transformer rating is specified as 100% of manufacturer’s nameplate FA or FOA rating at 65C rise, at an ambient temperature of 20C.  Normal transformer ratings are specified as 100% of the emergency transformer rating.

The normal and emergency ratings are good forever.

The newer 345/138 kV autotransformers have FA ratings.

The older autotransformers have FOA ratings.

Under normal conditions, the loading of the transmission lines and transformers should be less than the normal ratings, while under contingencies; the loading has to be 100% or less of the emergency ratings.  If the loading exceeds the ratings, operational fixes or transmission additions are considered.

South Texas Electric Cooperative, Inc.

Calculations made with IEEE Rate temp DOS program.

Standard assumptions:

Earth resistivity is 100 -meters

Frequency is 60 Hz

The conductor names follow the standard convention, such as Drake & Penguin

Typical data (resistance, reactance) from “Southwire Company Overhead Conductor Manual”

Conductor length based on Surveyed Horizontal Plane Distances

Standard Voltage (69kV, 138kV, 345kV, etc.)

Actual tower configurations provide values of conductor, bundling, and ground wire spacing

Rating Descriptions:

- Normal = 90% of 1.36mph wind, 102 deg ambient temp, 100 deg C conductor, Time 1400 - 1600, Clear skies

- Emergency (2 hour) = 1.36 mph wind, 102 deg C ambient, 100 deg C conductor, Time 1400-1600, Clear Skies

- Emergency 15 Minute = Capacity for 15 minutes with Normal (A) pre loading

Normal Conditions set are:

Wind Direction (from line)			90 degrees

Location Latitude				29 degrees

Local Sun Time				2 P.M.

Line Direction				North/South

Line Elevation				200 ft

Coefficient of Emissivity			0.5

Coefficient of Solar Absorption		0.5

TYPICAL CONDUCTOR THERMAL RATINGS

| Conductor | Design Temp | Normal Rating |  | Emergency Rating |  | 15 Min. Rating |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Degrees C | 69 kV | 138 kV | 69 kV | 138 kV | 69 kV | 138 kV |
|  |  | MVA | MVA | MVA | MVA | MVA | MVA |
| 4/0 ACSR | 75 | 32 |  | 35 |  | 36 |  |
| 4/0 ACSR | 100 | 40 |  | 45 |  | 45 |  |
| 336 ACSR | 100 | 62 |  | 69 |  | 70 |  |
| 477 ACSR | 100 | 78 | 156 | 87 | 173 | 89 | 177 |
| 795 ACSR | 75 |  | 161 |  | 178 |  | 186 |
| 795 ACSR | 100 | 110 | 216 | 122 | 240 | 127 | 251 |
| 1590 ACSR | 100 |  | 325 |  | 361 |  | 389 |

Notes:

The 69kV STEC lines built in the 1960s met the NESC & RUS codes at that time which specified a minimum ground clearance at 120 degrees F.  The codes then changed to include minimum ground clearances regardless of temperature. STEC then built some lines that reached minimum clearances at 75 degrees C.  New lines are designed to meet the minimum ground clearances at 100 degrees C.

Autotransformer MVA Ratings

1. Normal rating:	Manufacturer’s FOA rating at 55o C rise.

2. Emergency rating:	Manufacturer’s FOA rating at 65o C rise.

Current Transformer Ratings

1.  Normal rating:	90% of manufacturer’s specified rating.

2.  Emergency rating:	100% of manufacturer’s specified rating.

ONCOR

ONCOR Electric Line Constants calculation

ONCOR Electric uses the APSEN Line Constants Program for calculating Line Impedance.  The ASPEN program consists of two modules, the ASPEN Construction module and the Lines Construction module.  The Construction Module contains tower configuration data for each right-of-way in a system.  This data consists of tower spacing, sag, bundle separation (if applicable) and conductor type.  The Lines Construction module is where the point-to-point line section is constructed.  For each line section the mileage data is entered and a tower configuration from the Construction Module is referenced for calculating the impedance.  The ONCOR system consists of 621 lines (breaker to breaker) with 3373 total sections.  Calculations are performed with the following constants:

Earth resistivity	100 ohms-meter

Frequency		60 Hz

Conductor Temp	50 °C

Ground wires are included in the calculations

Typical sag is assumed for each voltage level.

22.52 feet for 345 kV

13.33 feet for 138 kV

8.92 feet for 69 kV

Conductor data (resistance, reactance, and outside diameter) is taken from the EPRI Transmission Line Reference book.

Transformer Constants

Transformer impedance is calculated when possible using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer's test results data to resistance and reactance values on the required per-unit base.  If actual data is not available, typical data from similar transformers in the system is used.

Conductor Ratings

Conductor ampere ratings are calculated by the IEEE method detailed in ANSI/IEEE Standard 738-86 with the following input parameters:

Wind speed: 2 feet per second normal to conductor

Line orientation: North – South

Coefficient of emissivity: 0.5

Coefficient of solar absorption: 0.5

Line elevation above sea level: 600 feet

Local sun time: 2:00 PM.

Ambient temperature: 40°C

Conductor temperature: 90°C

Line latitude: 32° north

Atmospheric conditions: clear

ONCOR does not use a normal rating for transmission lines.  Normal loadings up to the emergency rating are acceptable on a continuous basis.   Some ONCOR transmission lines are designed to operate with a conductor temperature greater than 90°C.   Each line is rated using the ambient assumptions defined earlier and the maximum conductor temperature unique to that line.

The short-term emergency rating is the maximum current carrying capacity of the conductor for a short duration with acceptable line clearance.  For overhead transmission conductor it is 110% of the ampacity of the conductor at 90oC if the line has been surveyed and cleared for operating at a higher temperature for a short duration and the nameplate rating of the switches, breakers and current traps is greater than or equal to 110% of the conductor rating.  For underground transmission conductor the emergency rating is 300 hours of emergency operation at 100°C.

Line Ratings

The maximum overall rating of a transmission line is the current carrying capability of the most limiting element in series between the breakers at its two end points.  Unless otherwise limited by equipment installed in the transmission line such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the emergency rating of a transmission line is the conductor emergency rating.  Where such equipment has a manufacturer's nameplate continuous current rating less than the conductor emergency rating, then that equipment’s continuous rating shall be used for the emergency rating of the transmission line.

Transformer Ratings

Both normal and emergency ratings are calculated in accordance with either ANSI/IEEE Standard C57.92 (1981) or IEEE Standard 756-1984.  Both summer and winter ratings are based upon appropriate daily load and ambient temperature cycles.

Normal ratings are based upon no reduction in normally expected transformer life.

Emergency ratings are based upon the occurrence of two or three long-duration (months) or multiple short-duration (days) contingencies affecting the life of a transformer.  They recognize a hottest spot limit to prevent bubble evolution and a limitation in the loss of transformer expected life of no more than 0.2% per daily load cycle.  (Tests indicate that bubble evolution may occur in operating power transformer at temperatures of 140°C and above; however, a maximum emergency hottest spot temperature of 135°C is used for planning purposes to allow for abnormally high daily loads and/or ambient temperatures.)

Limiting temperatures in degrees C are as follows:

Maximum Hottest Spot

Rated Rise	Top Oil	Normal	Emergency

55		   100		   105		     135

65		   110		   120		     135

Summer Ambient – 40o C

# TMPA Line and Equipment Ratings

Transmission Line Conductor        Emergency ratings are based on 25o C ambient, 75o C

Conductor temperature, 1.4 mph wind, sun.

Normal ratings are 90% of the emergency rating.

Autotransformer MVA Ratings

- Normal rating:  Manufacturer FOA rating at 55o C rise.

- Emergency rating:  Manufacturer FOA rating at 65 o C rise.

Current Transformer Ratings

Normal rating:  90% of manufacturer specified rating.

Emergency rating:  100% of manufacturer specified rating.

Substation Bus and Equipment Normal Voltage Ratings

69 kV:  65.55 kV – 72.45 kV

- 138 kV:  131.10 kV – 144.9 kV

- 345 kV:  327.75 – 362.25 kV

Oil and Gas Circuit Breaker Current Ratings

- Normal rating:  90% of manufacturer specified rating.

Emergency rating:  100% of manufacturer specified rating.

City of Garland

Line Constants:

IEEE Transactions on Power Apparatus and System Textbook

Earth resistivity is 100 ohms-meter

Frequency is 60 Hz

Sag--tests were done assuming no sag, and assuming a reasonable sag value, equal in all phases and in the ground wires

Manufacturers’ data: resistance and reactance per phase per mile

Actual length of lines

Actual tower configurations

Ground wires assumed to be segmented

Line Ratings Methodology: The maximum overall rating of a transmission line is the current capability of the most elements in series between its two end points. Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, switches, disconnects, wave traps, jumpers, current transformers, etc. The normal and emergency ratings of a transmission line are the conductor normal and emergency ratings.

The transmission line ratings are calculated from a program that uses the IEEE Standard for Calculation of Bare Overhead Conductor. Conductor characteristics are taken from the Aluminum Association Electrical Conductor Handbook. Loading levels are tolerated until 100% of rating. Begin taking action at 90% of rating. Assumptions used to make normal and emergency calculations:

Ambient temperature: 40oC

Conductor temperature: 90oC

Wind speed: 2 feet per second

Emissivity coefficient: 0.5

Solar absorption coefficient: 0.5

Line orientation: North-South

Line elevation above sea level: 600 feet

Line latitude: 32o north

Atmospheric condition: clear

Time of day: 2 PM

| Typical conductor information |  |  |  |
| --- | --- | --- | --- |
| No. | Capacity Rating at Voltage | Type | Stranding |
| 1 | 218MW @ 138kV | 795 ACSR | 26/7 |
| 2 | 110MW @ 69kV | 795 ACSR | 26/7 |
| 3 | 77MW @ 69kV | 477 ACSR | 26/7 |
| 4 | 60MW @ 69kV | 336 ACSR | 26/7 |
| 5 | 87MW @ 69kV | 556 ACSR | 26/7 |
| 6 | 174MW @ 138kV | 556 ACSR | 26/7 |
| 7 | 314MW @ 138kV | 556 ACSS | 26/7 |
| 8 | 110MW @ 69kV | 954 ACSR | 54/7 |
| 9 | 40MW @ 69kV | 1/0 ACSR | 6/1 |
| 10 | 58MW @ 138kV | 1/0 ACSR | 6/1 |
| 11 | 157MW @ 69kV | 556 SSAC | 26/7 |

Transformer Constants:

Use manufacturer actual nameplate data.

City of Denton

The city of Denton owns only 69kV transmission lines and no transmission voltage transformers.  Little historical information is available to indicate the exact methodology used in developing impedance date for the 69kV lines.  It appears that the data was developed in the early 1980s using the Westinghouse method.  These values were apparently verified, or at least accepted, by TMPA.  The values developed are still in use in analytical programs.  Line impedance data for line construction or line rebuilds will be developed using the ASPEN program.  Evaluation of the potential effect of proposed conductor size changes indicate that the impedance values in use are within reason.  Data for all line sections will be reviewed in the future and documentation prepared to describe methodology.

Line Ratings

The 50 C conductor ratings are used as the normal and the emergency ratings for existing lines.  Almost all transmission lines are under built with one or two distribution circuits.  This limits the amount of sag that can be tolerated.  Specific historical design information is not available to use in evaluating potential ratings.  Studies will be undertaken as needed to determine possible increases in ratings.  New lines will be designed for 100 C operation.

# Brownsville Public Utilities Board

Line Constants Line impedance constants are calculated using formulas detailed in the Electrical Transmission and Distribution Reference Book by Westinghouse (T&D Reference Book).  Factors used in the calculations are:

- Conductor characteristic data from T&D Reference Book, Electrical Conductor Handbook, or manufacturer's data sheets

- Tower or pole and conductor configuration information

- Actual length of line with no allowance for sag

- Earth resistivity = 100 ohm-meters

- Frequency = 60 Hz

- Ground wires are included in zero sequence impedance calculations

Transformer Constants

Transformer impedance is calculated using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer’s test results data to resistance and reactance values on the required per-unit base. If it is not available, PUB will use typical data from similar transformers.

Conductor Ratings

Conductor thermal ratings are calculated using the IEEE method detailed in ANSI/IEEE Standard 738 with the following input parameters:

Latitude  = 30 N

Wind velocity  = 2 feet per second

Wind angle = 90° to conductor

Emissivity coefficient  = 0.5

Solar absorption coefficient  = 0.5

Line elevation  = 600 feet AMSL

Line orientation  = East – West

Time of day   = 2 P.M.

Atmospheric condition  = Clear

Air temperature  = 25 C

Conductor temperature  = 75 C

The normal rating is 100% of the conductor thermal rating. The emergency rating of the conductor is 110% of the conductor thermal rating. No allowance is made for design or operational thermal limits such as conductor sag or for circuit elements other than the transmission line conductor.

Line Ratings

The maximum overall rating of a transmission line is the current capability of the most limiting element in series between its two end points. Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the normal and emergency rating of a transmission line is the conductor normal and emergency ratings.

Transformer Ratings

The normal rating of a transformer is the manufacturer’s highest continuous FA rating at 55C rise.

The emergency rating of a transformer is the manufacturer’s highest continuous FA rating at 65C rise.

# Bryan Texas Utilities’ Facility Ratings Calculations

Line Constants Calculations

BTU uses PTI’s Line Constants program (LineProp30) to calculate line constants.  The program requires conductor sag and tower configuration data, conductor sag data, conductor characteristic data, and the phase location on the structure relative to earth.

The following assumptions are used to make calculations:

- Earth resistivity is 100 ohm-meters.

- Frequency is 60 Hz

Conductor names follow the standard convention such as Drake (795ACSR), Arbutus (795AAC), etc., as described in the Aluminum Association’s Electrical Conductor Handbook.

Conductor temperature used for calculating impedance is 25C

The calculation includes:

- The effect of overhead grounded shield wires,

- Tower configuration, and

- The length of line.

Transformer Constants Calculations

BTU uses either the manufacturer’s transformer test report data the manufacturer’s specification sheets or, if neither is available, industry-accepted values based on the transformer’s size and type.

Rating Calculations

Line Segments

The maximum overall rating of a transmission line is the current capability of the most limiting element in series between its two end points. Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, etc. the normal and emergency rating of a transmission line is the conductor normal and emergency ratings.

BTU utilizes the ampacity program SWRATE16, Version 2.05 developed by the Southwire Company for transmission line ratings.

For the equipment at the substation termination, BTU uses the nameplate ratings for equipment such as circuit breakers, switches, jumpers, and wave traps.

Assumptions used for ACSR and AAC conductor’s normal and emergency ratings are:

- Emergency rating at 100C,

- Normal rating set at 90% of emergency rating.

Conductor thermal ratings are calculated using the IEEE methodology described in IEEE 738 with the following input parameters into the SWRATE16 software:

- Conductor code name (Conductor code names follow the standard convention described under Line Constants Calculations)

- 40C air temperature.

- Wind speed of 2 feet/second at a 90 angle relative to the conductor.

- Latitude of BTU is 30N

- Elevation is 300 feet above mean sea level.

- Frequency of operation is 60 Hz.

- Coefficient of emissivity is 0.5

- Coefficient of solar absorption is 0.5

Current transformers and switches can be loaded to the normal rating under normal conditions and to the emergency rating under contingency conditions.

The normal rating of the MLSE is applied under normal conditions, and the emergency rating of the MLSE is applied under contingency conditions.

Transformers

BTU’s emergency rating for transformers is 100% of manufacturer’s nameplate FA or FOA rating at 65C rise, at an ambient temperature of 20C.  Normal transformer ratings are specified as 90% of the emergency transformer rating.

American Electric Power Service Corporation (AEPSC)

Line Constants Calculation

AEPSC uses actual transformer test data in calculating the transformer’s impedance. When actual test data is not available, engineering assumptions and nameplate data are employed to determine the impedance that will be used in modeling the transformers in AEPSC/ERCOT load-flow cases.

American Electric Power Service Corporation (AEPSC)) uses a Transmission Line Constants program (TLC) that was developed by Electric Power Research Institute (EPRI) in 1981 that computes electrical transmission parameters. Inputs to the program are collected from manufacturer’s test reports and data collected from the field and used conjunction with industry-accepted methods to calculate the modeling data required in the AEPSC/ERCOT load-flow cases.

Input Data / Assumptions

- Nominal Operating Voltages 69kV and above

- Structure geometry, tower height, including shield wire

- Conductor length – breaker to breaker

- Conductor characteristics geometric mean radius, conductor radius, resistance, reactance, etc.

- Frequency 60 Hz

- Earth resistivity – Depending on soil type ranges from 1 – 50 ohms-meter

- Data is obtained from the manufacture or; the Electrical Transmission and Distribution Reference Book, prepared by Westinghouse Electric Corporation or; EPRI’s Transmission Line Reference Book, 345 kV and Above/ Second Edition

The EPRI program and input data are used to calculate various impedances at 50o C including: Resistance, Reactance, Charging; Sequence Series Impedances; Shunt Admittance; and Mutual Impedances.

# American Electric Power Service Corporation Facility Ratings Calculations

In determining the thermal facility ratings of 69 kV and above, AEPSC incorporates Good Utility Practice with actual field data to ensure that the transmission system is in compliance with the ERCOT Reliability Criteria, AEPSC Transmission Planning Reliability Criteria, and North American Reliability Council (NERC).

Transmission Lines

- Existing transmission lines were designed to meet operating standards that were in effect at the time the line was built. The National Electric Safety Code (NESC) specified acceptable ground clearances are maintained while allowing for loss of conductor tensile strength. AEP will use thermal ratings that are consistent with the NESC design being practiced at the time the line was built.

- Lines are rated in accordance with the AEP’s System Planning Guidelines.  The normal and emergency thermal rating for generic pre 1977 lines is based on an operating temperature of 85o C.  The normal rating for generic post 1977 lines is based on a normal operating temperature of 85o C and an emergency operating temperature of 95o C.  Lines with documented sag information have an emergency rating based on the maximum operating temperatures a normal rating based on an operating temperature of 95o C.

- Other assumptions used in calculating the ratings of AEP transmission lines include:

| Wind Speed | 2 MPH (2.93 fps) |
| --- | --- |
| Wind angle to line | 60 degrees |
| Emissivity | 0.8 |
| Absorptivity | 0.8 |
| Summer Ambient Temperature | 40o C |
| Winter Ambient Temperature | 20o C |

- AEP’s transmission lines can operate at the emergency ratings for 1000 hours over the life of the conductor before the loss of strength will cause unacceptable sag conditions.  In accordance with this procedure manual, The Emergency Rating represents a 2-hour rating.  Operations must take action to reduce the flows below the conductor’s normal ratings within 2 hours for each occurrence.

- Disconnect Switches - Normal and emergency rating shall be 100% of nameplate rating.

- Wave Traps - Emergency rating shall be 110% of nameplate rating.

- Current Transformers - Normal rating shall be 100% of nameplate rating adjusted for the continuous thermal current rating factor.  The Emergency Rating shall be 110% of the Normal rating.

- Circuit Breakers - Normal and emergency rating shall be 100% of nameplate rating.

Autotransformers

- The normal rating for autotransformers shall be its top nameplate rating, including the effects of forced cooling equipment if it is available. The emergency rating for autotransformers shall be 110% of its top nameplate rating for the first two hours of emergency and 100% thereafter. Alternatively, transformer normal and emergency ratings may be calculated from test data, configuration and past history.

- The circuit thermal capabilities should be reduced to the ratings of the “Most Limiting Series Element” (MLSE) as described in the NERC Reliability Standards. This includes but is not limited to substation terminal equipment; disconnect switches, wave traps, current transformers, and circuit breakers.

AEPSC uses the above describe assumptions, standards, and good utility practice in determining and applying the facility ratings described in section 1.5.1.4.1 Ratings Definitions for modeling criteria.

Rayburn County Electric Cooperative, Inc.

| RAYBURN COUNTRY ELECTRIC COOPERATIVE, INC. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rockwall, Texas |  |  |  |  |  |  |  |  |  |  |  |
| Ampere Rating per Westinghouse T&D Manual |  |  |  |  |  |  |  |  |  |  |  |
| October 31, 2002 |  | SUMMER BASE LOADING LEVEL |  |  |  | SUMMER MAXIMUM PLANNING LEVEL |  |  | SUMMER MAXIMUM EMERGENCY (Short Term) |  |  |
|  |  | kVA |  | kVA |  | kVA | kVA |  | kVA | kVA |  |
| Designation | Conductor | @ 69kV |  | @ 138kV |  | @ 69kV | @ 138kV |  | @ 69kV | @ 138kV |  |
|  |  | 110° F Ambient, 167° F Conductor (43° C/75° C) |  |  |  | 110° F Ambient, 202° F Conductor (43° C/95° C) |  |  | 110° F Ambient, 212° F Conductor (43° C/100° C) |  |  |
| Single Conductor |  |  |  |  |  |  |  |  |  |  |  |
| RAVEN | 1/0 ACSR | 21,600 |  |  | 43,300 | 27,500 |  | 55,000 | 28,800 |  | 57,600 |
| QUAIL | 2/0 ACSR | 25,300 |  |  | 50,700 | 32,300 |  | 64,500 | 33,800 |  | 67,600 |
| PIGEON | 3/0 ACSR | 28,200 |  |  | 56,400 | 35,900 |  | 71,700 | 37,500 |  | 75,100 |
| PENGUIN | 4/0 ACSR | 32,000 |  |  | 64,100 | 40,600 |  | 81,300 | 42,500 |  | 85,100 |
| LINNET | 336 kCM ACSR | 49,800 |  |  | 99,700 | 63,300 |  | 126,700 | 66,300 |  | 132,700 |
| IBIS | 397 kCM ACSR | 55,500 |  |  | 110,900 | 70,500 |  | 141,000 | 73,900 |  | 147,700 |
| HAWK | 477 kCM ACSR | 63,000 |  |  | 126,000 | 80,100 |  | 160,100 | 83,900 |  | 167,800 |
| DOVE | 556 kCM ACSR | 68,600 |  |  | 137,200 | 87,200 |  | 174,500 | 91,400 |  | 182,900 |
| GROSBEAK | 636 kCM ACSR | 73,400 |  |  | 146,800 | 93,200 |  | 186,400 | 97,600 |  | 195,300 |
| DRAKE | 795 kCM ACSR | 84,600 |  |  | 169,200 | 107,600 |  | 215,100 | 112,700 |  | 225,400 |
| CARDINAL | 954 kCM ACSR | 95,000 |  |  | 190,000 | 120,700 |  | 241,400 | 126,400 |  | 252,900 |
| PHEASANT | 1272 kCM ACSR | 112,800 |  |  | 225,600 | 143,400 |  | 286,800 | 150,200 |  | 300,500 |

| RAYBURN COUNTRY ELECTRIC COOPERATIVE, INC. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rockwall, Texas |  |  |  |  |  |  |  |  |  |  |  |
| Ampere Rating per Westinghouse T&D Manual |  |  |  |  |  |  |  |  |  |  |  |
| October 31, 2002 |  | WINTER BASE LOADING LEVEL |  |  |  | WINTER MAXIMUM PLANNING LEVEL |  |  | WINTER MAXIMUM EMERGENCY (Short Term) |  |  |
|  |  | kVA |  | kVA |  | kVA | kVA |  | kVA | kVA |  |
| Designation | Conductor | @ 69kV |  | @ 138kV |  | @ 69kV | @ 138kV |  | @ 69kV | @ 138kV |  |
|  |  | 20° F Ambient, 100° F Conductor (-7° C/ 38° C) |  |  |  | 20° F Ambient, 120° F Conductor (-7° C/ 49° C) |  |  | 20° F Ambient, 167° F Conductor (-7° C/ 75° C) |  |  |
| Single Conductor |  |  |  |  |  |  |  |  |  |  |  |
| RAVEN | 1/0 ACSR | 27,700 |  |  | 55,500 | 30,000 |  | 60,000 | 35,900 |  | 71,700 |
| QUAIL | 2/0 ACSR | 32,600 |  |  | 65,300 | 35,300 |  | 70,500 | 42,100 |  | 84,100 |
| PIGEON | 3/0 ACSR | 36,200 |  |  | 72,400 | 39,200 |  | 78,400 | 46,700 |  | 93,500 |
| PENGUIN | 4/0 ACSR | 41,000 |  |  | 82,000 | 44,500 |  | 88,900 | 52,900 |  | 105,900 |
| LINNET | 336 kCM ACSR | 63,900 |  |  | 127,900 | 69,200 |  | 138,400 | 82,500 |  | 164,900 |
| IBIS | 397 kCM ACSR | 71,200 |  |  | 142,500 | 77,100 |  | 154,200 | 91,900 |  | 183,800 |
| HAWK | 477 kCM ACSR | 80,800 |  |  | 161,600 | 87,500 |  | 175,000 | 104,300 |  | 208,700 |
| DOVE | 556 kCM ACSR | 88,100 |  |  | 176,200 | 95,400 |  | 190,700 | 113,700 |  | 227,300 |
| GROSBEAK | 636 kCM ACSR | 94,100 |  |  | 188,100 | 101,900 |  | 203,900 | 121,400 |  | 242,800 |
| DRAKE | 795 kCM ACSR | 108,500 |  |  | 217,000 | 117,600 |  | 235,200 | 140,100 |  | 280,100 |
| CARDINAL | 954 kCM ACSR | 121,800 |  |  | 243,600 | 131,900 |  | 263,900 | 157,300 |  | 314,600 |
| PHEASANT | 1272 kCM ACSR | 144,700 |  |  | 289,500 | 156,800 |  | 313,600 | 186,800 |  | 373,600 |

Appendix D

Most Limiting Series Element Database Example

### Appendix E

Transmission Project and Information Tracking (TPIT)

The TPIT spreadsheet was created to help convey information on future transmission projects to all ERCOT market stakeholders. The main goals of TPIT are below.

Increase Openness of Information

Increase Transparency

Improve Project Tracking

Able to Sort/Search Information

Improve Consistency of Base cases

Better Work Organization

Increase accuracy and project knowledge

TPIT is posted on the controlled access website http://planning.ercot.com/login/login under Reports - Transmission Project Tracking.

A sample of the spreadsheet is attached.

### Appendix F

Treatment of Mothballed Units in Planning

The treatment described in this paper was developed by a joint workgroup of the Wholesale Market Subcommittee (WMS) and the Reliability and Operations Subcommittee (ROS) at the direction of the Technical Advisory Committee (TAC).

Reserve Margin

The ERCOT-wide reserve margin for assessing generation adequacy will continue to be calculated as recommended by the Generation Adequacy Task Force and approved by TAC in early 2003.  However, for the purpose of determining how mothballed units will be treated in the powerflow cases, an alternative reserve margin calculation will be performed.  In this alternative calculation, the capacity of mothballed units that have given sufficiently firm indication that they will return to service by a specified year will be included in the reserve calculation for that year and thereafter.  However, the capacity of all mothballed units that have not given such indication will not be included in the calculation for any year.  From this alternative reserve margin calculation, the year in which the ERCOT reserve margin drops below the target of 12.5% will be determined and will trigger the inclusion of the remaining mothballed units in the powerflow cases.

Powerflow Base Cases

In the first year that has a reserve margin less than 12.5%, based on the alternative reserve margin calculation described above, the mothballed units that have not committed to a specific un-mothballing date will be made available to meet the load requirement that is not able to be met by operational and planned generating units and imports (as included in the Capacity section of the CDR) in the powerflow base cases.   However, in order to minimize the effect on transmission plans of the decision to use mothballed units to meet the load requirement, the generation that is needed from mothballed units as a group will be allocated over all the mothballed units on a capacity ratio share basis.  If this technique results in some of the mothballed units being dispatched at a level below their minimum load, an economic ranking will be used to remove the least economic units from consideration for that particular case so that the allocation of the load requirement among the remaining mothballed units will result in all of those units being loaded above their minimum loads.

For example, assume that, in some future year, ERCOT has a projected peak demand of 80,000MW and installed capacity of 82,000MW with 3000MW of that installed capacity being units that are mothballed and have not indicated they will return.  For this simple example, assume that the mothballed capacity is 20 generating units of equal 150MW size.  Ignoring losses, the powerflow case would need to include 1000MW of the 3000MW mothballed capacity in order to match the load.   Thus, each of the 20 mothballed units would be set to an output of 50MW in the powerflow case (assuming their minimum load is less than 50MW).

Alternative Dispatch Studies

While this treatment of mothballed units attempts to generally minimize the effect of the assumption that mothballed units will be used to meet the load requirement in the powerflow cases (rather than assumed new generation), the planning process should also consider alternative generation dispatches in instances where this treatment of mothballed units could have a direct effect on transmission plans.  Specifically, in instances where having a mothballed unit available would alleviate the need for a transmission project that would be required to meet reliability criteria if the mothballed unit were not to return, the transmission project should not be deferred based on the assumption that the mothballed unit will return to service.

Appendix G

Load Forecasting Methodology

CenterPoint Energy

See CenterPoint Energy’s annual ALDR submittal for a detailed description of how load data is determined.

Texas-New Mexico Power Company

TNMP’s forecast loads in the SSWG power flow cases are based on the information provided in the ALDR.  The loads at the time of ERCOT’s coincident peak serve as a starting point for each substation within a TNMP business unit.  Future load projections for the majority of substations are forecast by escalating at a standard growth rate, typically 1% to 2% depending on general growth expectations of the business unit.  Specific unit substations may be escalated at significantly greater rates when factoring in known developments, information from specific customers or if these stations are in areas where rapid growth trends are expected to continue.  Occasionally loads at certain substations are shown as decreasing if there are know customer operations that are likely to be discontinued.

The reactive portion of the load is typically based on historical powerfactors as reported in the ALDR.  In forecasting, the reactive load may be adjusted for known changes or to incorporate the effect of improvements for maintaining minimum load powerfactor criteria.

CPS Energy

CPS Energy models the ERCOT Base Cases using CPS Energy system peak load, rather than the ERCOT peak load.  The system load forecast is derived from the ALDR and data from the CPS Energy Forecasting section.  The individual substation peak loads (ALDR) are developed by our Distribution Planning section (based on census data, new building permits, etc…) on very specific parts of the CPS Energy service area.  The peak substation loads are scaled down such that the total individual substation peak loads sum to the forecasted CPS Energy system peak load.  Individual substation power factor data derived from the ALDR is retained in the scaling process.

Lower Colorado River Authority

LCRA’s loads in the SSWG load flow cases are based on LCRA system peaks and are derived from the load information provided by its direct connect customers.  Each year LCRA’s direct connect customers provide their forecasted noncoincident loads, and LCRA compares these loads against historical actuals to insure consistency with past trends.  Applying the previous year’s summer and winter coincident factors to each customer’s summer and winter noncoincident load derives the LCRA summer and winter coincident loads for the SSWG cases. The previous year's summer and winter coincident factors for each load are calculated by dividing each load's value at the time of LCRA’s summer and winter peaks by each loads corresponding noncoincident summer and winter peak values.  LCRA’s loads for the spring, fall, and minimum SSWG cases are calculated by multiplying LCRA's coincident summer loads by the previous year's spring/summer, fall/summer, and minimum/summer load ratios.

Austin Energy

The substation area load forecast uses a combination of spatial, load, transmission and distribution planning models together with actual historical data of summer substation peak load to produce a five-year small area load or substation level forecast.

The spatial model is composed of residential, commercial and industrial customer land-use.  Thirteen (13) customer classes form the basis of the land-use map that contains highways, water, vacant land, golf courses, restricted areas etc.  Within the spatial model are substation locations and boundaries form the basis of the substation area map.

The load model is set up using customer profiles, curves or shapes based on hourly energy consumption patterns and multipliers derived from power factors, growth rates, income and employment of each class.  Transmission and Distribution Planning model utilizes substation data, voltage levels and equipment, and costs.

The forecasting process starts with the collection of land-use and growth data of especially high growth areas using the company’s site and subdivision development plan database.   The models are set up by dividing the entire service area into high-resolution one-acre cells that are used to create substation area base maps. Each cell contains a land-use class that is combined with the customer profiles and multipliers to produce an electric load. A load map is consequently created, and used to ratio out load among the various substations.  The process is repeated for each forecast year.

The small area or substation level load forecast is driven the by system load forecast. This means the sum of the summer coincident substation peak loads for each forecast year is calibrated to match exactly the summer system peak load of that particular forecast year.

South Texas Electric Cooperative, Inc.

STEC member cooperatives provide individual substation load data.  STEC uses individual substation load data and hourly interval MW and Mvar data to determine the substation power factors for the current year.  Member and interval data serves as the basis for individual substation load forecasting.  The most recent current year substation power factors are used for future year forecasts.   The STEC system demand forecast is obtained from the most recent STEC Electric Power Requirements study.  STEC non-coincident peak individual substation load forecast data is scaled to fit the STEC system coincident peak demand forecast from the STEC Power Requirements Study.

ONCOR

ONCOR Electric Delivery

ONCOR models its loads in the base cases using ONCOR system peak loads that originate from data supplied by our Financial Management Group (FMG).  These loads are derived through the four processes outlined below:

- Service area and U.S. economy forecasts are provided by Global Insight – income, employment, GDP, etc

- Customers are forecast through a series of fourteen econometric models which are primarily driven by employment in the service area.

- End-Use models (REEPS, COMMEND, and INFORM) are used to forecast three customer groups; Residential, Commercial and Industrial.

- Demands are forecast with the Hourly Electric Load Model (HELM) and the MWH sales forecasts from step 3.

FMG provides both the ONCOR system load forecasts and four regional load forecasts which sum to the ONCOR system forecasts.

In addition, the peak load forecasts for ONCOR’s distribution substations are prepared by the Distribution Planning group.  A combination of known load additions for projects under development and historical load growth trends are used to produce the substation load forecasts.

The load forecasts for customer-owned substations are obtained from the customer or the customer’s Retail Electric Provider.

All of these substation load forecasts and ONCOR system load forecasts are supplied to ERCOT in the ALDR.

The substation load forecasts from the ALDR along with the system and four regional forecasts are downloaded into a customized in-house program called the Transmission Modeling Information System (TMIS).   TMIS also contains historical coincident load factors and distribution design power factors.  A Load Manager program inside TMIS then uses all of this data to produce substation loads that sum to the regional load forecasts minus regional transmission losses.  The program also calculates transformer reactive losses which are included in the substation reactive load.   These new ONCOR diversified substation load values are then modeled in the load flow base cases.

Brownsville Public Utilities Board

BPUB models the load flow cases using the BPUB coincidental system peaks and are derived from results of an econometric load forecast software program. The input data to this program are the historical and present data such as energy, load factor, loss factor, weather, income, earning, and etc. The resulting monthly forecast system peak is then scaled down into each substation using the substation historical peak and the expected growth of each substation. The load is represented on the transmission side and includes transformer losses.

City of Garland

Based on the load growth every year, Garland Power and Light (GPL) has estimated its load increasing at a ratio of around 2% of its total load (not load obligation) for local non-coincident peak load.  By using historic document, to obtain and use the non-coincident peak substation loads, we have applied the normal on peak ratios of all substations and scaled the system to the projected local non-coincident peak load above.

City of Denton

DME is at present using a 2.5% projected growth rate for load forecasting and comparing that to a historical curve.  The rate is adjusted from time to time to reflect the nature of growth in the area.

# Brazos Electric Coop

The load forecasts provided by Brazos Electric in the ERCOT SSWG power flow cases are calculated as follows:

- In the spring/summer of each year the Brazos Electric member cooperatives and its other wholesale customers provide individual substation load forecasts for the next six years.  Provided by each cooperative/customer are the non-coincident summer and winter forecasts for each load.

- The power factor for each load is calculated from the previous year’s data.  Hourly interval mw and mvar data is available for each of the loads for the previous year.  The power factor for each load is that found to occur at the time of each loads non coincident summer or winter peak.  This power factor is forecast to remain constant for the forecast period.  For new substations the power factor is assumed to be .97 low side.

- The sum of the individual load forecasts from item 1.  plus an estimate for system losses are compared to the corresponding years total Brazos Electric system demand forecast and a ratio is obtained.  Each individual load forecast is then multiplied by this ratio so that the sum of the individual loads plus estimated losses will meet the system demand forecast.

- The system demand forecast is obtained from the Brazos Electric Power Requirements document.  This document contains a detailed forecast of the Brazos Electric demand and energy requirements of the next 25 years.  This forecast includes allowances for weather and economic variables.

Bryan Texas Utilities

The load forecasts provided by BTU to the ERCOT SSWG power flow cases are determined as follows:

- In the spring of each year as the ALDR data is gathered, a query is run on BTU’s SCADA database to determine the previous year’s summer and winter ERCOT coincident and noncoincident peak loads for each of BTU’s substations.  Since BTU only has archived SCADA data going back for just a few years, data from system logs was used to obtain an additional 8 years of loading.  This gives a 10+ year running list of individual substation loadings.

Using this data BTU is able to determine, using Least Squares Regression and some insight into system operations, a scaling factor for each substation’s growth rate is determined.  Since different areas of BTU’s service territory grows at different rates, this allows for more accurate load estimation.

- Also during the ALDR data gathering process, the power factor coincident for each previously mentioned peak for each substation is determined from the previous year’s data.  Using these power factors from the substation’s transformer low side, power factor on the high side of the distribution transformer is then estimated.   Power factor is assumed to be constant for the study periods.  Planned substations’ power factor is assumed to be 0.97 lag on the low side until actual data can be obtained.

- Adjustments are made for each year to account for anticipated load that will move between substations and/or to account for new, projected loads that will affect substation loading.

American Electric Power Service Corporation (AEPSC)

# ERCOT Power flow Case Load Calculation Methodology

- By March 1 of each year, AEP Economic Forecasting along with Distribution Asset Planning prepares data for the Annual Load Data Request (ALDR) and submits the data to ERCOT.  Loads are modeled on the transmission side of the distribution transformer and include transformer losses.  Individual substation non-coincident peaks are forecasted from historical metered summer and winter peak loads for the preceding five years data.  Load growth at each metering point and time-series methods are used to produce forecasts of individual loads.  These individual loads are adjusted to agree with forecasts for larger geographical areas.

- Forecasts for geographical areas involve detailed analysis of historical data and economic forecasts.  Sales data is obtained from the customer information system by revenue town and revenue class.  Interval MW data is obtained from SCADA and MV90 recorders via Transmission Dispatch and Load Research. AEP obtains underlying economic drivers from external subscription sources to national, regional and county economic and demographic forecasts such as population, employment, income and etc.  Sales are forecast through the use of revenue class base econometric models.  Peaks are forecast through the use of normalized historical load shapes and typical weather for the area.  Peak probabilities are derived from a peak normalization model of the interval data.

- AEP does not have reliable company coincident peak at this time, due to metering issues related to ERCOT’s transition to a single control area, and lack of cooperation from adjoining utilities.

- ERCOT provides the date and time of the system summer peak, the system winter peak, and system minimum loads for the previous year.  AEP obtains the load data for these times along with the peak load at each bus from historical records.  The coincidence factor for each bus is calculated by dividing the load coincidental with the system peak by the seasonal peak load at the bus.  This provides a percentage (coincidence factor) to calculate the future loads off of the forecasted peak at each bus.

- AEP Transmission Planning receives the ALDR data from ERCOT the first week of April.  Additional data on industrial and self-serve loads is obtained from local area personnel.

- The ALDR data is analyzed, and suspect bus numbers, power factors, and summer & winter coincidence factors are investigated and corrected.  Special attention is given to bus numbers that change from case to case due to voltage conversions.

- An Access database is used to read in the validated ALDR data for AEP and each of the coops that it serves.  Seasonal factors are used to develop case data for seasonal and off-peak cases that aren’t in the ALDR.

- Loads are adjusted for losses and industrial loads and calibrated to the ERCOT-coincident peak value for each load entity within the AEP transmission system footprint.

Appendix H

Transmission Element Naming Convention

ERCOT Nodal Protocol (Section 3.10 Network Operations Modeling and Telemetry) requires consistency among various network models including Annual Planning Models, CRR Network Models and Network Operating Models.  One of the requirements requests the name of existing Transmission Elements including Electrical Buses, lines, transformers, generators, loads, breakers, switches, capacitors, reactors, phase shifters, or other similar devices, if modeled as part of the ERCOT Transmission Grid, in these three models must be identical and shall be unique within all of ERCOT.  ERCOT SSWG and NDSWG have coordinated their efforts to develop the Transmission Element Naming Convention standard.  The naming convention standard is in three parts but constitutes one standard.  At the present, only the Electrical Bus names in Part 1 is applicable to SSWG’s Annual Planning Models.

Part 1: Electrical Busses Names

The 12 characters Electrical Bus Name representing the same Transmission Element shall be identical in the Network Operations Model, Updated Network Operations Model, Annual Planning Model and CRR Network Model and shall be unique within all of ERCOT.

The following technical requirements must be followed:

- Name shall only include uppercase alpha-numeric values (A to Z and 0 to 9),

- The only special character allowed is the underscore (“_”)

- No spaces are allowed except at end of the name, and

- Names must be unique.

The following points are recommended, but are not requirements:

- Names should be derived from the substation name,

- All Electrical Bus Names within a substation should be related,

- A unique voltage designator should be within the Name, and

- A TSP prefix should be used to avoid naming conflicts.

Part 2: Lines, Breakers and Switches Names

Transmission Breakers and Switches representing the same Transmission Breaker or Switch in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall be unique within the same substation and shall have the first 14 characters unique.

All other Transmission Elements representing the same Transmission Element in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall have the first 14 characters unique within the Transmission Element type within all of ERCOT.

Part 3: Substation Names

Substation names representing the same substation in the Network Operation Model, Updated Network Operations Model, and CRR Network Model shall be unique for all substations within ERCOT and shall be limited to 8 characters.

Appendix I

Methodology for Calculating Wind Generation levels in the SSWG Cases

Goal – Use the available prior year’s operating data from the wind farms to set the dispatch in the new SSWG base cases.

Process

- Develop list of PI tags for all existing wind farms.

- Retrieve MW output for the following time frames:

  - May		3-5AM		4-6PM

  - August		3-6AM		4-6PM

  - September	3-6AM		4-6PM

  - December	3-6AM		6-8PM

  - January	3-6AM		7-8AM

- Calculate the average capacity factor of each plant for each time frame.  For the winter numbers, combine the data for December of one calendar year and January of the next calendar year (same winter).  Winter peak typically occurs either immediately after the minimum in January, or early evening in December.

- Group the wind farms by geography until better individual plant forecasting information is available. Assign any future plants that are not near the current geography groups to default group, see table below.

- The default group is determined by taking the minimum of all identified areas with historical data.

- Calculate the average % capacity factor of each group for each time frame.  Round off to the closest 5%.

- For coastal wind farms that have no operation data, the AWS Truewind models using the similar time frame in point number 2 are used to determine the capacity factor. This is done because of the significant difference in the coastal wind patterns compared to the ones in the West.

- Below is an example:

The 2008 % Capacity Factor data is below.

| Area | code | spg1 | spg2 | sum1 | sum2 | fal1 | fal2 | win1 | win2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Trent | a | 15 | 20 | 20 | 35 | 15 | 30 | 35 | 45 |
| Big Spring | b | 20 | 25 | 20 | 40 | 15 | 30 | 35 | 45 |
| SW Abilene | c | 20 | 25 | 20 | 35 | 15 | 30 | 35 | 40 |
| Mesquite | d | 15 | 15 | 10 | 5 | 10 | 10 | 25 | 25 |
| McCamey | e | 25 | 35 | 25 | 40 | 20 | 35 | 25 | 30 |
| Kunitz and Delaware | f | 20 | 15 | 10 | 5 | 10 | 10 | 25 | 25 |
| Caprock | g | 20 | 30 | 20 | 50 | 15 | 45 | 35 | 45 |
| Gulfwind | h | 41 | 40 | 43 | 27 | 20 | 31 | 28 | 30 |
| Default (Duplicate area Minimum Capacity factor) | i | 15 | 15 | 10 | 5 | 10 | 10 | 25 | 25 |

Appendix J

Mexico’s Transmission System in ERCOT SSWG Cases

This appendix provides an explanation of the modeling that represents Mexico’s Comisión Federal de Electridad (CFE) system in SSWG cases. A drawing of the system is at the end of this appendix.  All AEP and CFE facilities (bus, lines, etc.) tied to the CFE grid will be assigned to area 24 and zone 605.  The AEP facilities will retain the owner 8 and CFE will be assigned owner 150.

The following generation modeled in the power flow and short circuit cases are system equivalents of the CFE system and are located in Mexico. These units are not in ERCOT and should only be used for specialized studies. These units should not be included when performing transfer studies in ERCOT unless one is studying a transfer to or from CFE. The generation capability is not counted in ERCOT reports. These units are online in the cases to offset the real and reactive losses that are caused by the other CFE transmission facilities and reactive flow across the Laredo VFT, Railroad HVDC, and Eagle Pass HVDC that are modeled in the SSWG cases.  Lines in CFE will not be included in the ERCOT contingency list.

| Generation Station Name | Bus Number | Bus Voltage |
| --- | --- | --- |
| CIDINDUS-138 (System Equivalent) | 86104 | 138kV |
| CIDINDUS-230 (Swing Bus/Equivalent) | 86105 | 230kV |
| CUF-230 (System Equivalent) | 86106 | 230kV |
| CUF-138 (System Equivalent) | 86107 | 138kV |

The following are the transmission lines between Mexico and the United States.  All of the tie lines between CFE and ERCOT are operated normally open with the exception of the asynchronous ties at Eagle Pass, Laredo, and Railroad.

| Mexico |  |  | United States |  |  |
| --- | --- | --- | --- | --- | --- |
| Bus Name | Bus Number | Bus Voltage | Bus Name | Bus Number | Bus Voltage |
| Falcon | 86111 | 138 | Falcon | 8395 | 138 |
| Piedras Negras | 86110 | 138 | Eagle Pass | 86109 | 138 |
| Ciudad Industrial | 86105 | 230 | Laredo VFT | 80168 | 230 |
| Ciudad Industrial | 86104 | 138 | Laredo VFT | 80169 | 138 |
| Cumbres | 86107 | 138 | Railroad | 8395 | 138 |
| Cumbres | 86107 | 138 | Frontera | 86114 | 138 |
| Matamoras | 86112 | 138 | Military Highway | 8339 | 138 |
| Matamoras | 86113 | 69 | Brownsville Switching Station | 8332 | 69 |

Asynchronous Ties

Laredo

The Variable Frequency Transformer (VFT) in Laredo has a detailed model at busses 80170 (ERCOT Side), 80014 (ERCOT Side), 80169 (CFE Side), and 80165 (CFE Side).  The VFT is tied to the CFE system by a 12.73 mile 230 kV transmission line and a 12.39 mile normally open 138 kV transmission line.  Both lines terminate at the CFE Ciudad Industrial Substation (86103 and 86104) and are breakered at each end.  There is also a normally open 138 kV transmission line between the Laredo Power Plant (8293) and the Laredo VFT (80169) that is utilized for emergency block load transfers between ERCOT and CFE.  The Laredo Power Plant to Laredo VFT 138 kV transmission line is breakered at both ends.

Railroad

The HVDC tie in Mission has a detailed model at busses 8825 (ERCOT Side) and 8824 (CFE Side).  The Railroad HVDC is tied to the CFE system at Cumbres (86107) by an 11.79 mile 138 kV transmission line and is breakered at each end.  There is also a normally open bus tie that by-passes the HVDC that is utilized for emergency block load transfers between ERCOT and CFE.  The by-pass is breakered at both ends.

Eagle Pass

The HVDC tie in Eagle Pass has a detailed model at busses 8270 (ERCOT Side), 80000 (ERCOT Side), 86108 (CFE Side), and 86109 (CFE Side).  The HVDC is tied to the CFE system at Piedras Negras (86110) by a 4.23 mile 138 kV transmission line and is breakered at each end.  There is also a normally open bus tie that by-passes the HVDC that is utilized for emergency block load transfers between ERCOT and CFE.  The by-pass is breakered at both ends.

Normally Open Block Load Ties

Brownsville Switching Station

The Brownsville Switching Station (8332) is connected to the CFE Matamoras Substation (86113) by a 1.9 mile 69 kV transmission line and is breakered at each end.  The transmission line is operated normally open and is utilized for emergency block load transfers between ERCOT and CFE.

Military Highway

The Military Highway Substation (8339) is connected to the CFE Matamoras Substation (86112) by a 1.44 mile 138 kV transmission line and is breakered at each end.  The transmission line is operated normally open and is utilized for emergency block load transfers between ERCOT and CFE.

Frontera

The Frontera Power Plant (86114) is connected to the CFE Cumbres Substation (86107) by a 138 kV transmission line.  This transmission line is privately owned and operated by the owners of the Frontera Power Plant and is utilized to move the generation at Frontera Power Plant between the ERCOT and CFE systems.

Falcon

The Falcon Substation (8395) is connected to the CFE Falcon Substation (86111) by a .3034 mile 138 kV transmission line and is breakered at each end.  The transmission line is operated normally open and is utilized for emergency block load transfers between ERCOT and CFE.

Normally Open Block Load Ties on Distribution 
  
There are three normally open ties with CFE that are on the 12.47 kV distribution systems. These ties are at Amistad, Presido and Redford. These ties are only used for emergency block load transfers. Since SSWG does not model radial distribution systems these points are not in the SSWG power flow cases.

Map of Area

END OF DOCUMENT

? If the auxiliary MVAr load is not supplied, it can be estimated from the auxiliary MW load by assuming a power factor. CenterPoint Energy reviewed test data for its units from the fall of 2005. By comparing generating unit net MVAr to the system (high side of GSU), gross MVAr at the generator terminals, and estimated generator step up transformer MVAr losses under test conditions, an estimated auxiliary load power factor of 0.87 was determined.