## SEM-NOMCR ISSUES
SEQ# | PRIORITY | STATUS | ISSUE NAME | ORGINATOR | SUBMIT DATE | DESCRIPTION | EXPECTED / RESOLUTION DATE | ASSIGNED TO | COMMENTS
1 | Low | On Hold | NMMS/CIM to Nodal EMS | NDSWG | 2009-09-15 | Present plan/dates for loading NMMS/CIM file into active EMS currently running State Estimator and observable via SOTE | 2009-11-13 | Matt Mereness | 9/24/09 will be addressed next Help session. 10/1/09 -- Nov 13 goal date. 10/13/09 process expected or model posting expected? 10/29/09 PMO has been alerted to the need and is working on a plan
2 | High | Closed | NMMS Branch Data | NDSWG | 2009-09-15 | Produce Branch Data Reports from the NMMS with ownership details added. | 2009-10-15 | Woody Rickerson | 9/24/09 Compilation of a report is progressing. Designed to be similar to the Zonal Database load report. Request for ICCP data posing a problem 10/1/09 -- emailed to NDSWG members of the 9/29/09 NMMS. Please add From/To substation names to Line data. 10/13/2009 Can it be generated every 2 weeks? The equipment tab needs owner/operator included? Under line parameters r and x expressed in what units -- should be labeled. ERCOT will investigate requests and report back. 10/29/09 From a compliance perspecitive, the first binding CRR Auction using NMMS is November (model posted in October- so likely the 90-day submission “nodal protocol requirement” is Oct 1 minus 90 days- and would be July 1 for protocol compliance. So perhaps we measure Feb 1 submissions and ramp in on that.
3 | Medium | On Hold | Protocal Section 3 | NDSWG | 2009-09-15 | Q: When do Section 3 protocols come into effect for 90-day lead time for NOMCR submission metrics and/or compliance purposes, related to Nodal Protocol Transition plan |  | Matt Mereness | 9/24/09 Will be addressed in future meetings. 10/1/09 -- Feb. 1 begin monthly Nodal Protocol reports produced for review only by TSPs. NODAL GO-Live reports to IMM and PUCT will not begin until future notification. 10/13/09 ERCOT will report back on how the transition will be carried out. 10/29/09 November CRR auction would require a August adherance to Data submisstion from TSPs. NOMCRs submitted after Aug 1 would be subject to Protocol submission and reporting deadlines. ERCOT will try to find a Protocol implementation table.
4 | High | Closed | Broken Outages | NDSWG | 2009-09-15 | Define a process to manage "broken outages" in the Zonal Outage Scheduler that occur when NOMCRs with equipment name changes are converted and loaded into the Zonal database. | 2009-09-15 | Woody Rickerson | 9/15/2009 Woody presented a flowchart defining the process at the Sep-15th NDSWG meeting.
5 | High | In Progress | A2E Process | NDSWG | 2009-09-15 | Define the Approval to Energize Process for now, possible other milestone changes (if any that would affect A2E process), and Nodal |  | ERCOT | 9/24/09 ERCOT to provide list of SRs in Pending state 10/1/09 -- email by end of business day to NDSWG members with list of SRs in Pending state. Approval to Energize process does not change until NODAL Go-Live. 12/15/2009 Nodal A2E process dependent on outcome of the database load frequency. Current plan is to require new equipment to be energized through the use of outages in the Outage Scheduler.
6 | High | In Progress | Owner/Operator 1 | NDSWG | 2009-09-15 | Owner/Operator Definitions and ERCOT Legal intrepretations (Proposed NPRR) | 2009-10-30 | ERCOT | 9/24/09 Pending decision by ERCOT legal to be decided 1st week in October. Will be addressed in future meetings. 10/1/09 NPRR proposal by end of October, Chad Seely 10/13/09 No New information, 11/16/2009 ERCOT is working with Siemens to give operatorship the ability to create new equipment 12/15/2009 NPRR draft supplied to NDSWG -- Comments due by Jan 11
7 | Medium | Closed | Owner/Operator 2 | NDSWG | 2009-09-15 | Downstream effect of Owner/Operator on compliance reporting (also implications in EMS applications and Planning) | 2009-10-15 | ERCOT | 9/24/09 ERCOT will provide clarity of telemetry reports -- Issue resolution is tied to item 6 10/1/09 -- Dual/Quad/AEP owner/operatorship assignment capability in question. 10/1/09 -- Q: NOMCR statistics based upon equip owner or by submitter of NOMCR. See NOGRR 25. Continued discussion next meeting. 10/13/09 No new information 11/16/2009 ERCOT send out list of downstream uses of the owner and operator designations
8 | High | Closed | Tieline Ratings | NDSWG | 2009-09-15 | Tieline Rating Business Process and EMS/MMS handling. Should it include Static and Dynamic ratings? | 2009-10-23 | NDSWG | 9/24/09 a Minimum of Each Owner's submittal is used in the EMS. NDSWG requested the functionality to be tested. 10/1/09 -- Functionality works by selecting min. of two ratings. Q: If Dyn.Ratings one side, Static Ratings other side will it work or needs Dyn.Ratings on both sides? A: Current ZONAL system requires Dyn.Ratings both sides. NODAL system to be checked.
9 | Low | On Hold | RTU Outage Process | NDSWG | 2009-09-15 | Planned RTU Outage Process- Coordination as well as Metric mangement. Document it for future reference. |  | ERCOT | 9/24/09 NMG to incorporate input from outside Network Modeling -- Requires ability to assign outages to RTUs, communication, etc. 10/1/09 -- J.Messer has a way to track ICCP outages. RTU outages will not be tracked. 10/13/09 discussed 10/29/09 MPs would like a formal statement that ERCOT will not be able to incorporate RTU outages in telemetry reports. What is the value of the report without proper inputs? 11/16/2009 Issue is still being investigated by ERCOT
10 | Medium | Closed | Non-Registered Entities | NDSWG | 2009-09-15 | Handling of the generic non-registered entity in the MMS, EMS, and Planning | 2009-10-30 | ERCOT Legal | 9/24/09 -- Issue resolution is tied to item 6 10/1/09 -- ERCOT to follow-up. 10/13/09 ERCOT to follow-up 11/16/2009 ERCOT plans to provide a non-registered entity in NMMS
11 | Medium | Closed | Load Rollover | Curtis Crews | 2009-09-16 | Load Rollover- Protocol Interpretation, How to do it, …and can it span multiple stations . | 2009-10-01 | ERCOT | 9/24/09 review of Protocols required. need additional week for review 10/1/09 -- LoadRollover can be supported across different substations. Protocols 3.10.7.1.3. Better to define in Op. Guides? Item to be discussed at future time. 10/13/09 Give an example of how it is modeled in NMMS. How would we expect to see a load roll over. Would it be on the distribution or transmission. Should this be defined in the Operating Guides. Does the EMS look for the high side breaker as a trigger. 10/29/09 EMS is looking for a dead node. Assumes the load rollover is active is a dead node is found. Will be tested in the next two weeks. 11/16/2009 Test successfully completed
12 | Low | Closed | SPS Modeling | Curtis Crews | 2009-09-16 | SPS- Please confirm proper modeling of SPS for your system and guidance for future SPS changes. | 2009-10-01 | ERCOT | 9/24/09 SAMRs required from MP. Review process. NOMCR submitted by undetermined. 10/1/09 All SAMR submittals to contain identical type of information currently sent in ZONAL.
13 | Low | Closed | SPS in Handbook | Curtis Crews | 2009-09-16 | SPS reference in the ICCP Handbook | 2009-10-15 | ERCOT | 9/24/09 Is the Status of an SPS required? ERCOT Chad Thompson to present in next NDSWG 10/1/09 -- Yes, Status will be shown on an ERCOT SCADA display dashboard. ICCP Handbook will be reviewed.
14 | Low | On Hold | EPS Meter Symbol | Curtis Crews | 2009-09-16 | EPS Meter symbol in graphic interface | 2009-12-01 | ERCOT | 9/24/09 ERCOT to report back on the Status of NMMS graphical representation of EPS meters from SIEMENS 10/1/09 -- Not available in the IMM. ERCOT to eval $ vs. need. Schema change needed for protecting EPS meter model not desired. 10/13/2009 ERCOT has a proposal to Siemens. ERCOT will report back. 10/29/09 Siemens will not be providing one-line autolayouts
15 | Low | Closed | ICCP Training | SEM Market Call | 2009-09-10 | Additional ICCP Modeling training. | 2009-10-13 | NDSWG | 9/24/09 NDSWG to provide issues and demand for training. 10/1/09 Discuss in Oct 13. NDSWG meeting. Low attendence in last "extra" training course. 10/13/2009 no further need at this time
16 | High | Closed | NOMCR Statuses | Ebby John | 2009-09-24 | Provide NOMCR Status Definitions. When is a NOMCR approved for the Zonal Database Load? How can we tell which NOMCRs are in the Zonal Database Load? | 2009-10-15 | ERCOT | 9/24/09 ERCOT will present life of NOMCR on next NDSWG meeting. ERCOT entered Psuedo switches for ZONAL only. J.Moseley to present 10/1/09 -- J.Moseley to present in next Oct. 13 NDSWG meeting or WebEX Oct 15.
17 | Low | Closed | Voltage Realys | Ebby John | 2009-09-24 | NMMS model has voltage relays (possibly for OTS) which are not real equipment in MP system. Can TSPs remove them? | 2009-10-01 | ERCOT | 9/24/09 If Breakers are to be removed then ok to remove Relay model. For ownership, ERCOT to be set as owner. 10/1/09 -- If equipment physically removed, Ok. If not, No. Coordination efforts needed between MP & ERCOT for removal.
18 | Low | Closed | Pseudo LAAR Loads | Ebby John | 2009-09-24 | NMMS model has extra pseudo loads for LAAR representation which are not real equipment in MP system. Can TSPs remove them? | 2009-10-30 | ERCOT | 9/24/09 No, TSP cannot remove LAARs. ERCOT to remodel. ERCOT to be assigned as owner. 10/13/09 ERCOT will provide a list of LAARs to the TSPs and possibly a template to aid modeling. 10/29/2009 List has been sent out. 11/16/2009 ERCOT has responded to MP requests to remove certain loads
19 | Medium | Closed | ICCP Objects missing | Ebby John | 2009-09-24 | ERCOT did not provide ICCP object to source MW/MVAR analog values in ERCOT model for some AC Line Segments and Transformers. ERCOT supplied model does not pass validation. | 2009-10-30 | NDSWG/ERCOT | 9/24/09 MG 13.1.8 (page 84) and Rule 133; MVA required, MW/MVAR can be deleted by MP. 10/1/09 -- Associated with #20. Options: 1) NOMCRs by MP 2) Recommended: ERCOT to identify location 3) ERCOT to clear all out ~3500 non-ICCP; MPs to add back in if needed 4).xml provided for the bulk change, but possible data-lock problems with other existing NOMCRs. MP to break-up .xml as required. 10/13/2009 ERCOT sent out summary report for TSPs to consider 11/16/2009 ERCOT has completed all requests form MPs
20 | Medium | Closed | Script to remove unassigned telemetry | NDSWG | 2009-09-24 | Can ERCOT write script to remove un-assigned telemetry for MW/MVAR/ &MVA calc. NDSWG to approve list of telemetry to be removed. | 2009-10-15 | ERCOT | 9/24/09 ERCOT will investigate and report back at next NDSWG Meeting 10/13/09 ERCOT will send out summary report 11/16/2009 See item 19
21 | Medium | On Hold | Performance Issues in PTC | NDSWG | 2009-09-24 | Performance issues in the PTC |  | NDSWG/ERCOT | 9/24/09 need MP to send screenshots, timestamps of the instance to track down in logs. MPs would like root cause explanations. 11/16/2009 NMMS performance issues are still being monitored
22 | Medium | Closed | Line Ownership | Feng Tu | 2009-09-25 | Process to change line ownerhip/operatorship in NMMS | 2009-10-07 | ERCOT | 10/1/09 -- ERCOT to provide similar effort to Station Ownership, similar forms. Joint-Operatorship info requested for Stations & Lines. 10/13/2009 ERCOT will send out by end of the week 10/29/09 List has been sent out. 11/16/2009 ERCOT has completed requests to reassign ownership
23 | Low | Closed | Analog/Discrete Ownership | Feng Tu | 2009-09-25 | discuss the Analog/Discrete ownership not being updated with the station ownership |  | ERCOT | 10/1/09 -- Desired by ERCOT. ICCP data deemed to provide the best information at hand.
24 | Medium | On Hold | Critical Bus List | NDSWG | 2009-10-08 | List of 20 critical buses which are required by protocols for one of the SE reports. All the buses are currently 345kv, may need to be 138kV. | 2009-10-30 | NDSWG | 10/13/2009 How was this list generated? -- 345 nuke buses, synch points in BS plan, buses associated with IROLs, CSC associations, high usage 345 buses Why just 345kv and not 138kV? -- 345 more crucial for SE. Which bus voltage in particular in the case of two 345kv buses. -- discussed with 10/29/09 Alex will coordinate how changes to the list is made. Addressed as part of the Telemetry Standard Review. 11/16/2009 Will need to be changed in State Estimator standards to remove the word critical and in NOGRR25
25 | Low | On Hold | EPS Meter Process | Curtis Crews | 2009-10-08 | How are EPS meter additions processed? What are TSP responsibilities? | 2009-10-30 | ERCOT | 10/13/09 How do you coordinate the TSP and Resource owner. What are the timelines for submittal. How to avoid getting interim update because of ERCOT process. ERCOT will report back on the timeline 10/29/09 no change 11/16/2009 TSPs required to submit Design proposal to ERCOT. RE changes will come in through the RARF.
26 | Medium | On Hold | Transformer Name vs. Winding Name | ERCOT | 2009-10-13 | Which name is used. | 2009-10-30 | ERCOT | 10/13/09 Being investigated by ERCOT -- report back at the next meeting 10/29/09 Nodal OS uses the transformer name -- ERCOT revisit Vamsi's email and clarify 11/16/2009 ERCOT changed the template so that the winding name and tsf name. EMS will only use the tsf name. Nodal OS will use the tsf name.
27 | Medium | Closed | Submission of Oneline with NOMCR | ERCOT | 2009-10-13 | Is this needed in the future | 2009-10-30 | ERCOT | 10/13/09 ERCOT will consider this in future.
28 | Medium | In Progress | Dual Owner problem | Dwight B | 2009-10-13 | Owner of equipment can only create children objects under the equipment Operators of an equipment may only update attributes of the equipment Should the operator have more expanded ability to create new objects | 2009-10-30 | ERCOT | 10/13/09 ERCOT will have offline discussions with Brazos and determine a course of action. Suggested having a special Webex just to discuss this issue. 11/16/2009 ERCOT is working with Siemens to give operatorship the ability to create new equipment
29 | Medium | Open | IMM report of co-owned lines | Curtis Crews | 2009-10-13 | posting of the co-owned lines, how will it be provided to the IMM | 2009-10-30 | ERCOT | 10/13/2009 ERCOT will report back
30 | Medium | Closed | GUI | Heidi Mansion | 2009-10-13 | Hiarch view truncating names of devices in the auto generated one-line | 2009-10-30 | ERCOT | 10/13/2009 TPS will provide screenshots to NOMCRhelp when this occurs 11/17/2009 ERCOT will put it on the list of things to be fixed
31 | Medium | Closed | SAMR download | Curtis Crews | 2009-10-13 | SAMR download option doesn't work | 2009-10-30 | ERCOT | 10/13/2009 ERCOT has put in a variance 11/16/2009 has been corrected
32 | Medium | Closed | Partial approval for NOMCRs | Dwight B | 2009-10-19 | Partial approval to energize submittals |  | ERCOT | 10/29/2009 There are no partial approval for to energize for NOMCRs. Each NOMCR is good for the one date. In Nodal the OS will be used to bring new pieces of equipment into service.
33 | High | Open | Incorrect ratings | Dwight B | 2009-10-19 | Incorrect ratings in the data as of SEM go live |  | ERCOT | 10/29/09 ERCOT will investigate and report back 11/17/2009 ERCOT will supply XML files to correct errors and send them to MPs.
34 | Medium | Closed | Planning Validation | cnp | 2009-10-29 | does the Planning model need to be validated by the Feb deadline along |  | ERCOT | 10/29/09 Wrickerson stated he didn't believe the Planning model was expected to be valid in February -- will verify 11/17/2009 ERCOT will report back
35 | Medium | Open | Tieline MW readings | Jackie Rainey - Lewis | 2009-10-15 | ERCOT wants 2 mw readings for tie lines? Is this a requirement in the guidelines. Tielines defined as lines between weather zones. |  |  | 11/17/2009 Can the redundant values be taken out for tielines crossing weather zones. ERCOT will investigate -- could be a redundant value. Are the TSPs required to send in two different values.
36 | Medium | Open | MW1, MW2, Mvar1, Mvar2 calcs | Jackie Rainey - Lewis | 2009-10-14 | What are the MW1, MW2, Mvar1, Mvar2 calculations for tielines? |  |  | see 35
37 | Medium | Open | Bus kV measurements | Jackie Rainey - Lewis | 2009-10-09 | ERCOT is maping line voltages to Busses. What problems do this cause? |  |  | 11/17/2009 ERCOT SE determines a voltage for each SE bus. ERCOT is testing to determine how the two voltages should be assigned. ERCOT will report back. MPs would like to be provided with a list of requested voltage measurements.
38 | Medium | In Progress | MLE notification | NDSWG | 2009-11-10 | If the rating of a line owned by company A is changed and that line terminates in a station owned by company B (that may have mle equipment) will company B be notified | 2009-11-16 | ERCOT | 11/16/2009 Company B will not be notified 11/17/2009 Possible solution would be to make the terminal equipment owner an operator on the line. MGRR language will be drafted for further consideration.
39 | Medium | On Hold | Connectivity Nodes limited to 4 characters | NDSWG | 2009-11-10 | Can the Connectivity nodes and busbar names be expanded past 4 characters |  | ERCOT | 11/16/2009 MMS can't support more than 4 characters. Investing IA. 11/17/2009 SCR will be required in order to further investigate this issue. ERCOT will investigate whether validation rules can be modified or if a validation rule is missing.

## MODELING GUIDLEINES ISSUES
SEQ# | PRIORITY | STATUS | CURRENT VERSION | SECTION NO. | ORGINATOR | SUBMIT DATE | DESCRIPTION | RESOLUTION DATE | ASSIGNED TO | COMMENTS | NDSWG REVIEW
1 | Low | Open | 1.0 | 10 |  |  | Rule change to naming measurement locations as grandparent name for lines |  |  | Current guideline rule: mearsurementlocation must be same name as parent object. Model does not follow this rule.
2 | High | Open | 1.0 | 10 |  |  | Modeling guideline has no mention of SSID object for Aclinesegment. |  |  | SSID was mentioned in training and is usd to take ownership of more than one Onwersharerating
3
4

## SCHEMA CHANGES
SEQ# | PRIORITY | STATUS | ISSUE NAME | ORGINATOR | SUBMIT DATE | AREA | MODULE NAME | DESCRIPTION | EXPECTED RESOLUTION DATE | ASSIGNED TO | COMMENTS | NDSWG REVIEW
1
2
3
4

## TEMPLATES
LAAR Template
Contingency deletion template