## test results
CRE test for: |  | Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] | [5 empty] | PASS
Line Rating: |  | 1072
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.13753
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.19296
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12517
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.045454
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.1501
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.18938
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12576
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.042604
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.32691
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.011763
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.18013
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.31873
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.14751
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.16777
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.32691 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.32691 | 0.32691
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.39606
[6 empty] | Concentration |  | 1.2115 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.37433
[6 empty] | Concentration |  | 1.1451 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 86.5642
| Percent of line rating => | [6 empty] | 8.075% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.2295
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.0021511 | 0.016614 | 0.014463 | 0.0021511
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0023134 | 0.21915 | 0.22147 | -0.0023134
[7 empty] | B4 (S-W) | 0.0022813 | -0.38958 | -0.39187 | 0.0022813
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0056874 | -0.18705 | -0.18136 | -0.0056874
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0044752 | 0.20179 | 0.20627 | -0.0044752
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 0.5352%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.5756%
[7 empty] | B4 | 0.5676%
[7 empty] | B5 | -1.415%
[7 empty] | B6 | -1.113%
[7 empty] | Max Abs Error | 1.415% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.20866 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 53.2083
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 31.0903
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.697
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.697
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 31.925
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 28.0908
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 14.9818
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14582 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 10.6449
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 17.3527
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 29.8933
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 14.8737
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 13.9988
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.7154
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.7154
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 25.8712
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 13.8596
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6295
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6295
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.5512
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 41.8977
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.3853
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.3853
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.14461 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 16.2691
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.14307 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.7227
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.3001
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 15.1621
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 20.8837
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14304 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.871
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.7026
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 9.1378
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.8567
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.5709
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.8562
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.047651 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 22.0624
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 8.1125
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.9896
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.2354
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.2354
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.2354
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 14.0125
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12292 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 63.3023
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.4136
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7961
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7961
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.5411
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.5411
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.2861
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.8771
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.3083
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.9278
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 19.0774
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.9803
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.6467
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.7924
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 18.0067
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.1936
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.8379
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.8379
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.3248
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12563 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.2412
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.5918
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12641 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 15.1688
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.12527 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.2655
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12558 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.8986
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 19.245
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.81723
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.2471
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.9583
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 15.1754
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.14001 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 51.2426
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.13972 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 33.813
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.13371 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 53.4844
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13372 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 31.5579
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13523 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 22.3128
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 29.2799
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 28.8493
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 34.734
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8036
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8036
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.8036
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.383
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.14284 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 17.1414
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.14151 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 8.4905
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.7309
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.389
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.6481
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 22.9101
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.3373
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 28.0648
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.3373
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 22.4805
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 28.3512
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14345 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 24.3867
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14345 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 74.5945
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 53.021
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 79.8013
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 82.8045
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 115.5545
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 16.4638
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.147 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 14.6998
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 55.5652
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 32.185
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 30.3632
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 40.346
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.1486 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 114.4205
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 10.4706
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.321
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.321
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 10.1714
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 170.7639
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 170.9115
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 35.0815
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 35.3948
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 33.864
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 33.8171
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 33.2022
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 33.0456
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.14987 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 59.1987
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.14957 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 65.0612
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.14987 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 65.1934
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.14433 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 19.9175
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 17.1992
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14576 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 16.7619
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 81.0403
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.143 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 55.4824
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.143 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 73.6429
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 107.0881
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 108.4523
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 106.406
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 24.4282
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 64.963
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.1408 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 31.5392
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.13483 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.7413
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.13489 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.6652
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 77.4445
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 73.9186
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.23958 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 128.6545
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.23958 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 188.5495
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 14.9224
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 44.1705
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -160.0597
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -38.6272
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -39.9209
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.18472 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -75.1827
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.5017
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -8.6865
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.5017
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.5017
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -78.5112
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -78.6964
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -10.6535
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -16.3476
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -8.082
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -8.082
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -7.8983
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -8.2656
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -76.2295
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -74.0092
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -100.2298
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -137.6782
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -11.3298
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -17.6448
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -28.046
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -28.5857
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -31.3521
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -28.5857
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14932 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -3.285
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.6425
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.6425
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -7.1863
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -5.6195
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -6.9302
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -7.2315
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8867
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.7295
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16385 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.9324
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.9324
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.7686
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.17391 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -68.868
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -130.1115
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -129.6234
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.8846
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.9887
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2.3229
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.15486 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -7.2783
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.2685
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12954 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.4318
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.12259 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 20.7783
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.056431 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 8.4647
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.1276 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 8.0389
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.13639 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 88.6158
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.7437
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.7437
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.19242 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -81.2029
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -30.2085
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -30.6662
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -73.9192
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -37.4248
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -37.8986
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -41.4515
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -122.779
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -125.0916
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.21002 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -90.9404
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -45.7555
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -45.9803
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -45.8986
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -46.3277
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8755
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8755
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.3197
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.3197
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -2.7664
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.18349 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -2.5138
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.6309
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.6309
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.7975
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -7.5748
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.7975
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -5.4236
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -5.6173
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.3061
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.6909
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.5056
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.5056
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.5056
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.5056
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.20737 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -1.2442
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.47318
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.47318
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.55205
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.19451 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.77802
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.46646
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.46646
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.9396
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -26.229
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -26.6091
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.9396
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -34.5918
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -37.6329
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -36.2188
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -35.5063
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -55.2425
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -27.9754
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -28.5664
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -29.7485
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -57.1329
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.9356
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -2.224
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8867
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.15096 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -11.0202
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -11.1618
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -11.4443
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -4.0998
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -1.0249
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -11.1618
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -11.303
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -11.077
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.5322
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -6.4992
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.15971 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -100.4588
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -21.9767
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -28.6918
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.18285 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -2.1942
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.11226 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.67358
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -51.4913
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -51.2994
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -52.2209
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.1538 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.8445
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.8411
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.8411
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.15379 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.8441
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.15452 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -4.4811
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -22.7293
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -22.7753
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -23.4497
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -23.9689
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -23.2104
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -15.1702
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -21.9968
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -22.3002
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -19.2662
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -22.7708
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -22.9884
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -26.8897
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -32.115
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -33.6199
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -37.5451
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -22.3402
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -22.3402
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -26.5289
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -73.2555
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -97.5952
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -10.0428
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.521
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.521
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -11.2384
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -11.4872
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.7839
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.7839
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -11.0184
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -36.1027
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -34.6961
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.2528
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.2528
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7639
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7639
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.6185
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0159
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0159
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.3979
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 26.0619
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.7877
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.5734
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 17.0241
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.401
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 26.2872
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 27.0268
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.3583
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 32.1994
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 25.4751
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 25.4366
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.5036
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.12342 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.3896
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.8312
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.8312
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12672 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 28.512
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 16.0525
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 16.0525
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 20.062
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 20.2053
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 44.2797
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 20.4919
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 20.6352
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 44.423
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 28.7779
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 16.2977
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14436 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.8155
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.2406
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.2406
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 58.6684
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 22.9572
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.8155
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 23.0989
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 57.9598
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 20.0877
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 17.6446
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 19.6806
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 54.1555
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 19.2418
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 19.2801
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 22.651
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 19.3864
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 19.4888
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 22.7134
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -163.4353
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.6283
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.6283
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.040111 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.2836
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 1.7544
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.6813
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.48262
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.0511
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.040218 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.68371
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.8848
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 1.0054
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.036551 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 3.8379
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.12808 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.7586
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.11002 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.8015
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.4853
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.4853
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -3.37
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -3.1749
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.5227
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -7.2922
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -7.3064
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -7.2493
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -4.5695
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -11.6142
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.904
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.7775
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -4.425
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.8918
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.8585
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.5242
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.4289
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.5058
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.5058
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -8.0468
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -7.4044
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 13.1153
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 13.1756
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.035405 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -4.8151
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.054269 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.7909
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.484
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.484
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.3427
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.3427
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -5.0293
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.70835
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -9.0467
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -9.0467
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -13.5977
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.5972
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.3974
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.5972
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.5972
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -5.5112
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -2.4079
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.7175
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -3.5786
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -3.5541
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -2.2264
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.49839
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.031605 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -23.4825
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.033118 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -24.3417
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.3576
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.3576
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.3576
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -3.937
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.035104 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -6.073
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.035104 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -4.739
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -4.897
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -4.8549
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -4.7797
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -8.0975
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -2.3608
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -2.3313
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -3.0469
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.715
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -6.1748
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -5.944
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -5.9592
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -5.9403
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -10.1779
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.15843
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.66539
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 5.6172
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 5.6828
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 5.6828
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 13.8426
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -11.8246
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.7769
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.7769
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.7769
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.1246
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.1246
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -2.086
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 84.7129
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 83.8934
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.056004 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.5818
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.369
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.369
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -10.1809
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -7.1751
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -7.1751
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -9.89
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -6.6348
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -5.846
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -5.787
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.037465 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.3113
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.043134 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -19.7985
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -2.0589
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -2.0906
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -2.2173
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.9956
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.9639
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -3.2943
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.8689
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -3.5501
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -3.5046
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -3.5046
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.022757 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -3.6866
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.03133 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -4.9188
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.5771
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.6134
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.4156
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.0889
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -2.987
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -3.0636
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.036896 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.59772
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.037012 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -6.107
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.037043 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -6.2603
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.036905 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -7.8608
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.036874 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -8.4073
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.037066 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.44479
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.037066 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.66719
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.045093 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -2.2546
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.5019
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.5019
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.8183
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.7846
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.8183
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.9193
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.8183
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.8183
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.953
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.953
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.032283 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.3874
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.6274
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.7145
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.6274
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.6274
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.7145
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.6274
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.091624 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -6.0472
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -8.6542
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -8.923
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -13.3307
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -29.3491
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -34.5632
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -36.1949
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -31.3578
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -33.3594
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053753 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.69879
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.031647 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.37976
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -1.1135
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -1.1364
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -1.0709
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.5032
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.57968
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.6681
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.65172
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -1.1462
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.5895
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -2.7969
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -4.847
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.644
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -5.3481
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.3706
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.5652
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -6.4417
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -6.5915
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.7452
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.3483
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -7.0409
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -5.2432
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.7189
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -5.393
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.8537
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.5652
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -7.2656
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -7.715
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.6926
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.9922
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.9922
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -12.8084
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3606
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.10448 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.9931
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.8198
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.4099
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.8937
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.11005 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.8037
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.4226
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.10372 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.7127
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.8937
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -21.953
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 15.1718
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 29.4587
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.5187
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -42.7505
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -35.4329
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -43.1357
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -22.1456
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -19.257
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.13136 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.8817
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.095774 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.078876 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11461 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.55013
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.8407
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.8766
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.4265
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.3611
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.5539
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.3913
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12499 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.7487
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 14.0017
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.6068
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 23.1496
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.6967
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.15486 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.11768 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.16289 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.9561
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -6.1602
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -10.4553
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.5472
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -6.345
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.8808
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.9404
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.5472
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -5.5713
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -6.6546
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -3.4047
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.7104
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1963
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -1.0249
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1963
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.7104
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.7104
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -22.904
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.7378
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -8.5116
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.7378
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.1517 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.8204
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -2.221
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -3.4055
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.1425 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -6.8399
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.147 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.176
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.15329 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -27.5931
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -27.5846
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -27.6464
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -27.6464
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -16.2904
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -16.2904
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.437
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.8078
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -2.2847
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -81.452
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -81.452
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1629 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.16173 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.088959 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.15894 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.15731 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414] | [7 empty] | 86.5642
Number of Bus | Name of Bus | ID | Max MW | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.20866 | north | Y | 0.071134 | 0.40162 | 0.083494 | 0.25411 | 0.071134 | North | N | 0.071134 | 0
239 | BOSQUESW | 1 | 149 | 0.20866 | north | Y | 0.071134 | 0.40162 | 0.083494 | 0.25411 | 0.071134 | North | N | 0.071134 | 0
244 | WHITNYDM | 1 | 15 | 0.1798 | north | N | 0.042271 | 0.37276 | 0.054631 | 0.22525 | 0.042271 | North | N | 0.042271 | 0
245 | WHITNYDM | 2 | 15 | 0.1798 | north | N | 0.042271 | 0.37276 | 0.054631 | 0.22525 | 0.042271 | North | N | 0.042271 | 0
247 | BOSQUESW | 2 | 153 | 0.20866 | north | Y | 0.071134 | 0.40162 | 0.083494 | 0.25411 | 0.071134 | North | N | 0.071134 | 0
251 | BOSQUESW | 2 | 150 | 0.18727 | north | Y | 0.049746 | 0.38023 | 0.062106 | 0.23273 | 0.049746 | North | N | 0.049746 | 0
253 | BOSQUESW | 2 | 80 | 0.18727 | north | Y | 0.049746 | 0.38023 | 0.062106 | 0.23273 | 0.049746 | North | N | 0.049746 | 0
332 | RWMILLER | 1 | 73 | 0.14582 | north | Y | 0.0082953 | 0.33878 | 0.020655 | 0.19128 | 0.0082953 | North | N | 0.0082953 | 0
333 | RWMILLER | 2 | 119 | 0.14582 | north | Y | 0.0082953 | 0.33878 | 0.020655 | 0.19128 | 0.0082953 | North | N | 0.0082953 | 0
334 | RWMILLER | 3 | 205 | 0.14582 | north | Y | 0.0082953 | 0.33878 | 0.020655 | 0.19128 | 0.0082953 | North | N | 0.0082953 | 0
335 | RWMILLER | 4 | 102 | 0.14582 | north | Y | 0.0082953 | 0.33878 | 0.020655 | 0.19128 | 0.0082953 | North | N | 0.0082953 | 0
336 | RWMILLER | 5 | 96 | 0.14582 | north | Y | 0.0082953 | 0.33878 | 0.020655 | 0.19128 | 0.0082953 | North | N | 0.0082953 | 0
344 | MRSSHPRD | 1 | 12 | 0.14295 | north | N | 0.0054213 | 0.33591 | 0.017781 | 0.1884 | 0.0054213 | North | N | 0.0054213 | 0
345 | MRSSHPRD | 2 | 12 | 0.14295 | north | N | 0.0054213 | 0.33591 | 0.017781 | 0.1884 | 0.0054213 | North | N | 0.0054213 | 0
366 | JNSNCNTY | 1 | 168 | 0.15399 | north | Y | 0.016469 | 0.34696 | 0.028829 | 0.19945 | 0.016469 | North | N | 0.016469 | 0
367 | JNSNCNTY | 2 | 90 | 0.15399 | north | Y | 0.016469 | 0.34696 | 0.028829 | 0.19945 | 0.016469 | North | N | 0.016469 | 0
503 | NTHTEXAS | 1 | 18 | 0.14608 | north | Y | 0.0085593 | 0.33905 | 0.020919 | 0.19154 | 0.0085593 | North | N | 0.0085593 | 0
504 | NTHTEXAS | 2 | 18 | 0.14608 | north | Y | 0.0085593 | 0.33905 | 0.020919 | 0.19154 | 0.0085593 | North | N | 0.0085593 | 0
505 | NTHTEXAS | 3 | 38 | 0.14608 | north | Y | 0.0085593 | 0.33905 | 0.020919 | 0.19154 | 0.0085593 | North | N | 0.0085593 | 0
580 | JCKCNTY8 | 1 | 288 | 0.14548 | north | Y | 0.0079523 | 0.33844 | 0.020312 | 0.19093 | 0.0079523 | North | N | 0.0079523 | 0
581 | JCKCNTY8 | 2 | 147 | 0.14548 | north | Y | 0.0079523 | 0.33844 | 0.020312 | 0.19093 | 0.0079523 | North | N | 0.0079523 | 0
582 | JCKCNTY8 | 3 | 147 | 0.14548 | north | Y | 0.0079523 | 0.33844 | 0.020312 | 0.19093 | 0.0079523 | North | N | 0.0079523 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.14461 | north | Y | 0.0070883 | 0.33758 | 0.019448 | 0.19007 | 0.0070883 | North | N | 0.0070883 | 0
837 | NEWMAN_G | 1 | 40 | 0.14307 | north | Y | 0.0055423 | 0.33603 | 0.017902 | 0.18852 | 0.0055423 | North | N | 0.0055423 | 0
842 | OLINGER_ | 1 | 79 | 0.14304 | north | Y | 0.0055133 | 0.336 | 0.017873 | 0.18849 | 0.0055133 | North | N | 0.0055133 | 0
843 | OLINGER_ | 1 | 106 | 0.14304 | north | Y | 0.0055133 | 0.336 | 0.017873 | 0.18849 | 0.0055133 | North | N | 0.0055133 | 0
844 | OLINGER_ | 1 | 146 | 0.14304 | north | Y | 0.0055133 | 0.336 | 0.017873 | 0.18849 | 0.0055133 | North | N | 0.0055133 | 0
845 | OLINGER_ | 1 | 76 | 0.14304 | north | Y | 0.0055133 | 0.336 | 0.017873 | 0.18849 | 0.0055133 | North | N | 0.0055133 | 0
923 | SPENCER_ | 1 | 60 | 0.14504 | north | Y | 0.0075183 | 0.33801 | 0.019878 | 0.1905 | 0.0075183 | North | N | 0.0075183 | 0
924 | SPENCER_ | 1 | 63 | 0.14504 | north | Y | 0.0075183 | 0.33801 | 0.019878 | 0.1905 | 0.0075183 | North | N | 0.0075183 | 0
948 | STEAM1 | 1 | 20 | 0.14283 | north | Y | 0.0053083 | 0.3358 | 0.017668 | 0.18829 | 0.0053083 | North | N | 0.0053083 | 0
949 | STEAM2 | 1 | 25 | 0.14283 | north | Y | 0.0053083 | 0.3358 | 0.017668 | 0.18829 | 0.0053083 | North | N | 0.0053083 | 0
950 | STEAM3 | 1 | 41 | 0.14283 | north | Y | 0.0053083 | 0.3358 | 0.017668 | 0.18829 | 0.0053083 | North | N | 0.0053083 | 0
990 | GIBN_CRE | 1 | 463 | 0.047651 | north | Y | -0.089875 | 0.24061 | -0.077515 | 0.093105 | 0.077515 | west | Y | 0.089875 | 5.7225
1002 | PBCTAGE_ | A | 66 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1003 | PBCTBGE_ | B | 65 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1004 | PBCTCGE_ | C | 67 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1005 | PBCTDGE_ | D | 67 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1006 | PBCTEGE_ | E | 67 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12292 | west | Y | -0.014609 | 0.31588 | -0.002249 | 0.16837 | 0.002249 | west | N | 0.002249 | 0
1039 | MRGNAG_1 | A | 66 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1040 | MRGNBG_2 | B | 69 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1041 | MRGNCG_3 | C | 69 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1042 | MRGNDG_4 | D | 67 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1043 | MRGNEG_5 | E | 67 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1044 | MRGNFG_6 | F | 65 | 0.12748 | west | Y | -0.010047 | 0.32044 | 0.002313 | 0.17293 | 0.002313 | west | N | 0.002313 | 0
1045 | CALENG1G | 1 | 70 | 0.12682 | west | N | -0.01071 | 0.31978 | 0.00165 | 0.17227 | 0.00165 | west | N | 0.00165 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12682 | west | N | -0.01071 | 0.31978 | 0.00165 | 0.17227 | 0.00165 | west | N | 0.00165 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12682 | west | N | -0.01071 | 0.31978 | 0.00165 | 0.17227 | 0.00165 | west | N | 0.00165 | 0
1058 | LONGSHOR | 1 | 150 | 0.12718 | west | Y | -0.010343 | 0.32015 | 0.002017 | 0.17264 | 0.002017 | west | N | 0.002017 | 0
1058 | LONGSHOR | 2 | 220 | 0.12718 | west | Y | -0.010343 | 0.32015 | 0.002017 | 0.17264 | 0.002017 | west | N | 0.002017 | 0
1061 | CIELOGEN | 1 | 99 | 0.12774 | west | Y | -0.0097817 | 0.32071 | 0.002578 | 0.1732 | 0.002578 | west | N | 0.002578 | 0
1062 | CIELOGEN | 1 | 61 | 0.12774 | west | Y | -0.0097817 | 0.32071 | 0.002578 | 0.1732 | 0.002578 | west | N | 0.002578 | 0
1068 | SCURRYCW | 1 | 141 | 0.12771 | west | Y | -0.0098187 | 0.32067 | 0.002541 | 0.17316 | 0.002541 | west | N | 0.002541 | 0
1069 | KINDERMG | 1 | 25 | 0.12774 | west | N | -0.0097817 | 0.32071 | 0.002578 | 0.1732 | 0.002578 | west | N | 0.002578 | 0
1070 | KINDERMG | 1 | 45.7 | 0.12774 | west | N | -0.0097817 | 0.32071 | 0.002578 | 0.1732 | 0.002578 | west | N | 0.002578 | 0
1071 | KINDERMG | 1 | 45.7 | 0.12774 | west | N | -0.0097817 | 0.32071 | 0.002578 | 0.1732 | 0.002578 | west | N | 0.002578 | 0
1073 | SCURRYCW | 2 | 120 | 0.12771 | west | Y | -0.0098187 | 0.32067 | 0.002541 | 0.17316 | 0.002541 | west | N | 0.002541 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12563 | west | N | -0.011897 | 0.31859 | 0.00046301 | 0.17108 | 0.00046301 | west | N | 0.00046301 | 0
1326 | STANTONW | 1 | 100.5 | 0.12529 | west | Y | -0.012234 | 0.31825 | 0.00012601 | 0.17075 | 0.00012601 | west | N | 0.00012601 | 0
1327 | WILDHRSE | 1 | 120 | 0.12641 | west | Y | -0.011119 | 0.31937 | 0.001241 | 0.17186 | 0.001241 | west | N | 0.001241 | 0
1328 | OCOTILLO | 1 | 58 | 0.12527 | west | Y | -0.012258 | 0.31823 | 0.00010201 | 0.17072 | 0.00010201 | west | N | 0.00010201 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12558 | west | Y | -0.011949 | 0.31854 | 0.00041101 | 0.17103 | 0.00041101 | west | N | 0.00041101 | 0
1343 | TRENTIPP | 1 | 150 | 0.1283 | west | Y | -0.0092257 | 0.32126 | 0.003134 | 0.17375 | 0.003134 | west | N | 0.003134 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12382 | west | Y | -0.013704 | 0.31678 | -0.001344 | 0.16928 | 0.001344 | west | N | 0.001344 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12382 | west | Y | -0.013704 | 0.31678 | -0.001344 | 0.16928 | 0.001344 | west | N | 0.001344 | 0
1354 | AEPWIND_ | 1 | 101 | 0.1283 | west | Y | -0.0092257 | 0.32126 | 0.003134 | 0.17375 | 0.003134 | west | N | 0.003134 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12646 | west | Y | -0.011064 | 0.31942 | 0.001296 | 0.17192 | 0.001296 | west | N | 0.001296 | 0
1432 | GRHAMSES | 2 | 366 | 0.14001 | north | Y | 0.0024813 | 0.33297 | 0.014841 | 0.18546 | 0.0024813 | North | N | 0.0024813 | 0
1433 | GRHAMSES | 1 | 242 | 0.13972 | north | Y | 0.0021973 | 0.33269 | 0.014557 | 0.18518 | 0.0021973 | North | N | 0.0021973 | 0
1437 | MESQUITW | 1 | 400 | 0.13371 | west | Y | -0.0038147 | 0.32667 | 0.008545 | 0.17917 | 0.0038147 | North | Y | 0.008545 | 1.8921
1438 | MESQUITW | 1 | 236 | 0.13372 | west | Y | -0.0038057 | 0.32668 | 0.008554 | 0.17917 | 0.0038057 | North | Y | 0.008554 | 1.1206
1442 | COKFIELD | 1 | 165 | 0.13523 | west | Y | -0.0022967 | 0.32819 | 0.010063 | 0.18068 | 0.0022967 | North | Y | 0.010063 | 1.2814
1453 | WCPWRCO_ | 1 | 204 | 0.14353 | north | Y | 0.0060033 | 0.33649 | 0.018363 | 0.18898 | 0.0060033 | North | N | 0.0060033 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.14353 | north | Y | 0.0060033 | 0.33649 | 0.018363 | 0.18898 | 0.0060033 | North | N | 0.0060033 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.14353 | north | Y | 0.0060033 | 0.33649 | 0.018363 | 0.18898 | 0.0060033 | North | N | 0.0060033 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.14018 | west | Y | 0.0026523 | 0.33314 | 0.015012 | 0.18563 | 0.0026523 | North | Y | 0.015012 | 0.24719
1479 | WFCOGEN_ | 2 | 20 | 0.14018 | west | Y | 0.0026523 | 0.33314 | 0.015012 | 0.18563 | 0.0026523 | North | Y | 0.015012 | 0.24719
1482 | WFCOGEN_ | 1 | 20 | 0.14018 | west | Y | 0.0026523 | 0.33314 | 0.015012 | 0.18563 | 0.0026523 | North | Y | 0.015012 | 0.24719
1482 | WFCOGEN_ | 2 | 17 | 0.14018 | west | Y | 0.0026523 | 0.33314 | 0.015012 | 0.18563 | 0.0026523 | North | Y | 0.015012 | 0.21012
1600 | BARTNWND | 1 | 120 | 0.14284 | north | Y | 0.0053193 | 0.33581 | 0.017679 | 0.1883 | 0.0053193 | North | N | 0.0053193 | 0
1643 | SLSTR1PP | 1 | 60 | 0.14151 | north | Y | 0.0039823 | 0.33447 | 0.016342 | 0.18696 | 0.0039823 | North | N | 0.0039823 | 0
1675 | PEC_1G | 1 | 75 | 0.14308 | north | N | 0.0055523 | 0.33604 | 0.017912 | 0.18853 | 0.0055523 | North | N | 0.0055523 | 0
1676 | PEC_2G | 2 | 79.6 | 0.14308 | north | N | 0.0055523 | 0.33604 | 0.017912 | 0.18853 | 0.0055523 | North | N | 0.0055523 | 0
1677 | PEC_3G | 3 | 88.4 | 0.14308 | north | N | 0.0055523 | 0.33604 | 0.017912 | 0.18853 | 0.0055523 | North | N | 0.0055523 | 0
1678 | LAMARPWR | 1 | 160 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1679 | LAMARPWR | 2 | 156 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1680 | LAMARPWR | 3 | 196 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1681 | LAMARPWR | 4 | 156 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1682 | LAMARPWR | 5 | 157 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1683 | LAMARPWR | 6 | 198 | 0.14319 | north | Y | 0.0056623 | 0.33615 | 0.018022 | 0.18864 | 0.0056623 | North | N | 0.0056623 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14345 | north | Y | 0.0059253 | 0.33641 | 0.018285 | 0.18891 | 0.0059253 | North | N | 0.0059253 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14345 | north | Y | 0.0059253 | 0.33641 | 0.018285 | 0.18891 | 0.0059253 | North | N | 0.0059253 | 0
1689 | VALLEY_3 | 3 | 370 | 0.1433 | north | Y | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
1701 | MOSES_1G | 1 | 558 | 0.14301 | north | Y | 0.0054873 | 0.33598 | 0.017847 | 0.18847 | 0.0054873 | North | N | 0.0054873 | 0
1702 | MOSES_2G | 2 | 579 | 0.14301 | north | Y | 0.0054873 | 0.33598 | 0.017847 | 0.18847 | 0.0054873 | North | N | 0.0054873 | 0
1703 | MOSES_3G | 3 | 808 | 0.14301 | north | Y | 0.0054873 | 0.33598 | 0.017847 | 0.18847 | 0.0054873 | North | N | 0.0054873 | 0
1861 | EAGLEMNT | MB | 112 | 0.147 | north | Y | 0.0094723 | 0.33996 | 0.021832 | 0.19245 | 0.0094723 | North | N | 0.0094723 | 0
1862 | EAGLEMNT | MB | 100 | 0.147 | north | Y | 0.0094723 | 0.33996 | 0.021832 | 0.19245 | 0.0094723 | North | N | 0.0094723 | 0
1863 | EAGLEMNT | MB | 378 | 0.147 | north | Y | 0.0094723 | 0.33996 | 0.021832 | 0.19245 | 0.0094723 | North | N | 0.0094723 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.14811 | north | Y | 0.010587 | 0.34108 | 0.022947 | 0.19357 | 0.010587 | North | N | 0.010587 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.14811 | north | Y | 0.010587 | 0.34108 | 0.022947 | 0.19357 | 0.010587 | North | N | 0.010587 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.14811 | north | Y | 0.010587 | 0.34108 | 0.022947 | 0.19357 | 0.010587 | North | N | 0.010587 | 0
1889 | DECRDOVA | MB | 770 | 0.1486 | north | Y | 0.011072 | 0.34156 | 0.023432 | 0.19405 | 0.011072 | North | N | 0.011072 | 0
1892 | DECRDOVA | A | 70 | 0.14958 | north | Y | 0.012054 | 0.34254 | 0.024414 | 0.19503 | 0.012054 | North | N | 0.012054 | 0
1893 | DECRDOVA | B | 69 | 0.14958 | north | Y | 0.012054 | 0.34254 | 0.024414 | 0.19503 | 0.012054 | North | N | 0.012054 | 0
1894 | DECRDOVA | C | 69 | 0.14958 | north | Y | 0.012054 | 0.34254 | 0.024414 | 0.19503 | 0.012054 | North | N | 0.012054 | 0
1895 | DECRDOVA | D | 68 | 0.14958 | north | Y | 0.012054 | 0.34254 | 0.024414 | 0.19503 | 0.012054 | North | N | 0.012054 | 0
1898 | COMCHEPK | 1 | 1157 | 0.14759 | north | N | 0.010066 | 0.34055 | 0.022426 | 0.19305 | 0.010066 | North | N | 0.010066 | 0
1899 | COMCHEPK | 2 | 1158 | 0.14759 | north | N | 0.010066 | 0.34055 | 0.022426 | 0.19305 | 0.010066 | North | N | 0.010066 | 0
1937 | MDLTHELP | 5 | 224 | 0.15661 | north | Y | 0.019088 | 0.34958 | 0.031448 | 0.20207 | 0.019088 | North | N | 0.019088 | 0
1938 | MDLTHELP | 6 | 226 | 0.15661 | north | Y | 0.019088 | 0.34958 | 0.031448 | 0.20207 | 0.019088 | North | N | 0.019088 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.15649 | north | Y | 0.018962 | 0.34945 | 0.031322 | 0.20194 | 0.018962 | North | N | 0.018962 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.15649 | north | Y | 0.018962 | 0.34945 | 0.031322 | 0.20194 | 0.018962 | North | N | 0.018962 | 0
1943 | MDLTHELP | 3 | 212 | 0.15661 | north | Y | 0.019088 | 0.34958 | 0.031448 | 0.20207 | 0.019088 | North | N | 0.019088 | 0
1944 | MDLTHELP | 4 | 211 | 0.15661 | north | Y | 0.019088 | 0.34958 | 0.031448 | 0.20207 | 0.019088 | North | N | 0.019088 | 0
1947 | HANDLEY_ | 3 | 395 | 0.14987 | north | Y | 0.012344 | 0.34283 | 0.024704 | 0.19532 | 0.012344 | North | N | 0.012344 | 0
1948 | HANDLEY_ | 4 | 435 | 0.14957 | north | Y | 0.01204 | 0.34253 | 0.0244 | 0.19502 | 0.01204 | North | N | 0.01204 | 0
1949 | HANDLEY_ | 5 | 435 | 0.14987 | north | Y | 0.012344 | 0.34283 | 0.024704 | 0.19532 | 0.012344 | North | N | 0.012344 | 0
2371 | COLLIN_1 | MB | 138 | 0.14433 | north | Y | 0.0068043 | 0.33729 | 0.019164 | 0.18978 | 0.0068043 | North | N | 0.0068043 | 0
2413 | MTCK6_G | 6 | 118 | 0.14576 | north | Y | 0.0082303 | 0.33872 | 0.02059 | 0.19121 | 0.0082303 | North | N | 0.0082303 | 0
2414 | MTCK7_G | 7 | 115 | 0.14576 | north | Y | 0.0082303 | 0.33872 | 0.02059 | 0.19121 | 0.0082303 | North | N | 0.0082303 | 0
2417 | MTCK8_G | 8 | 556 | 0.14576 | north | Y | 0.0082303 | 0.33872 | 0.02059 | 0.19121 | 0.0082303 | North | N | 0.0082303 | 0
2451 | LKHB1_G | 1 | 388 | 0.143 | north | Y | 0.0054703 | 0.33596 | 0.01783 | 0.18845 | 0.0054703 | North | N | 0.0054703 | 0
2452 | LKHB2_G | 2 | 515 | 0.143 | north | Y | 0.0054703 | 0.33596 | 0.01783 | 0.18845 | 0.0054703 | North | N | 0.0054703 | 0
3097 | MARTLAKE | 1 | 785 | 0.13642 | north | Y | -0.0011077 | 0.32938 | 0.011252 | 0.18187 | 0.0011077 | North | N | 0.0011077 | 0
3098 | MARTLAKE | 2 | 795 | 0.13642 | north | Y | -0.0011077 | 0.32938 | 0.011252 | 0.18187 | 0.0011077 | North | N | 0.0011077 | 0
3099 | MARTLAKE | 3 | 780 | 0.13642 | north | Y | -0.0011077 | 0.32938 | 0.011252 | 0.18187 | 0.0011077 | North | N | 0.0011077 | 0
3107 | STRYKER_ | 1 | 182 | 0.13422 | north | Y | -0.0033047 | 0.32718 | 0.009055 | 0.17968 | 0.0033047 | North | N | 0.0033047 | 0
3108 | STRYKER_ | 2 | 484 | 0.13422 | north | Y | -0.0033047 | 0.32718 | 0.009055 | 0.17968 | 0.0033047 | North | N | 0.0033047 | 0
3126 | TRINIDAD | 1 | 224 | 0.1408 | north | Y | 0.0032743 | 0.33376 | 0.015634 | 0.18625 | 0.0032743 | North | N | 0.0032743 | 0
3309 | ASPN_G | 1 | 50 | 0.13483 | north | Y | -0.0026987 | 0.32779 | 0.009661 | 0.18028 | 0.0026987 | North | N | 0.0026987 | 0
3348 | CHAMPION | MB | 42 | 0.13489 | north | N | -0.0026397 | 0.32785 | 0.00972 | 0.18034 | 0.0026397 | North | N | 0.0026397 | 0
3381 | BBRN_1G | 1 | 615 | 0.12593 | north | Y | -0.0116 | 0.31889 | 0.00076001 | 0.17138 | 0.00076001 | west | Y | 0.0116 | 6.6664
3382 | BBRN_2G | 2 | 587 | 0.12593 | north | Y | -0.0116 | 0.31889 | 0.00076001 | 0.17138 | 0.00076001 | west | Y | 0.0116 | 6.3629
3403 | THOUSE_1 | MB | 537 | 0.23958 | north | Y | 0.10205 | 0.43254 | 0.11441 | 0.28503 | 0.10205 | North | N | 0.10205 | 0
3404 | THOUSE_2 | 2 | 787 | 0.23958 | north | Y | 0.10205 | 0.43254 | 0.11441 | 0.28503 | 0.10205 | North | N | 0.10205 | 0
3416 | LAKE_CRK | MB | 75 | 0.19897 | north | Y | 0.06144 | 0.39193 | 0.0738 | 0.24442 | 0.06144 | North | N | 0.06144 | 0
3417 | LAKE_CRK | MB | 222 | 0.19897 | north | Y | 0.06144 | 0.39193 | 0.0738 | 0.24442 | 0.06144 | North | N | 0.06144 | 0
3432 | SANDOW_4 | 4 | 569 | -0.2813 | south | Y | -0.41883 | -0.088337 | -0.40647 | -0.23585 | 0.088337 | south | N | 0.088337 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.18472 | south | Y | -0.32225 | 0.0082388 | -0.30989 | -0.13927 | 0.0082388 | south | N | 0.0082388 | 0
5031 | BRA_VHBC | 1 | 46 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5032 | BRA_VHBC | 2 | 47 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5033 | BRA_VHBC | 3 | 46 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5034 | BRA_VHBC | 4 | 46 | -0.18482 | south | Y | -0.32234 | 0.0081438 | -0.30998 | -0.13936 | 0.0081438 | south | N | 0.0081438 | 0
5111 | CALAVER_ | 1 | 424 | -0.18517 | south | Y | -0.32269 | 0.0077948 | -0.31033 | -0.13971 | 0.0077948 | south | N | 0.0077948 | 0
5112 | CALAVER_ | 2 | 425 | -0.18517 | south | Y | -0.32269 | 0.0077948 | -0.31033 | -0.13971 | 0.0077948 | south | N | 0.0077948 | 0
5264 | LEON_LCP | 3 | 58 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5265 | LEON_LCP | 4 | 89 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5266 | LEON_LCP | 1 | 44 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5267 | LEON_LCP | 2 | 44 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5268 | LEON_LCP | 3 | 43 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5269 | LEON_LCP | 4 | 45 | -0.18368 | south | Y | -0.32121 | 0.0092818 | -0.30885 | -0.13823 | 0.0092818 | south | N | 0.0092818 | 0
5396 | CALAVER_ | 1 | 412 | -0.18502 | south | Y | -0.32255 | 0.0079398 | -0.31019 | -0.13957 | 0.0079398 | south | N | 0.0079398 | 0
5397 | CALAVER_ | 2 | 400 | -0.18502 | south | Y | -0.32255 | 0.0079398 | -0.31019 | -0.13957 | 0.0079398 | south | N | 0.0079398 | 0
5401 | CALAVER_ | 1 | 546 | -0.18357 | south | Y | -0.3211 | 0.0093918 | -0.30874 | -0.13812 | 0.0093918 | south | N | 0.0093918 | 0
5402 | CALAVER_ | 2 | 750 | -0.18357 | south | Y | -0.3211 | 0.0093918 | -0.30874 | -0.13812 | 0.0093918 | south | N | 0.0093918 | 0
5436 | TUTTL_WB | MB | 61 | -0.18574 | south | Y | -0.32326 | 0.0072278 | -0.3109 | -0.14028 | 0.0072278 | south | N | 0.0072278 | 0
5438 | TUTTL_WB | MB | 95 | -0.18574 | south | Y | -0.32326 | 0.0072278 | -0.3109 | -0.14028 | 0.0072278 | south | N | 0.0072278 | 0
5439 | TUTTL_WB | MB | 151 | -0.18574 | south | Y | -0.32326 | 0.0072278 | -0.3109 | -0.14028 | 0.0072278 | south | N | 0.0072278 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.18442 | south | Y | -0.32195 | 0.0085388 | -0.30959 | -0.13897 | 0.0085388 | south | N | 0.0085388 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.18442 | south | Y | -0.32195 | 0.0085388 | -0.30959 | -0.13897 | 0.0085388 | south | N | 0.0085388 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.18442 | south | Y | -0.32195 | 0.0085388 | -0.30959 | -0.13897 | 0.0085388 | south | N | 0.0085388 | 0
5503 | RAYBURNG | 1 | 22 | -0.14932 | south | Y | -0.28685 | 0.043643 | -0.27449 | -0.10387 | 0.043643 | south | N | 0.043643 | 0
5505 | RAYBURNG | 1 | 11 | -0.14932 | south | Y | -0.28685 | 0.043643 | -0.27449 | -0.10387 | 0.043643 | south | N | 0.043643 | 0
5506 | RAYBURNG | 1 | 11 | -0.14932 | south | Y | -0.28685 | 0.043643 | -0.27449 | -0.10387 | 0.043643 | south | N | 0.043643 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.15066 | south | Y | -0.28818 | 0.042307 | -0.27582 | -0.1052 | 0.042307 | south | N | 0.042307 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.15066 | south | Y | -0.28818 | 0.042307 | -0.27582 | -0.1052 | 0.042307 | south | N | 0.042307 | 0
5511 | RAYBURNC | 1 | 46 | -0.15066 | south | Y | -0.28818 | 0.042307 | -0.27582 | -0.1052 | 0.042307 | south | N | 0.042307 | 0
5512 | RAYBURNC | 1 | 48 | -0.15066 | south | Y | -0.28818 | 0.042307 | -0.27582 | -0.1052 | 0.042307 | south | N | 0.042307 | 0
5728 | FALCONHY | 2 | 12 | -0.15722 | south | N | -0.29475 | 0.035739 | -0.28239 | -0.11177 | 0.035739 | south | N | 0.035739 | 0
5729 | FALCONHY | 3 | 11 | -0.15722 | south | N | -0.29475 | 0.035739 | -0.28239 | -0.11177 | 0.035739 | south | N | 0.035739 | 0
5890 | PEARSALL | 1 | 24 | -0.16385 | south | Y | -0.30138 | 0.029111 | -0.28902 | -0.1184 | 0.029111 | south | N | 0.029111 | 0
5891 | PEARSALL | 1 | 24 | -0.16385 | south | Y | -0.30138 | 0.029111 | -0.28902 | -0.1184 | 0.029111 | south | N | 0.029111 | 0
5892 | PEARSALL | 1 | 23 | -0.16385 | south | Y | -0.30138 | 0.029111 | -0.28902 | -0.1184 | 0.029111 | south | N | 0.029111 | 0
5903 | SANMIGUE | 1 | 396 | -0.17391 | south | Y | -0.31143 | 0.019054 | -0.29907 | -0.12845 | 0.019054 | south | N | 0.019054 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.097608 | houston | N | -0.23513 | 0.095355 | -0.22277 | -0.052154 | 0.052154 | houston | N | 0.052154 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.097608 | houston | N | -0.23513 | 0.095355 | -0.22277 | -0.052154 | 0.052154 | houston | N | 0.052154 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.13753 | 0
5932 | SI_RAY9 | 9 | 38 | -0.15486 | south | Y | -0.29238 | 0.038106 | -0.28002 | -0.1094 | 0.038106 | south | N | 0.038106 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.15486 | south | Y | -0.29238 | 0.038106 | -0.28002 | -0.1094 | 0.038106 | south | N | 0.038106 | 0
5934 | SI_RAY5 | 5 | 15 | -0.15486 | south | Y | -0.29238 | 0.038106 | -0.28002 | -0.1094 | 0.038106 | south | N | 0.038106 | 0
5935 | SI_RAY10 | 10 | 47 | -0.15486 | south | Y | -0.29238 | 0.038106 | -0.28002 | -0.1094 | 0.038106 | south | N | 0.038106 | 0
6016 | SWMESA | 1 | 75 | 0.11025 | west | Y | -0.027279 | 0.30321 | -0.014919 | 0.1557 | 0.014919 | west | N | 0.014919 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.12517 | 0
6144 | MCADOO1A | 1 | 150 | 0.12954 | west | Y | -0.0079807 | 0.32251 | 0.004379 | 0.175 | 0.004379 | west | N | 0.004379 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.12259 | west | Y | -0.01494 | 0.31555 | -0.00258 | 0.16804 | 0.00258 | west | N | 0.00258 | 0
6476 | LANGFORD | 1 | 150 | 0.056431 | west | Y | -0.081095 | 0.24939 | -0.068735 | 0.10189 | 0.068735 | west | N | 0.068735 | 0
6637 | SNYDERW1 | 1 | 63 | 0.1276 | west | Y | -0.0099247 | 0.32056 | 0.002435 | 0.17306 | 0.002435 | west | N | 0.002435 | 0
6752 | OKLA0A | 1 | 649.7 | 0.13639 | west | Y | -0.0011307 | 0.32936 | 0.011229 | 0.18185 | 0.0011307 | North | Y | 0.011229 | 6.5609
6948 | DENISNDM | 1 | 40 | 0.14359 | north | N | 0.0060673 | 0.33656 | 0.018427 | 0.18905 | 0.0060673 | North | N | 0.0060673 | 0
6948 | DENISNDM | 2 | 40 | 0.14359 | north | N | 0.0060673 | 0.33656 | 0.018427 | 0.18905 | 0.0060673 | North | N | 0.0060673 | 0
7000 | L_FERGUS | 1 | 422 | -0.19242 | south | Y | -0.32995 | 0.00053876 | -0.31759 | -0.14697 | 0.00053876 | south | N | 0.00053876 | 0
7004 | L_SIMGID | 1 | 132 | -0.22885 | south | Y | -0.36638 | -0.035889 | -0.35402 | -0.1834 | 0.035889 | south | N | 0.035889 | 0
7005 | L_SIMGID | 2 | 134 | -0.22885 | south | Y | -0.36638 | -0.035889 | -0.35402 | -0.1834 | 0.035889 | south | N | 0.035889 | 0
7006 | L_SIMGID | 3 | 323 | -0.22885 | south | Y | -0.36638 | -0.035889 | -0.35402 | -0.1834 | 0.035889 | south | N | 0.035889 | 0
7007 | L_LOSTPI | 1 | 158 | -0.23687 | south | Y | -0.37439 | -0.043903 | -0.36203 | -0.19141 | 0.043903 | south | N | 0.043903 | 0
7008 | L_LOSTPI | 2 | 160 | -0.23687 | south | Y | -0.37439 | -0.043903 | -0.36203 | -0.19141 | 0.043903 | south | N | 0.043903 | 0
7009 | L_LOSTPI | 3 | 175 | -0.23687 | south | Y | -0.37439 | -0.043903 | -0.36203 | -0.19141 | 0.043903 | south | N | 0.043903 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.21024 | south | Y | -0.34776 | -0.017275 | -0.3354 | -0.16478 | 0.017275 | south | N | 0.017275 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.21024 | south | Y | -0.34776 | -0.017275 | -0.3354 | -0.16478 | 0.017275 | south | N | 0.017275 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.21002 | south | Y | -0.34755 | -0.017061 | -0.33519 | -0.16457 | 0.017061 | south | N | 0.017061 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.20436 | south | Y | -0.34188 | -0.011394 | -0.32952 | -0.1589 | 0.011394 | south | N | 0.011394 | 0
7015 | L_HAYSEN | 2 | 225 | -0.20436 | south | Y | -0.34188 | -0.011394 | -0.32952 | -0.1589 | 0.011394 | south | N | 0.011394 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.20436 | south | Y | -0.34188 | -0.011394 | -0.32952 | -0.1589 | 0.011394 | south | N | 0.011394 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.20436 | south | Y | -0.34188 | -0.011394 | -0.32952 | -0.1589 | 0.011394 | south | N | 0.011394 | 0
7020 | L_AUSTPL | 1 | 8 | -0.23444 | south | N | -0.37197 | -0.04148 | -0.35961 | -0.18899 | 0.04148 | south | N | 0.04148 | 0
7020 | L_AUSTPL | 2 | 8 | -0.23444 | south | N | -0.37197 | -0.04148 | -0.35961 | -0.18899 | 0.04148 | south | N | 0.04148 | 0
7022 | L_BUCHAN | 1 | 18 | -0.18443 | south | N | -0.32195 | 0.0085378 | -0.30959 | -0.13897 | 0.0085378 | south | N | 0.0085378 | 0
7023 | L_BUCHAN | 2 | 18 | -0.18443 | south | N | -0.32195 | 0.0085378 | -0.30959 | -0.13897 | 0.0085378 | south | N | 0.0085378 | 0
7024 | L_BUCHAN | 3 | 15 | -0.18443 | south | N | -0.32195 | 0.0085378 | -0.30959 | -0.13897 | 0.0085378 | south | N | 0.0085378 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.18349 | south | N | -0.32101 | 0.0094768 | -0.30865 | -0.13803 | 0.0094768 | south | N | 0.0094768 | 0
7028 | L_MARBFA | 1 | 18 | -0.20172 | south | N | -0.33924 | -0.0087532 | -0.32688 | -0.15626 | 0.0087532 | south | N | 0.0087532 | 0
7029 | L_MARBFA | 2 | 18 | -0.20172 | south | N | -0.33924 | -0.0087532 | -0.32688 | -0.15626 | 0.0087532 | south | N | 0.0087532 | 0
7031 | L_MARSFO | 1 | 35 | -0.22279 | south | N | -0.36031 | -0.029824 | -0.34795 | -0.17733 | 0.029824 | south | N | 0.029824 | 0
7032 | L_MARSFO | 2 | 34 | -0.22279 | south | N | -0.36031 | -0.029824 | -0.34795 | -0.17733 | 0.029824 | south | N | 0.029824 | 0
7033 | L_MARSFO | 3 | 35 | -0.22279 | south | N | -0.36031 | -0.029824 | -0.34795 | -0.17733 | 0.029824 | south | N | 0.029824 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.1937 | south | N | -0.33123 | -0.00073724 | -0.31887 | -0.14825 | 0.00073724 | south | N | 0.00073724 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.1937 | south | N | -0.33123 | -0.00073724 | -0.31887 | -0.14825 | 0.00073724 | south | N | 0.00073724 | 0
7038 | L_DELAWA | 1 | 35 | 0.12303 | west | Y | -0.014495 | 0.31599 | -0.002135 | 0.16849 | 0.002135 | west | N | 0.002135 | 0
7038 | L_DELAWA | 2 | 30 | 0.12303 | west | Y | -0.014495 | 0.31599 | -0.002135 | 0.16849 | 0.002135 | west | N | 0.002135 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.21011 | south | Y | -0.34764 | -0.017149 | -0.33528 | -0.16466 | 0.017149 | south | N | 0.017149 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.21011 | south | Y | -0.34764 | -0.017149 | -0.33528 | -0.16466 | 0.017149 | south | N | 0.017149 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.21011 | south | Y | -0.34764 | -0.017149 | -0.33528 | -0.16466 | 0.017149 | south | N | 0.017149 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.21011 | south | Y | -0.34764 | -0.017149 | -0.33528 | -0.16466 | 0.017149 | south | N | 0.017149 | 0
7487 | L_CANYHY | 1 | 6 | -0.20737 | south | N | -0.34489 | -0.014406 | -0.33253 | -0.16191 | 0.014406 | south | N | 0.014406 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.19716 | south | N | -0.33468 | -0.0041962 | -0.32232 | -0.1517 | 0.0041962 | south | N | 0.0041962 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.19716 | south | N | -0.33468 | -0.0041962 | -0.32232 | -0.1517 | 0.0041962 | south | N | 0.0041962 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.19716 | south | N | -0.33468 | -0.0041962 | -0.32232 | -0.1517 | 0.0041962 | south | N | 0.0041962 | 0
7609 | L_SCHUMA | 1 | 4 | -0.19451 | south | N | -0.33203 | -0.0015432 | -0.31967 | -0.14905 | 0.0015432 | south | N | 0.0015432 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.19436 | south | N | -0.33189 | -0.0013972 | -0.31953 | -0.14891 | 0.0013972 | south | N | 0.0013972 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.19436 | south | N | -0.33189 | -0.0013972 | -0.31953 | -0.14891 | 0.0013972 | south | N | 0.0013972 | 0
7800 | L_GUADGE | 1 | 147 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7801 | L_GUADGE | 2 | 138 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7802 | L_GUADGE | 3 | 140 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7803 | L_GUADGE | 4 | 147 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7804 | L_GUADGE | 5 | 182 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7805 | L_GUADGE | 6 | 198 | -0.19007 | south | Y | -0.32759 | 0.0028978 | -0.31523 | -0.14461 | 0.0028978 | south | N | 0.0028978 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.2375 | south | Y | -0.37503 | -0.044537 | -0.36267 | -0.19205 | 0.044537 | south | N | 0.044537 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.2375 | south | Y | -0.37503 | -0.044537 | -0.36267 | -0.19205 | 0.044537 | south | N | 0.044537 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.2375 | south | Y | -0.37503 | -0.044537 | -0.36267 | -0.19205 | 0.044537 | south | N | 0.044537 | 0
7810 | L_RIONOG | 1 | 142 | -0.19701 | south | Y | -0.33454 | -0.0040472 | -0.32218 | -0.15156 | 0.0040472 | south | N | 0.0040472 | 0
7811 | L_RIONOG | 2 | 145 | -0.19701 | south | Y | -0.33454 | -0.0040472 | -0.32218 | -0.15156 | 0.0040472 | south | N | 0.0040472 | 0
7812 | L_RIONOG | 3 | 151 | -0.19701 | south | Y | -0.33454 | -0.0040472 | -0.32218 | -0.15156 | 0.0040472 | south | N | 0.0040472 | 0
7813 | L_RIONOG | 4 | 290 | -0.19701 | south | Y | -0.33454 | -0.0040472 | -0.32218 | -0.15156 | 0.0040472 | south | N | 0.0040472 | 0
8032 | AMISTADH | 1 | 33 | -0.088959 | south | N | -0.22648 | 0.104 | -0.21412 | -0.043505 | 0.043505 | houston | Y | 0.104 | 0
8033 | AMISTADH | 2 | 25 | -0.088959 | south | N | -0.22648 | 0.104 | -0.21412 | -0.043505 | 0.043505 | houston | Y | 0.104 | 0
8048 | FALCONHY | 1 | 12 | -0.15722 | south | N | -0.29475 | 0.035739 | -0.28239 | -0.11177 | 0.035739 | south | N | 0.035739 | 0
8066 | DUP1V#1 | 1 | 73 | -0.15096 | south | N | -0.28849 | 0.042002 | -0.27613 | -0.10551 | 0.042002 | south | N | 0.042002 | 0
8134 | FOR69CG0 | 1 | 79 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8138 | FOR69CG0 | 2 | 81 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8147 | UCAR #2 | 10 | 28 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
8148 | UCAR #1 | 2 | 7 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
8153 | FOR69CG0 | 3 | 79 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8154 | FOR69CG0 | 4 | 80 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8156 | FOR69CG0 | 6 | 25 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8157 | FOR69CG0 | 7 | 46 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
8161 | COLETOU1 | 1 | 629 | -0.15971 | south | Y | -0.29724 | 0.033251 | -0.28488 | -0.11426 | 0.033251 | south | N | 0.033251 | 0
8173 | VICEC51A | 5 | 144 | -0.15262 | south | Y | -0.29014 | 0.040347 | -0.27778 | -0.10716 | 0.040347 | south | N | 0.040347 | 0
8174 | VICEC61A | 6 | 188 | -0.15262 | south | Y | -0.29014 | 0.040347 | -0.27778 | -0.10716 | 0.040347 | south | N | 0.040347 | 0
8189 | CUERO 2 | 1 | 12 | -0.18285 | south | N | -0.32038 | 0.010112 | -0.30802 | -0.1374 | 0.010112 | south | N | 0.010112 | 0
8262 | ELPS | 1 | 6 | -0.11226 | south | N | -0.24979 | 0.080699 | -0.23743 | -0.06681 | 0.06681 | houston | Y | 0.080699 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8442 | NBEC71A | 1 | 336 | -0.15325 | south | Y | -0.29077 | 0.039715 | -0.27841 | -0.10779 | 0.039715 | south | N | 0.039715 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.13753 | 0.19296 | -0.12517 | 0.045454 | 0.045454 | houston | Y | 0.19296 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.15359 | south | Y | -0.29112 | 0.039372 | -0.27876 | -0.10814 | 0.039372 | south | N | 0.039372 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.15359 | south | Y | -0.29112 | 0.039372 | -0.27876 | -0.10814 | 0.039372 | south | N | 0.039372 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.1538 | south | N | -0.29133 | 0.039161 | -0.27897 | -0.10835 | 0.039161 | south | N | 0.039161 | 0
8506 | VAL #1 | 1 | 25 | -0.15364 | south | N | -0.29117 | 0.039319 | -0.27881 | -0.10819 | 0.039319 | south | N | 0.039319 | 0
8507 | VAL #2 | 2 | 25 | -0.15364 | south | N | -0.29117 | 0.039319 | -0.27881 | -0.10819 | 0.039319 | south | N | 0.039319 | 0
8511 | OXY_CC0A | 1 | 38 | -0.15379 | south | N | -0.29132 | 0.03917 | -0.27896 | -0.10834 | 0.03917 | south | N | 0.03917 | 0
8517 | CELANEBI | 1 | 29 | -0.15452 | south | N | -0.29204 | 0.038444 | -0.27968 | -0.10906 | 0.038444 | south | N | 0.038444 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.15327 | south | N | -0.29079 | 0.039697 | -0.27843 | -0.10781 | 0.039697 | south | N | 0.039697 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.15327 | south | N | -0.29079 | 0.039697 | -0.27843 | -0.10781 | 0.039697 | south | N | 0.039697 | 0
8562 | CNOPST1 | 3 | 153 | -0.15327 | south | N | -0.29079 | 0.039697 | -0.27843 | -0.10781 | 0.039697 | south | N | 0.039697 | 0
8926 | LGE_GT10 | 1 | 158 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8927 | LGE_GT20 | 2 | 153 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8928 | LGE_STG0 | 3 | 100 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8930 | ICPGN10A | 1 | 145 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8931 | ICPGN20A | 2 | 147 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8932 | ICPGN30A | 3 | 127 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.15543 | south | Y | -0.29296 | 0.037531 | -0.2806 | -0.10998 | 0.037531 | south | N | 0.037531 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.15543 | south | Y | -0.29296 | 0.037531 | -0.2806 | -0.10998 | 0.037531 | south | N | 0.037531 | 0
8935 | FGNTS201 | 3 | 173 | -0.15543 | south | Y | -0.29296 | 0.037531 | -0.2806 | -0.10998 | 0.037531 | south | N | 0.037531 | 0
8936 | MVGN#1 | 1 | 207 | -0.15515 | south | Y | -0.29267 | 0.037818 | -0.28031 | -0.10969 | 0.037818 | south | N | 0.037818 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.15515 | south | Y | -0.29267 | 0.037818 | -0.28031 | -0.10969 | 0.037818 | south | N | 0.037818 | 0
8938 | MVGN#3 | 3 | 242 | -0.15515 | south | Y | -0.29267 | 0.037818 | -0.28031 | -0.10969 | 0.037818 | south | N | 0.037818 | 0
8981 | HECN1 | 1 | 144 | -0.15514 | south | Y | -0.29267 | 0.037823 | -0.28031 | -0.10969 | 0.037823 | south | N | 0.037823 | 0
8982 | HECN2 | 2 | 144 | -0.15514 | south | Y | -0.29267 | 0.037823 | -0.28031 | -0.10969 | 0.037823 | south | N | 0.037823 | 0
8983 | HECN3 | 3 | 171 | -0.15514 | south | Y | -0.29267 | 0.037823 | -0.28031 | -0.10969 | 0.037823 | south | N | 0.037823 | 0
9000 | DECKR_G1 | 1 | 310 | -0.23631 | south | Y | -0.37383 | -0.043345 | -0.36147 | -0.19085 | 0.043345 | south | N | 0.043345 | 0
9001 | DECKR_G2 | 2 | 413 | -0.23631 | south | Y | -0.37383 | -0.043345 | -0.36147 | -0.19085 | 0.043345 | south | N | 0.043345 | 0
9002 | DECKR_G3 | 3 | 42 | -0.23911 | south | Y | -0.37664 | -0.046151 | -0.36428 | -0.19366 | 0.046151 | south | N | 0.046151 | 0
9003 | DECKR_G4 | 4 | 44 | -0.23911 | south | Y | -0.37664 | -0.046151 | -0.36428 | -0.19366 | 0.046151 | south | N | 0.046151 | 0
9004 | DECKR_G5 | 5 | 44 | -0.23911 | south | Y | -0.37664 | -0.046151 | -0.36428 | -0.19366 | 0.046151 | south | N | 0.046151 | 0
9005 | DECKR_G6 | 6 | 47 | -0.23911 | south | Y | -0.37664 | -0.046151 | -0.36428 | -0.19366 | 0.046151 | south | N | 0.046151 | 0
9016 | SANDH_G1 | 1 | 49 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9017 | SANDH_G2 | 2 | 46 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9018 | SANDH_G3 | 3 | 46 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9019 | SANDH_G4 | 4 | 47 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9020 | SANDHG5A | 5A | 154 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9021 | SANDHG5C | 5C | 148 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9022 | SANDH_G6 | 6 | 48 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
9023 | SANDH_G7 | 7 | 48 | -0.23443 | south | Y | -0.37196 | -0.04147 | -0.3596 | -0.18898 | 0.04147 | south | N | 0.04147 | 0
11001 | NAV1CT | 1 | 70 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.1252 | west | Y | -0.012327 | 0.31816 | 3.3015e-05 | 0.17065 | 3.3015e-05 | west | N | 3.3015e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.12518 | west | Y | -0.012349 | 0.31814 | 1.1015e-05 | 0.17063 | 1.1015e-05 | west | N | 1.1015e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12932 | west | Y | -0.0082107 | 0.32228 | 0.004149 | 0.17477 | 0.004149 | west | N | 0.004149 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12932 | west | Y | -0.0082107 | 0.32228 | 0.004149 | 0.17477 | 0.004149 | west | N | 0.004149 | 0
11058 | PYRON_1G | 1 | 249 | 0.12932 | west | Y | -0.0082107 | 0.32228 | 0.004149 | 0.17477 | 0.004149 | west | N | 0.004149 | 0
11059 | INADALE_ | 1 | 197 | 0.12932 | west | Y | -0.0082107 | 0.32228 | 0.004149 | 0.17477 | 0.004149 | west | N | 0.004149 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12718 | west | Y | -0.010343 | 0.32015 | 0.002017 | 0.17264 | 0.002017 | west | N | 0.002017 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12718 | west | Y | -0.010343 | 0.32015 | 0.002017 | 0.17264 | 0.002017 | west | N | 0.002017 | 0
11147 | NOTREES_ | 1 | 149 | 0.12342 | west | Y | -0.014106 | 0.31638 | -0.001746 | 0.16887 | 0.001746 | west | N | 0.001746 | 0
11309 | BULLCREK | 1 | 180 | 0.12684 | west | Y | -0.010686 | 0.3198 | 0.001674 | 0.17229 | 0.001674 | west | N | 0.001674 | 0
11310 | BULLCREK | 1 | 180 | 0.12684 | west | Y | -0.010686 | 0.3198 | 0.001674 | 0.17229 | 0.001674 | west | N | 0.001674 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12672 | west | Y | -0.010806 | 0.31968 | 0.001554 | 0.17217 | 0.001554 | west | N | 0.001554 | 0
11415 | LORAINE_ | 1 | 125 | 0.12842 | west | Y | -0.0091057 | 0.32138 | 0.003254 | 0.17387 | 0.003254 | west | N | 0.003254 | 0
11416 | LORAINE_ | 1 | 125 | 0.12842 | west | Y | -0.0091057 | 0.32138 | 0.003254 | 0.17387 | 0.003254 | west | N | 0.003254 | 0
11691 | KMICHICT | 1 | 140 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
11692 | KMICHICT | 2 | 141 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
11693 | KMICHIST | 3 | 309 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
11694 | KMICHICT | 4 | 143 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
11695 | KMICHICT | 5 | 144 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
11696 | KMICHIST | 6 | 310 | 0.1433 | north | N | 0.0057743 | 0.33626 | 0.018134 | 0.18875 | 0.0057743 | North | N | 0.0057743 | 0
12322 | ENNSTRAC | 1 | 196 | 0.14683 | north | Y | 0.0093003 | 0.33979 | 0.02166 | 0.19228 | 0.0093003 | North | N | 0.0093003 | 0
12323 | ENNSTRAC | 2 | 111 | 0.14683 | north | Y | 0.0093003 | 0.33979 | 0.02166 | 0.19228 | 0.0093003 | North | N | 0.0093003 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14436 | north | N | 0.0068393 | 0.33733 | 0.019199 | 0.18982 | 0.0068393 | North | N | 0.0068393 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14171 | north | Y | 0.0041853 | 0.33467 | 0.016545 | 0.18717 | 0.0041853 | North | N | 0.0041853 | 0
12440 | PARKD_1S | 1 | 0 | 0.14356 | north | N | 0.0060383 | 0.33653 | 0.018398 | 0.18902 | 0.0060383 | North | N | 0.0060383 | 0
12449 | PARKD_2S | 1 | 0 | 0.14356 | north | N | 0.0060383 | 0.33653 | 0.018398 | 0.18902 | 0.0060383 | North | N | 0.0060383 | 0
13116 | TGATEWAY | 1 | 148 | 0.13573 | north | N | -0.0017977 | 0.32869 | 0.010562 | 0.18118 | 0.0017977 | North | N | 0.0017977 | 0
13117 | TGATEWAY | 2 | 130 | 0.13573 | north | N | -0.0017977 | 0.32869 | 0.010562 | 0.18118 | 0.0017977 | North | N | 0.0017977 | 0
13118 | TGATEWAY | 3 | 145 | 0.13573 | north | N | -0.0017977 | 0.32869 | 0.010562 | 0.18118 | 0.0017977 | North | N | 0.0017977 | 0
13119 | TGATEWAY | 4 | 399 | 0.13573 | north | N | -0.0017977 | 0.32869 | 0.010562 | 0.18118 | 0.0017977 | North | N | 0.0017977 | 0
13131 | CALFREST | 1 | 150.7 | 0.12768 | north | Y | -0.0098427 | 0.32065 | 0.002517 | 0.17314 | 0.002517 | west | Y | 0.0098427 | 1.104
13132 | CALFREST | 2 | 151 | 0.12768 | north | Y | -0.0098427 | 0.32065 | 0.002517 | 0.17314 | 0.002517 | west | Y | 0.0098427 | 1.1062
13133 | CALFREST | 3 | 177.4 | 0.12768 | north | Y | -0.0098427 | 0.32065 | 0.002517 | 0.17314 | 0.002517 | west | Y | 0.0098427 | 1.2996
13134 | CALFREST | 4 | 151.5 | 0.12796 | north | Y | -0.0095627 | 0.32093 | 0.002797 | 0.17342 | 0.002797 | west | Y | 0.0095627 | 1.025
13135 | CALFREST | 5 | 152.3 | 0.12796 | north | Y | -0.0095627 | 0.32093 | 0.002797 | 0.17342 | 0.002797 | west | Y | 0.0095627 | 1.0304
13136 | CALFREST | 6 | 177.5 | 0.12796 | north | Y | -0.0095627 | 0.32093 | 0.002797 | 0.17342 | 0.002797 | west | Y | 0.0095627 | 1.2009
13432 | SANDOW_5 | 5 | 581 | -0.2813 | south | Y | -0.41883 | -0.088337 | -0.40647 | -0.23585 | 0.088337 | south | N | 0.088337 | 0
13691 | OAKGROVE | 1 | 855 | 0.086115 | north | Y | -0.051411 | 0.27908 | -0.039051 | 0.13157 | 0.039051 | west | Y | 0.051411 | 10.5676
13692 | OAKGROVE | 2 | 855 | 0.086115 | north | Y | -0.051411 | 0.27908 | -0.039051 | 0.13157 | 0.039051 | west | Y | 0.051411 | 10.5676
32798 | BRYN_TAM | 1 | 32 | 0.040111 | north | N | -0.097415 | 0.23307 | -0.085055 | 0.085565 | 0.085055 | west | Y | 0.097415 | 0
32883 | BRYN_DNS | 1 | 48 | 0.036551 | north | Y | -0.10097 | 0.22951 | -0.088615 | 0.082005 | 0.082005 | houston | Y | 0.10097 | 0.91054
32884 | BRYN_DNS | 1 | 46 | 0.036551 | north | Y | -0.10097 | 0.22951 | -0.088615 | 0.082005 | 0.082005 | houston | Y | 0.10097 | 0.8726
32886 | BRYN_ATK | MB | 12 | 0.040218 | north | Y | -0.097308 | 0.23318 | -0.084948 | 0.085672 | 0.084948 | west | Y | 0.097308 | 0
32887 | BRYN_ATK | MB | 51 | 0.040218 | north | Y | -0.097308 | 0.23318 | -0.084948 | 0.085672 | 0.084948 | west | Y | 0.097308 | 0
32888 | BRYN_ATK | 1 | 17 | 0.040218 | north | Y | -0.097308 | 0.23318 | -0.084948 | 0.085672 | 0.084948 | west | Y | 0.097308 | 0.21012
32890 | BRYN_ATK | MB | 22 | 0.040218 | north | Y | -0.097308 | 0.23318 | -0.084948 | 0.085672 | 0.084948 | west | Y | 0.097308 | 0
32891 | BRYN_ATK | MB | 25 | 0.040218 | north | Y | -0.097308 | 0.23318 | -0.084948 | 0.085672 | 0.084948 | west | Y | 0.097308 | 0
32892 | BRYN_DNS | 1 | 105 | 0.036551 | north | Y | -0.10097 | 0.22951 | -0.088615 | 0.082005 | 0.082005 | houston | Y | 0.10097 | 1.9918
36998 | RDCNYNG1 | 1 | 84 | 0.12808 | west | Y | -0.0094477 | 0.32104 | 0.002912 | 0.17353 | 0.002912 | west | N | 0.002912 | 0
38332 | WDWRDU2 | 1 | 80 | 0.11002 | west | Y | -0.027507 | 0.30298 | -0.015147 | 0.15547 | 0.015147 | west | N | 0.015147 | 0
38437 | TNSRBNMS | 1 | 150 | 0.1099 | west | Y | -0.027624 | 0.30286 | -0.015264 | 0.15536 | 0.015264 | west | N | 0.015264 | 0
38438 | TNSRBNMS | 1 | 150 | 0.1099 | west | Y | -0.027624 | 0.30286 | -0.015264 | 0.15536 | 0.015264 | west | N | 0.015264 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38600 | TNBP_CGN | 5 | 53 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38614 | TNBPAMCG | 4 | 96 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38615 | TNBPAMCG | 1 | 244 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38690 | TNBP_CGN | 3 | 40 | -0.047599 | houston | N | -0.18512 | 0.14536 | -0.17276 | -0.0021448 | 0.0021448 | houston | N | 0.0021448 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.047632 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021778 | 0.0021778 | houston | N | 0.0021778 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.047632 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021778 | 0.0021778 | houston | N | 0.0021778 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.047632 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021778 | 0.0021778 | houston | N | 0.0021778 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.047632 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021778 | 0.0021778 | houston | N | 0.0021778 | 0
39470 | TNDOWCGN | 1 | 32 | -0.04763 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021758 | 0.0021758 | houston | N | 0.0021758 | 0
39480 | TNDOWCGN | 1 | 30 | -0.04763 | houston | N | -0.18516 | 0.14533 | -0.1728 | -0.0021758 | 0.0021758 | houston | N | 0.0021758 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.06762 | houston | N | -0.20515 | 0.12534 | -0.19279 | -0.022166 | 0.022166 | houston | N | 0.022166 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.06762 | houston | N | -0.20515 | 0.12534 | -0.19279 | -0.022166 | 0.022166 | houston | N | 0.022166 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.06762 | houston | N | -0.20515 | 0.12534 | -0.19279 | -0.022166 | 0.022166 | houston | N | 0.022166 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.06762 | houston | N | -0.20515 | 0.12534 | -0.19279 | -0.022166 | 0.022166 | houston | N | 0.022166 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.086115 | north | Y | -0.051411 | 0.27908 | -0.039051 | 0.13157 | 0.039051 | west | Y | 0.051411 | 1.8824
39970 | TNTNPONE | 1 | 153 | 0.086115 | north | Y | -0.051411 | 0.27908 | -0.039051 | 0.13157 | 0.039051 | west | Y | 0.051411 | 1.891
48500 | APD_GT1_ | 1 | 136 | -0.035405 | houston | N | -0.17293 | 0.15756 | -0.16057 | 0.010049 | 0.010049 | houston | N | 0.010049 | 0
48510 | AK_GT1__ | 1 | 33 | -0.054269 | houston | N | -0.19179 | 0.13869 | -0.17943 | -0.0088148 | 0.0088148 | houston | N | 0.0088148 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.035333 | houston | Y | -0.17286 | 0.15763 | -0.1605 | 0.010121 | 0.010121 | houston | N | 0.010121 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.035333 | houston | Y | -0.17286 | 0.15763 | -0.1605 | 0.010121 | 0.010121 | houston | N | 0.010121 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.035333 | houston | Y | -0.17286 | 0.15763 | -0.1605 | 0.010121 | 0.010121 | houston | N | 0.010121 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.035333 | houston | Y | -0.17286 | 0.15763 | -0.1605 | 0.010121 | 0.010121 | houston | N | 0.010121 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.070835 | houston | N | -0.20836 | 0.12213 | -0.196 | -0.025381 | 0.025381 | houston | N | 0.025381 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.070835 | houston | N | -0.20836 | 0.12213 | -0.196 | -0.025381 | 0.025381 | houston | N | 0.025381 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.055501 | houston | N | -0.19303 | 0.13746 | -0.18067 | -0.010047 | 0.010047 | houston | N | 0.010047 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.055501 | houston | N | -0.19303 | 0.13746 | -0.18067 | -0.010047 | 0.010047 | houston | N | 0.010047 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.055501 | houston | N | -0.19303 | 0.13746 | -0.18067 | -0.010047 | 0.010047 | houston | N | 0.010047 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.039957 | houston | N | -0.17748 | 0.15301 | -0.16512 | 0.0054972 | 0.0054972 | houston | N | 0.0054972 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.039957 | houston | N | -0.17748 | 0.15301 | -0.16512 | 0.0054972 | 0.0054972 | houston | N | 0.0054972 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.039957 | houston | N | -0.17748 | 0.15301 | -0.16512 | 0.0054972 | 0.0054972 | houston | N | 0.0054972 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.039957 | houston | N | -0.17748 | 0.15301 | -0.16512 | 0.0054972 | 0.0054972 | houston | N | 0.0054972 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.036988 | houston | N | -0.17451 | 0.15597 | -0.16215 | 0.0084662 | 0.0084662 | houston | N | 0.0084662 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.036988 | houston | N | -0.17451 | 0.15597 | -0.16215 | 0.0084662 | 0.0084662 | houston | N | 0.0084662 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.040852 | houston | N | -0.17838 | 0.15211 | -0.16602 | 0.0046022 | 0.0046022 | houston | N | 0.0046022 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.040852 | houston | N | -0.17838 | 0.15211 | -0.16602 | 0.0046022 | 0.0046022 | houston | N | 0.0046022 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.040852 | houston | N | -0.17838 | 0.15211 | -0.16602 | 0.0046022 | 0.0046022 | houston | N | 0.0046022 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.040852 | houston | N | -0.17838 | 0.15211 | -0.16602 | 0.0046022 | 0.0046022 | houston | N | 0.0046022 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.040852 | houston | N | -0.17838 | 0.15211 | -0.16602 | 0.0046022 | 0.0046022 | houston | N | 0.0046022 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.031605 | houston | Y | -0.16913 | 0.16136 | -0.15677 | 0.013849 | 0.013849 | houston | N | 0.013849 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.033118 | houston | Y | -0.17064 | 0.15984 | -0.15828 | 0.012336 | 0.012336 | houston | N | 0.012336 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.031149 | houston | Y | -0.16867 | 0.16181 | -0.15631 | 0.014305 | 0.014305 | houston | N | 0.014305 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.031149 | houston | Y | -0.16867 | 0.16181 | -0.15631 | 0.014305 | 0.014305 | houston | N | 0.014305 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.031149 | houston | Y | -0.16867 | 0.16181 | -0.15631 | 0.014305 | 0.014305 | houston | N | 0.014305 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.022757 | houston | N | -0.16028 | 0.17021 | -0.14792 | 0.022697 | 0.022697 | houston | N | 0.022697 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.035104 | houston | N | -0.17263 | 0.15786 | -0.16027 | 0.01035 | 0.01035 | houston | N | 0.01035 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.035104 | houston | N | -0.17263 | 0.15786 | -0.16027 | 0.01035 | 0.01035 | houston | N | 0.01035 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.03008 | houston | N | -0.16761 | 0.16288 | -0.15525 | 0.015374 | 0.015374 | houston | N | 0.015374 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.03008 | houston | N | -0.16761 | 0.16288 | -0.15525 | 0.015374 | 0.015374 | houston | N | 0.015374 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.03008 | houston | N | -0.16761 | 0.16288 | -0.15525 | 0.015374 | 0.015374 | houston | N | 0.015374 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.03008 | houston | N | -0.16761 | 0.16288 | -0.15525 | 0.015374 | 0.015374 | houston | N | 0.015374 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.036888 | houston | N | -0.17441 | 0.15607 | -0.16205 | 0.0085662 | 0.0085662 | houston | N | 0.0085662 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.036888 | houston | N | -0.17441 | 0.15607 | -0.16205 | 0.0085662 | 0.0085662 | houston | N | 0.0085662 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.036888 | houston | N | -0.17441 | 0.15607 | -0.16205 | 0.0085662 | 0.0085662 | houston | N | 0.0085662 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.036888 | houston | N | -0.17441 | 0.15607 | -0.16205 | 0.0085662 | 0.0085662 | houston | N | 0.0085662 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.037836 | houston | N | -0.17536 | 0.15513 | -0.163 | 0.0076182 | 0.0076182 | houston | N | 0.0076182 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.037836 | houston | N | -0.17536 | 0.15513 | -0.163 | 0.0076182 | 0.0076182 | houston | N | 0.0076182 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.037836 | houston | N | -0.17536 | 0.15513 | -0.163 | 0.0076182 | 0.0076182 | houston | N | 0.0076182 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.037836 | houston | N | -0.17536 | 0.15513 | -0.163 | 0.0076182 | 0.0076182 | houston | N | 0.0076182 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.037836 | houston | N | -0.17536 | 0.15513 | -0.163 | 0.0076182 | 0.0076182 | houston | N | 0.0076182 | 0
48651 | EP_1_2 | 1 | 5 | -0.031685 | houston | N | -0.16921 | 0.16128 | -0.15685 | 0.013769 | 0.013769 | houston | N | 0.013769 | 0
48651 | EP_1_2 | 2 | 21 | -0.031685 | houston | N | -0.16921 | 0.16128 | -0.15685 | 0.013769 | 0.013769 | houston | N | 0.013769 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.036428 | north | N | -0.1011 | 0.22939 | -0.088738 | 0.081882 | 0.081882 | houston | Y | 0.1011 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.036428 | north | N | -0.1011 | 0.22939 | -0.088738 | 0.081882 | 0.081882 | houston | Y | 0.1011 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.036428 | north | N | -0.1011 | 0.22939 | -0.088738 | 0.081882 | 0.081882 | houston | Y | 0.1011 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.036428 | north | N | -0.1011 | 0.22939 | -0.088738 | 0.081882 | 0.081882 | houston | Y | 0.1011 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.02971 | houston | Y | -0.16724 | 0.16325 | -0.15488 | 0.015744 | 0.015744 | houston | N | 0.015744 | 0
48691 | GBY_7374 | A | 46 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48691 | GBY_7374 | B | 46 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48692 | GBY_8182 | C | 46 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48692 | GBY_8182 | D | 55 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48693 | GBY_8384 | E | 55 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48693 | GBY_8384 | F | 54 | -0.038629 | houston | Y | -0.17615 | 0.15433 | -0.16379 | 0.0068252 | 0.0068252 | houston | N | 0.0068252 | 0
48721 | LEG_1___ | 1 | 827 | 0.10243 | north | Y | -0.035092 | 0.2954 | -0.022732 | 0.14789 | 0.022732 | west | Y | 0.035092 | 10.2215
48722 | LEG_2___ | 2 | 819 | 0.10243 | north | Y | -0.035092 | 0.2954 | -0.022732 | 0.14789 | 0.022732 | west | Y | 0.035092 | 10.1226
48730 | MNS_GT | 1 | 46.1 | -0.056004 | houston | N | -0.19353 | 0.13696 | -0.18117 | -0.01055 | 0.01055 | houston | N | 0.01055 | 0
48731 | CBE_GT1 | 1 | 76 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48732 | CBE_GT2 | 1 | 76 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48733 | CBE_ST12 | 1 | 105 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48734 | CBE_GT3 | 1 | 74 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48735 | CBE_GT4 | 1 | 74 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48736 | CBE_ST34 | 1 | 102 | -0.096961 | houston | Y | -0.23449 | 0.096002 | -0.22213 | -0.051507 | 0.051507 | houston | N | 0.051507 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.03686 | houston | N | -0.17439 | 0.1561 | -0.16203 | 0.0085942 | 0.0085942 | houston | N | 0.0085942 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.03686 | houston | N | -0.17439 | 0.1561 | -0.16203 | 0.0085942 | 0.0085942 | houston | N | 0.0085942 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.03686 | houston | N | -0.17439 | 0.1561 | -0.16203 | 0.0085942 | 0.0085942 | houston | N | 0.0085942 | 0
48761 | PR_GT1__ | 1 | 35 | -0.037465 | houston | N | -0.17499 | 0.1555 | -0.16263 | 0.0079892 | 0.0079892 | houston | N | 0.0079892 | 0
48772 | PHR_GN2_ | MB | 459 | -0.043134 | houston | Y | -0.18066 | 0.14983 | -0.1683 | 0.0023202 | 0.0023202 | houston | N | 0.0023202 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.031676 | houston | N | -0.1692 | 0.16129 | -0.15684 | 0.013778 | 0.013778 | houston | N | 0.013778 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.022757 | houston | N | -0.16028 | 0.17021 | -0.14792 | 0.022697 | 0.022697 | houston | N | 0.022697 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.022757 | houston | N | -0.16028 | 0.17021 | -0.14792 | 0.022697 | 0.022697 | houston | N | 0.022697 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.022757 | houston | N | -0.16028 | 0.17021 | -0.14792 | 0.022697 | 0.022697 | houston | N | 0.022697 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.022757 | houston | N | -0.16028 | 0.17021 | -0.14792 | 0.022697 | 0.022697 | houston | N | 0.022697 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.03133 | houston | N | -0.16886 | 0.16163 | -0.1565 | 0.014124 | 0.014124 | houston | N | 0.014124 | 0
48820 | SHELLG1_ | 1 | 71 | -0.036297 | houston | N | -0.17382 | 0.15667 | -0.16146 | 0.0091572 | 0.0091572 | houston | N | 0.0091572 | 0
48821 | SHELLG2 | 2 | 72 | -0.036297 | houston | N | -0.17382 | 0.15667 | -0.16146 | 0.0091572 | 0.0091572 | houston | N | 0.0091572 | 0
48822 | SHELLG3_ | 1 | 39 | -0.036297 | houston | N | -0.17382 | 0.15667 | -0.16146 | 0.0091572 | 0.0091572 | houston | N | 0.0091572 | 0
48822 | SHELLG3_ | 2 | 30 | -0.036297 | houston | N | -0.17382 | 0.15667 | -0.16146 | 0.0091572 | 0.0091572 | houston | N | 0.0091572 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.038295 | houston | N | -0.17582 | 0.15467 | -0.16346 | 0.0071592 | 0.0071592 | houston | N | 0.0071592 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.038295 | houston | N | -0.17582 | 0.15467 | -0.16346 | 0.0071592 | 0.0071592 | houston | N | 0.0071592 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.036896 | houston | N | -0.17442 | 0.15607 | -0.16206 | 0.0085582 | 0.0085582 | houston | N | 0.0085582 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.037012 | houston | Y | -0.17454 | 0.15595 | -0.16218 | 0.0084422 | 0.0084422 | houston | N | 0.0084422 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.037043 | houston | Y | -0.17457 | 0.15592 | -0.16221 | 0.0084112 | 0.0084112 | houston | N | 0.0084112 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.036905 | houston | Y | -0.17443 | 0.15606 | -0.16207 | 0.0085492 | 0.0085492 | houston | N | 0.0085492 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.036874 | houston | Y | -0.1744 | 0.15609 | -0.16204 | 0.0085802 | 0.0085802 | houston | N | 0.0085802 | 0
48855 | SRB_GT21 | B2 | 12 | -0.037066 | houston | Y | -0.17459 | 0.1559 | -0.16223 | 0.0083882 | 0.0083882 | houston | N | 0.0083882 | 0
48855 | SRB_GT21 | MB | 18 | -0.037066 | houston | Y | -0.17459 | 0.1559 | -0.16223 | 0.0083882 | 0.0083882 | houston | N | 0.0083882 | 0
48865 | TECO_GT1 | 1 | 50 | -0.045093 | houston | Y | -0.18262 | 0.14787 | -0.17026 | 0.0003612 | 0.0003612 | houston | N | 0.0003612 | 0
48873 | THW_ST3_ | 3 | 104 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48874 | THW_ST4_ | 4 | 104 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48875 | THW_3132 | A | 54 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48875 | THW_3132 | B | 53 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48877 | THW_3334 | C | 54 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48877 | THW_3334 | D | 57 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48879 | THW_4142 | E | 54 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48879 | THW_4142 | F | 54 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48881 | THW_4344 | G | 58 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48881 | THW_4344 | H | 58 | -0.033672 | houston | Y | -0.1712 | 0.15929 | -0.15884 | 0.011782 | 0.011782 | houston | N | 0.011782 | 0
48883 | THW_GT1_ | B2 | 12 | -0.032283 | houston | Y | -0.16981 | 0.16068 | -0.15745 | 0.013171 | 0.013171 | houston | N | 0.013171 | 0
48885 | THW_5152 | A | 56 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48885 | THW_5152 | B | 59 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48886 | THW_5354 | C | 56 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48886 | THW_5354 | D | 56 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48887 | THW_5556 | E | 59 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48887 | THW_5556 | F | 56 | -0.02906 | houston | Y | -0.16659 | 0.1639 | -0.15423 | 0.016394 | 0.016394 | houston | N | 0.016394 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.091624 | houston | Y | -0.22915 | 0.10134 | -0.21679 | -0.04617 | 0.04617 | houston | N | 0.04617 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.053753 | houston | Y | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.053753 | houston | Y | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.053753 | houston | Y | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.053753 | houston | Y | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.053753 | houston | N | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.055599 | houston | Y | -0.19312 | 0.13736 | -0.18076 | -0.010145 | 0.010145 | houston | N | 0.010145 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.055599 | houston | Y | -0.19312 | 0.13736 | -0.18076 | -0.010145 | 0.010145 | houston | N | 0.010145 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.055599 | houston | Y | -0.19312 | 0.13736 | -0.18076 | -0.010145 | 0.010145 | houston | N | 0.010145 | 0
48929 | WAPGT21_ | B1 | 13 | -0.053753 | houston | Y | -0.19128 | 0.13921 | -0.17892 | -0.0082988 | 0.0082988 | houston | N | 0.0082988 | 0
48940 | WARVUE_G | G1 | 12 | -0.031647 | houston | Y | -0.16917 | 0.16132 | -0.15681 | 0.013807 | 0.013807 | houston | N | 0.013807 | 0
49803 | EXN_15GT | 1 | 34 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49826 | EXN938GT | 5 | 45.9 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49828 | EXN941GT | 10 | 17.7 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49829 | EXN942GT | 11 | 20.4 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49830 | EXN943GT | 12 | 19.9 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49831 | EXN944GT | 13 | 35 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49832 | EXN945GT | 9 | 18 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49837 | EXN_GT | 4 | 85.4 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49838 | EXN_14GT | 14 | 148 | -0.03275 | houston | N | -0.17028 | 0.16021 | -0.15792 | 0.012704 | 0.012704 | houston | N | 0.012704 | 0
49851 | DOW17000 | 37 | 62 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49858 | DOW38100 | 31 | 71.4 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49859 | DOW38200 | 33 | 45 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49860 | DOW38300 | 32 | 101 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49862 | DOW39100 | 36 | 86 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49863 | DOW39200 | 35 | 88 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49865 | DOW41000 | 41 | 50 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49866 | DOW42000 | 42 | 18 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49869 | DOW49000 | 45 | 94 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49870 | DOW61000 | 61 | 70 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49871 | DOW62000 | 62 | 63 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49872 | DOW63000 | 63 | 72 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49873 | DOW64000 | 64 | 64.8 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49876 | DOW65000 | 65 | 101 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49877 | DOW66000 | 66 | 97 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49878 | DOW67000 | 67 | 103 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49882 | DOW81000 | 81 | 76 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49884 | DOW82000 | 82 | 80 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49885 | DOW83000 | 83 | 80 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
49886 | DOW84000 | 84 | 171 | -0.074903 | houston | N | -0.21243 | 0.11806 | -0.20007 | -0.029449 | 0.029449 | houston | N | 0.029449 | 0
58909 | PEARSALL | 1 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58909 | PEARSALL | 2 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58909 | PEARSALL | 3 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58909 | PEARSALL | 4 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58909 | PEARSALL | 5 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58909 | PEARSALL | 6 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 1 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 2 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 3 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 4 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 5 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58919 | PEARSALL | 6 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 1 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 2 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 3 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 4 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 5 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58929 | PEARSALL | 6 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 1 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 2 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 3 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 4 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 5 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
58949 | PEARSALL | 6 | 8.4 | -0.16198 | south | Y | -0.2995 | 0.030988 | -0.28714 | -0.11652 | 0.030988 | south | N | 0.030988 | 0
60000 | DSKY2 | 1 | 76.5 | 0.10448 | west | Y | -0.033041 | 0.29745 | -0.020681 | 0.14994 | 0.020681 | west | N | 0.020681 | 0
60003 | KING_NE1 | 1 | 80 | 0.11025 | west | Y | -0.027279 | 0.30321 | -0.014919 | 0.1557 | 0.014919 | west | N | 0.014919 | 0
60005 | KING_SE1 | 1 | 40 | 0.11025 | west | Y | -0.027279 | 0.30321 | -0.014919 | 0.1557 | 0.014919 | west | N | 0.014919 | 0
60007 | KING_SW1 | 1 | 80 | 0.11117 | west | Y | -0.026355 | 0.30413 | -0.013995 | 0.15663 | 0.013995 | west | N | 0.013995 | 0
60016 | WOODWRD1 | 1 | 80 | 0.11005 | west | Y | -0.02748 | 0.30301 | -0.01512 | 0.1555 | 0.01512 | west | N | 0.01512 | 0
60017 | ORNNWP1 | 1 | 80 | 0.10528 | west | Y | -0.032244 | 0.29824 | -0.019884 | 0.15074 | 0.019884 | west | N | 0.019884 | 0
60018 | DSKY1 | 1 | 84 | 0.10372 | west | Y | -0.033803 | 0.29669 | -0.021443 | 0.14918 | 0.021443 | west | N | 0.021443 | 0
60019 | KING_NW1 | 1 | 80 | 0.11117 | west | Y | -0.026355 | 0.30413 | -0.013995 | 0.15663 | 0.013995 | west | N | 0.013995 | 0
60057 | CALLAHAN | 1 | 114 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12643 | west | Y | -0.011094 | 0.31939 | 0.001266 | 0.17189 | 0.001266 | west | N | 0.001266 | 0
60060 | CIRELLO | 1 | 233 | 0.12643 | west | Y | -0.011094 | 0.31939 | 0.001266 | 0.17189 | 0.001266 | west | N | 0.001266 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12643 | west | Y | -0.011094 | 0.31939 | 0.001266 | 0.17189 | 0.001266 | west | N | 0.001266 | 0
60066 | H_HOLLOW | 1 | 222 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60074 | HORSH5 | 1 | 100 | -0.19257 | south | Y | -0.3301 | 0.00039276 | -0.31774 | -0.14712 | 0.00039276 | south | N | 0.00039276 | 0
60081 | WHRLWIND | 1 | 60 | 0.13136 | west | Y | -0.0061647 | 0.32432 | 0.006195 | 0.17682 | 0.0061647 | North | Y | 0.006195 | 0.0018187
60201 | RIO DRCS | F | 0 | -0.095774 | south | N | -0.2333 | 0.097189 | -0.22094 | -0.05032 | 0.05032 | houston | Y | 0.097189 | 0
60202 | FRIEND_R | F | 0 | 0.078876 | west | N | -0.05865 | 0.27184 | -0.04629 | 0.12433 | 0.04629 | west | N | 0.04629 | 0
60203 | PRES0A | BT | 4.8 | 0.11461 | west | N | -0.022915 | 0.30757 | -0.010555 | 0.16007 | 0.010555 | west | N | 0.010555 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
71057 | L_SWEETW | W1 | 135 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
71059 | L_SWEETW | W1 | 119 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
71060 | L_SWEETW | W1 | 105 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12909 | west | Y | -0.0084407 | 0.32205 | 0.003919 | 0.17454 | 0.003919 | west | N | 0.003919 | 0
76031 | L_GASCCR | W1 | 150 | 0.12499 | west | Y | -0.012535 | 0.31795 | -0.00017499 | 0.17045 | 0.00017499 | west | N | 0.00017499 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12446 | west | Y | -0.013066 | 0.31742 | -0.00070599 | 0.16991 | 0.00070599 | west | N | 0.00070599 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12446 | west | Y | -0.013066 | 0.31742 | -0.00070599 | 0.16991 | 0.00070599 | west | N | 0.00070599 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12446 | west | Y | -0.013066 | 0.31742 | -0.00070599 | 0.16991 | 0.00070599 | west | N | 0.00070599 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12446 | west | Y | -0.013066 | 0.31742 | -0.00070599 | 0.16991 | 0.00070599 | west | N | 0.00070599 | 0
80003 | MILHWYS | F | 0 | -0.15486 | south | N | -0.29238 | 0.038106 | -0.28002 | -0.1094 | 0.038106 | south | N | 0.038106 | 0
80010 | EPLVT1 | F | 0 | -0.11768 | south | N | -0.25521 | 0.075278 | -0.24285 | -0.072231 | 0.072231 | houston | Y | 0.075278 | 0
80012 | LAR | F | 0 | -0.16289 | south | N | -0.30042 | 0.030073 | -0.28806 | -0.11744 | 0.030073 | south | N | 0.030073 | 0
80051 | FORPVCM0 | 8 | 28 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
80053 | FOR69CG0 | 10 | 74 | -0.14129 | south | N | -0.27881 | 0.051675 | -0.26645 | -0.095834 | 0.051675 | south | N | 0.051675 | 0
80080 | GWINDT11 | 1 | 94 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80080 | GWINDT11 | 2 | 41 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80080 | GWINDT11 | 3 | 38 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80080 | GWINDT11 | 4 | 19 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80081 | GWINDT21 | 1 | 94 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80081 | GWINDT21 | 2 | 36 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80081 | GWINDT21 | 3 | 43 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80081 | GWINDT21 | 4 | 22 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80137 | CSDR89 | 8 | 39 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80137 | CSDR89 | 9 | 15 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80138 | CSDR7 | 7 | 7 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80139 | CSDR56 | 5 | 15 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80139 | CSDR56 | 6 | 39 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80140 | CSDR11 | 11 | 39 | -0.14642 | south | N | -0.28395 | 0.046542 | -0.27159 | -0.10097 | 0.046542 | south | N | 0.046542 | 0
80180 | PNSCALT1 | 1 | 148 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80180 | PNSCALT1 | 2 | 50 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80181 | PNSCALT2 | 1 | 55 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80181 | PNSCALT2 | 2 | 50 | -0.15476 | south | Y | -0.29228 | 0.038206 | -0.27992 | -0.1093 | 0.038206 | south | N | 0.038206 | 0
80223 | REYSHR G | 1 | 12 | -0.1517 | south | N | -0.28923 | 0.041261 | -0.27687 | -0.10625 | 0.041261 | south | N | 0.041261 | 0
80224 | VISTRONG | 1 | 15 | -0.14807 | south | N | -0.28559 | 0.044898 | -0.27323 | -0.10261 | 0.044898 | south | N | 0.044898 | 0
80225 | VISTRONG | 2 | 23 | -0.14807 | south | N | -0.28559 | 0.044898 | -0.27323 | -0.10261 | 0.044898 | south | N | 0.044898 | 0
80226 | ALCOA G | 1 | 48 | -0.1425 | south | N | -0.28002 | 0.050466 | -0.26766 | -0.097043 | 0.050466 | south | N | 0.050466 | 0
80227 | AIRCO G | 1 | 8 | -0.147 | south | N | -0.28453 | 0.045959 | -0.27217 | -0.10155 | 0.045959 | south | N | 0.045959 | 0
80261 | NBEC81A | 1 | 180 | -0.15329 | south | Y | -0.29082 | 0.039668 | -0.27846 | -0.10784 | 0.039668 | south | N | 0.039668 | 0
80262 | NBEC91A | 1 | 180 | -0.15325 | south | Y | -0.29077 | 0.039715 | -0.27841 | -0.10779 | 0.039715 | south | N | 0.039715 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.15359 | south | Y | -0.29112 | 0.039372 | -0.27876 | -0.10814 | 0.039372 | south | N | 0.039372 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.15359 | south | Y | -0.29112 | 0.039372 | -0.27876 | -0.10814 | 0.039372 | south | N | 0.039372 | 0
80265 | LARECU40 | 4 | 100 | -0.1629 | south | Y | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
80266 | LARECU50 | 5 | 100 | -0.1629 | south | Y | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
80291 | PAPALOTE | 1 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80291 | PAPALOTE | 2 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80291 | PAPALOTE | 3 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80291 | PAPALOTE | 4 | 16 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80294 | PAPALOTE | 5 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80294 | PAPALOTE | 6 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80294 | PAPALOTE | 7 | 25 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
80294 | PAPALOTE | 8 | 15 | -0.15231 | south | Y | -0.28984 | 0.040651 | -0.27748 | -0.10686 | 0.040651 | south | N | 0.040651 | 0
86104 | CID-138 | EQ | 0 | -0.1629 | south | N | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
86105 | CID-230 | EQ | 500 | -0.1629 | south | N | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
86106 | CUF-230 | EQ | 500 | -0.1629 | south | N | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
86107 | CUF-138 | EQ | 0 | -0.1629 | south | N | -0.30043 | 0.030059 | -0.28807 | -0.11745 | 0.030059 | south | N | 0.030059 | 0
88198 | BEEVILLE | F | 0 | -0.16173 | south | N | -0.29925 | 0.031236 | -0.28689 | -0.11627 | 0.031236 | south | N | 0.031236 | 0
88253 | HAMILTON | F | 0 | -0.088959 | south | N | -0.22648 | 0.104 | -0.21412 | -0.043505 | 0.043505 | houston | Y | 0.104 | 0
88299 | ZAPATA | F | 0 | -0.15894 | south | N | -0.29646 | 0.034025 | -0.2841 | -0.11348 | 0.034025 | south | N | 0.034025 | 0
88508 | FALFURRI | F | 0 | -0.15731 | south | N | -0.29483 | 0.035657 | -0.28247 | -0.11185 | 0.035657 | south | N | 0.035657 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.23958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42896 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.23958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 188.5495 | 787 | 0.42896 | 337.5934 | 787 | 337.5934
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.20866 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 53.2083 | 255 | 0.39804 | 101.5008 | 1042 | 439.0943
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 31.0903 | 149 | 0.39804 | 59.3083 | 1191 | 498.4026 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 31.925 | 153 | 0.39804 | 60.9005 | 1344 | 559.3031 | North | 0.13753
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.38835 | 0 | 1344 | 559.3031 | South | -0.18938
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.38835 | 0 | 1344 | 559.3031 |  | 0.32691
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0908 | 150 | 0.37665 | 56.4982 | 1494 | 615.8013
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.9818 | 80 | 0.37665 | 30.1324 | 1574 | 645.9336 | Line Rating | 1072
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.697 | 0 | 0.36918 | 0 | 1574 | 645.9336 | Conc Gen | 2024
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.697 | 0 | 0.36918 | 0 | 1574 | 645.9336 | Weighted Imp. | 801.632
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.0815 | 224 | 0.346 | 77.5032 | 1798 | 723.4368 | PTDF | 0.39606
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.3948 | 226 | 0.346 | 78.1952 | 2024 | 801.632
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.2022 | 212 | 0.346 | 73.3512 |  |  | Concentration | 1.2115
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.0456 | 211 | 0.346 | 73.0053
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.864 | 216.4 | 0.34587 | 74.8464
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.8171 | 216.1 | 0.34587 | 74.7426
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.8712 | 168 | 0.34338 | 57.6874
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8596 | 90 | 0.34338 | 30.904
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.14987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 59.1987 | 395 | 0.33925 | 134.0047
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.14987 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.1934 | 435 | 0.33925 | 147.5748
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.4706 | 70 | 0.33896 | 23.7274
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.321 | 69 | 0.33896 | 23.3884
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.321 | 69 | 0.33896 | 23.3884
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1714 | 68 | 0.33896 | 23.0494
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.14957 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.0612 | 435 | 0.33895 | 147.4426
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1486 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33798 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.185 | 217.3 | 0.3375 | 73.3378
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.3632 | 205 | 0.3375 | 69.1866
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 40.346 | 272.4 | 0.3375 | 91.9338
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.7639 | 0 | 0.33697 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.9115 | 0 | 0.33697 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.147 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.7779 | 196 | 0.33621 | 65.8969
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2977 | 111 | 0.33621 | 37.3191
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6295 | 18 | 0.33547 | 6.0384
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6295 | 18 | 0.33547 | 6.0384
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.5512 | 38 | 0.33547 | 12.7478
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14582 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.6449 | 73 | 0.3352 | 24.4699
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3527 | 119 | 0.3352 | 39.8892
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8933 | 205 | 0.3352 | 68.7167
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.8737 | 102 | 0.3352 | 34.1908
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9988 | 96 | 0.3352 | 32.1795
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.1992 | 118 | 0.33514 | 39.5463
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14576 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.7619 | 115 | 0.33514 | 38.5409
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 81.0403 | 556 | 0.33514 | 186.337
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.8977 | 288 | 0.33486 | 96.4398
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3853 | 147 | 0.33486 | 49.2245
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3853 | 147 | 0.33486 | 49.2245
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7026 | 60 | 0.33443 | 20.0656
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.1378 | 63 | 0.33443 | 21.0689
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14461 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.2691 | 112.5 | 0.334 | 37.5746
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14436 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33375 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14433 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33371 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7437 | 0 | 0.33298 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7437 | 0 | 0.33298 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33295 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33295 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2799 | 204 | 0.33291 | 67.9139
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8493 | 201 | 0.33291 | 66.9152
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.734 | 242 | 0.33291 | 80.5646
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.3867 | 170 | 0.33283 | 56.5817
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14345 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.5945 | 520 | 0.33283 | 173.0734
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.1433 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.021 | 370 | 0.33268 | 123.0925
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.062 | 0 | 0.33268 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2053 | 0 | 0.33268 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.2797 | 0 | 0.33268 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.4919 | 0 | 0.33268 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6352 | 0 | 0.33268 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.423 | 0 | 0.33268 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9101 | 160 | 0.33257 | 53.2113
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3373 | 156 | 0.33257 | 51.881
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0648 | 196 | 0.33257 | 65.1838
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3373 | 156 | 0.33257 | 51.881
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4805 | 157 | 0.33257 | 52.2136
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3512 | 198 | 0.33257 | 65.8489
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.7309 | 0 | 0.33246 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.389 | 0 | 0.33246 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.6481 | 0 | 0.33246 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14307 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7227 | 40 | 0.33245 | 13.298
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.3001 | 79 | 0.33242 | 26.2613
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.1621 | 106 | 0.33242 | 35.2367
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.8837 | 146 | 0.33242 | 48.5335
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14304 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.871 | 76 | 0.33242 | 25.264
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.8013 | 558 | 0.3324 | 185.4767
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.8045 | 579 | 0.3324 | 192.457
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 115.5545 | 808 | 0.3324 | 268.5755
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.143 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 55.4824 | 388 | 0.33238 | 128.9628
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.143 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.6429 | 515 | 0.33238 | 171.1749
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7154 | 0 | 0.33233 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7154 | 0 | 0.33233 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14284 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 17.1414 | 120 | 0.33223 | 39.8673
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8567 | 20 | 0.33222 | 6.6443
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5709 | 25 | 0.33222 | 8.3054
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8562 | 41 | 0.33222 | 13.6209
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8155 | 161 | 0.33109 | 53.306
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2406 | 164 | 0.33109 | 54.2993
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2406 | 164 | 0.33109 | 54.2993
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.6684 | 414 | 0.33109 | 137.0727
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9572 | 162 | 0.33109 | 53.6371
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8155 | 161 | 0.33109 | 53.306
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0989 | 163 | 0.33109 | 53.9682
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.9598 | 409 | 0.33109 | 135.4172
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.14151 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.4905 | 60 | 0.33089 | 19.8534
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.1408 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.5392 | 224 | 0.33018 | 73.9609
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.383 | 17 | 0.32956 | 5.6025
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.14001 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 51.2426 | 366 | 0.32939 | 120.5565
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13972 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.813 | 242 | 0.32911 | 79.6435
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 107.0881 | 785 | 0.3258 | 255.7534
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.4523 | 795 | 0.3258 | 259.0114
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 106.406 | 780 | 0.3258 | 254.1243
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13639 | west | 4 | Y | N | Ywest | Nwest | 1 | 88.6158 | 649.7 | 0.32578 | 211.6576
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.0877 | 0 | 0.32511 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.6446 | 0 | 0.32511 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.6806 | 0 | 0.32511 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 54.1555 | 0 | 0.32511 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13523 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3128 | 165 | 0.32461 | 53.5609
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13489 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32427 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13483 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7413 | 50 | 0.32421 | 16.2105
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.4282 | 182 | 0.3236 | 58.8958
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 64.963 | 484 | 0.3236 | 156.6241
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13372 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.5579 | 236 | 0.3231 | 76.2522
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13371 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.4844 | 400 | 0.32309 | 129.2374
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13136 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8817 | 60 | 0.32074 | 19.2446
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12954 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4318 | 150 | 0.31893 | 47.8391
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0268 | 209 | 0.3187 | 66.6078
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3583 | 126.5 | 0.3187 | 40.3152
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1994 | 249 | 0.3187 | 79.3557
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.4751 | 197 | 0.3187 | 62.7834
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8407 | 37.5 | 0.31847 | 11.9425
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8766 | 107.5 | 0.31847 | 34.2353
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.4265 | 135 | 0.31847 | 42.9931
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3611 | 119 | 0.31847 | 37.8976
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.5539 | 105 | 0.31847 | 33.4391
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3913 | 80.5 | 0.31847 | 25.6366
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0525 | 125 | 0.3178 | 39.7253
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0525 | 125 | 0.3178 | 39.7253
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.245 | 150 | 0.31768 | 47.6524
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.9583 | 101 | 0.31768 | 32.0859
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12808 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7586 | 84 | 0.31746 | 26.6667
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.3864 | 151.5 | 0.31735 | 48.0778
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4888 | 152.3 | 0.31735 | 48.3317
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7134 | 177.5 | 0.31735 | 56.3288
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6467 | 99 | 0.31713 | 31.3955
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7924 | 61 | 0.31713 | 19.3447
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 3.1936 | 0 | 0.31713 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8379 | 0 | 0.31713 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8379 | 0 | 0.31713 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0067 | 141 | 0.31709 | 44.7096
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3248 | 120 | 0.31709 | 38.0507
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2418 | 150.7 | 0.31707 | 47.7818
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2801 | 151 | 0.31707 | 47.8769
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.651 | 177.4 | 0.31707 | 56.2474
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.1276 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0389 | 63 | 0.31698 | 19.97
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4136 | 66 | 0.31686 | 20.9129
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 69 | 0.31686 | 21.8634
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 69 | 0.31686 | 21.8634
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 67 | 0.31686 | 21.2297
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 67 | 0.31686 | 21.2297
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2861 | 65 | 0.31686 | 20.596
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0774 | 150 | 0.31657 | 47.4848
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9803 | 220 | 0.31657 | 69.6444
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.4366 | 200 | 0.31657 | 63.3131
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5036 | 121.9 | 0.31657 | 38.5893
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.8312 | 180 | 0.31622 | 56.92
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.8312 | 180 | 0.31622 | 56.92
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8771 | 0 | 0.3162 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 9.3083 | 0 | 0.3162 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 8.9278 | 0 | 0.3162 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12672 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.512 | 225 | 0.3161 | 71.1231
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1754 | 120 | 0.31584 | 37.9013
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1718 | 120 | 0.31581 | 37.8977
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.4587 | 233 | 0.31581 | 73.5848
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.5187 | 170.2 | 0.31581 | 53.7516
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12641 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1688 | 120 | 0.31579 | 37.8947
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4445 | 615 | 0.31531 | 193.9147
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.9186 | 587 | 0.31531 | 185.0861
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12563 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2412 | 0 | 0.31501 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12558 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8986 | 214.2 | 0.31496 | 67.4643
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5918 | 100.5 | 0.31467 | 31.6248
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12527 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2655 | 58 | 0.31465 | 18.2497
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7639 | 70 | 0.31458 | 22.0207
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7639 | 70 | 0.31458 | 22.0207
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.6185 | 92.8 | 0.31458 | 29.1932
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0159 | 80 | 0.31458 | 25.1665
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0159 | 80 | 0.31458 | 25.1665
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3979 | 115 | 0.31458 | 36.1769
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.0619 | 208.2 | 0.31456 | 65.4913
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.7877 | 142.1 | 0.31456 | 44.6989
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.5734 | 132.4 | 0.31456 | 41.6477
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.0241 | 136 | 0.31456 | 42.7801
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.401 | 147 | 0.31456 | 46.2402
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.2872 | 210 | 0.31456 | 66.0575
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12499 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7487 | 150 | 0.31437 | 47.156
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0017 | 112.5 | 0.31384 | 35.3073
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6068 | 149.5 | 0.31384 | 46.9194
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1496 | 186 | 0.31384 | 58.3747
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.6967 | 214.5 | 0.31384 | 67.3192
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.81723 | 6.6 | 0.3132 | 2.0671
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2471 | 34.3 | 0.3132 | 10.7429
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12342 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3896 | 149 | 0.3128 | 46.6076
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3061 | 35 | 0.31241 | 10.9345
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6909 | 30 | 0.31241 | 9.3724
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1125 | 66 | 0.3123 | 20.6118
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9896 | 65 | 0.3123 | 20.2995
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12292 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12292 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3123 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12259 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.7783 | 169.5 | 0.31197 | 52.8787
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11461 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55013 | 0 | 0.30399 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8937 | 80 | 0.30055 | 24.0443
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8937 | 80 | 0.30055 | 24.0443
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2685 | 75 | 0.29963 | 22.4722
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8198 | 80 | 0.29963 | 23.9704
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4099 | 40 | 0.29963 | 11.9852
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11005 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8037 | 80 | 0.29943 | 23.9543
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11002 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8015 | 80 | 0.2994 | 23.9521
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.4853 | 150 | 0.29928 | 44.8927
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.4853 | 150 | 0.29928 | 44.8927
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4226 | 80 | 0.29466 | 23.5732
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10448 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9931 | 76.5 | 0.29387 | 22.4809
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10372 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7127 | 84 | 0.29311 | 24.6209
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.7129 | 827 | 0.29182 | 241.3322
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.8934 | 819 | 0.29182 | 238.9977
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.6283 | 855 | 0.2755 | 235.5503
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.6283 | 855 | 0.2755 | 235.5503
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1153 | 152.3 | 0.2755 | 41.9583
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1756 | 153 | 0.2755 | 42.1511
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078876 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26826 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.056431 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4647 | 150 | 0.24581 | 36.872
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.047651 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.0624 | 463 | 0.23703 | 109.7465
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.040218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.68371 | 17 | 0.2296 | 3.9032
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.040111 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.2836 | 0 | 0.22949 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7544 | 48 | 0.22593 | 10.8448
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6813 | 46 | 0.22593 | 10.3929
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.036551 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.8379 | 105 | 0.22593 | 23.723
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6172 | 0 | 0.22581 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6828 | 0 | 0.22581 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6828 | 0 | 0.22581 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.8426 | 0 | 0.22581 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18938 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.18938 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.095774 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.093608 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -19.257 | 100 | -0.0031876 | -0.31876
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13753 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13753 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.937 | 0 | -0.16028 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5501 | 0 | -0.16028 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5046 | 0 | -0.16028 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5046 | 0 | -0.16028 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.022757 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6866 | 0 | -0.16028 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7145 | 59 | -0.16659 | -9.8286
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7145 | 59 | -0.16659 | -9.8286
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.8246 | 398 | -0.16724 | -66.5598
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.897 | 0 | -0.16761 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8549 | 0 | -0.16761 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7797 | 0 | -0.16761 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0975 | 0 | -0.16761 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.03133 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9188 | 0 | -0.16886 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.031605 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -23.4825 | 743 | -0.16913 | -125.6641
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.031647 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.37976 | 12 | -0.16917 | -2.0301
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0589 | 0 | -0.1692 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0906 | 0 | -0.1692 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2173 | 0 | -0.1692 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9956 | 0 | -0.1692 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9639 | 0 | -0.1692 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2943 | 0 | -0.1692 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8689 | 0 | -0.1692 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15843 | 0 | -0.16921 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66539 | 0 | -0.16921 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.032283 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3874 | 12 | -0.16981 | -2.0377
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1135 | 0 | -0.17028 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1364 | 0 | -0.17028 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0709 | 0 | -0.17028 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5032 | 0 | -0.17028 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57968 | 0 | -0.17028 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6681 | 0 | -0.17028 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65172 | 0 | -0.17028 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1462 | 0 | -0.17028 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5895 | 0 | -0.17028 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7969 | 0 | -0.17028 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.847 | 0 | -0.17028 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.033118 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -24.3417 | 735 | -0.17064 | -125.4231
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5019 | 104 | -0.1712 | -17.8046
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5019 | 104 | -0.1712 | -17.8046
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.7846 | 53 | -0.1712 | -9.0735
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9193 | 57 | -0.1712 | -9.7583
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.953 | 58 | -0.1712 | -9.9295
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.953 | 58 | -0.1712 | -9.9295
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.035104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.073 | 0 | -0.17263 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.035104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.739 | 0 | -0.17263 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.484 | 42 | -0.17286 | -7.2601
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.484 | 42 | -0.17286 | -7.2601
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3427 | 38 | -0.17286 | -6.5686
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3427 | 38 | -0.17286 | -6.5686
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.035405 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8151 | 0 | -0.17293 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5771 | 0 | -0.17382 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6134 | 0 | -0.17382 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4156 | 0 | -0.17382 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0889 | 0 | -0.17382 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6348 | 0 | -0.17439 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.846 | 0 | -0.17439 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.787 | 0 | -0.17439 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.036874 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.4073 | 228 | -0.1744 | -39.7631
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3608 | 0 | -0.17441 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3313 | 0 | -0.17441 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0469 | 0 | -0.17441 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.715 | 0 | -0.17441 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.036896 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59772 | 0 | -0.17442 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.036905 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.8608 | 213 | -0.17443 | -37.1537
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5112 | 0 | -0.17451 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4079 | 0 | -0.17451 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.037012 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.107 | 165 | -0.17454 | -28.7987
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.037043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.2603 | 169 | -0.17457 | -29.5021
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.037066 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44479 | 12 | -0.17459 | -2.0951
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.037066 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17459 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.037465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3113 | 0 | -0.17499 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1748 | 0 | -0.17536 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.944 | 0 | -0.17536 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.9592 | 0 | -0.17536 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.9403 | 0 | -0.17536 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1779 | 0 | -0.17536 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.987 | 0 | -0.17582 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0636 | 0 | -0.17582 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1246 | 55 | -0.17615 | -9.6885
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1246 | 55 | -0.17615 | -9.6885
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.086 | 54 | -0.17615 | -9.5124
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3974 | 0 | -0.17748 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7175 | 0 | -0.17838 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5786 | 0 | -0.17838 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5541 | 0 | -0.17838 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2264 | 0 | -0.17838 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49839 | 0 | -0.17838 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.043134 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18066 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.045093 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2546 | 50 | -0.18262 | -9.1309
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.37 | 0 | -0.18512 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1749 | 0 | -0.18512 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5227 | 0 | -0.18512 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2922 | 0 | -0.18512 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3064 | 0 | -0.18512 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2493 | 0 | -0.18512 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5695 | 0 | -0.18512 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6142 | 0 | -0.18512 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.904 | 0 | -0.18512 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5242 | 0 | -0.18516 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4289 | 0 | -0.18516 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7775 | 0 | -0.18516 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.425 | 0 | -0.18516 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8918 | 0 | -0.18516 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8585 | 0 | -0.18516 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.6542 | 161 | -0.19128 | -30.7959
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.923 | 166 | -0.19128 | -31.7523
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3307 | 248 | -0.19128 | -47.4371
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053753 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -29.3491 | 546 | -0.19128 | -104.4382
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053753 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.5632 | 0 | -0.19128 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.69879 | 13 | -0.19128 | -2.4866
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.054269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7909 | 0 | -0.19179 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.0467 | 0 | -0.19303 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.0467 | 0 | -0.19303 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.5977 | 0 | -0.19303 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -36.1949 | 651 | -0.19312 | -125.7242
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.3578 | 564 | -0.19312 | -108.9223
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -33.3594 | 600 | -0.19312 | -115.8748
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.056004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5818 | 0 | -0.19353 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.5058 | 0 | -0.20515 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.5058 | 0 | -0.20515 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0468 | 0 | -0.20515 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4044 | 0 | -0.20515 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0293 | 0 | -0.20836 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70835 | 0 | -0.20836 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.644 | 0 | -0.21243 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3481 | 0 | -0.21243 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3706 | 0 | -0.21243 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5652 | 0 | -0.21243 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4417 | 0 | -0.21243 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5915 | 0 | -0.21243 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7452 | 0 | -0.21243 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3483 | 0 | -0.21243 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0409 | 0 | -0.21243 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2432 | 0 | -0.21243 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7189 | 0 | -0.21243 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.393 | 0 | -0.21243 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8537 | 0 | -0.21243 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5652 | 0 | -0.21243 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2656 | 0 | -0.21243 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.715 | 0 | -0.21243 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6926 | 0 | -0.21243 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9922 | 0 | -0.21243 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9922 | 0 | -0.21243 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.8084 | 0 | -0.21243 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9356 | 0 | -0.22648 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.224 | 0 | -0.22648 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.088959 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22648 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.091624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0472 | 66 | -0.22915 | -15.1239
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.369 | 76 | -0.23449 | -17.821
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.369 | 76 | -0.23449 | -17.821
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.1809 | 105 | -0.23449 | -24.6211
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.1751 | 74 | -0.23449 | -17.352
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.1751 | 74 | -0.23449 | -17.352
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.89 | 102 | -0.23449 | -23.9176
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -130.1115 | 0 | -0.23513 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -129.6234 | 0 | -0.23513 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.11226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.67358 | 0 | -0.24979 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11768 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25521 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1618 | 0 | -0.27881 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.4443 | 0 | -0.27881 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1618 | 0 | -0.27881 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.303 | 0 | -0.27881 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.077 | 0 | -0.27881 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5322 | 0 | -0.27881 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.4992 | 0 | -0.27881 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9561 | 0 | -0.27881 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1602 | 0 | -0.27881 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4553 | 0 | -0.27881 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.1425 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.8399 | 0 | -0.28002 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0998 | 0 | -0.28395 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0249 | 0 | -0.28395 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1963 | 0 | -0.28395 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0249 | 0 | -0.28395 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1963 | 0 | -0.28395 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.147 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.176 | 0 | -0.28453 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.221 | 0 | -0.28559 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4055 | 0 | -0.28559 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14932 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.285 | 22 | -0.28685 | -6.3106
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6425 | 11 | -0.28685 | -3.1553
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6425 | 11 | -0.28685 | -3.1553
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1863 | 47.7 | -0.28818 | -13.7463
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6195 | 37.3 | -0.28818 | -10.7492
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9302 | 46 | -0.28818 | -13.2564
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2315 | 48 | -0.28818 | -13.8327
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.15096 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0202 | 0 | -0.28849 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.9689 | 0 | -0.28923 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.2104 | 0 | -0.28923 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -15.1702 | 0 | -0.28923 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.9968 | 0 | -0.28923 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.3002 | 0 | -0.28923 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.2662 | 0 | -0.28923 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.1517 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8204 | 0 | -0.28923 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.437 | 16 | -0.28984 | -4.6374
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 25 | -0.28984 | -7.2459
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2847 | 15 | -0.28984 | -4.3476
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9767 | 144 | -0.29014 | -41.7804
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.6918 | 188 | -0.29014 | -54.5466
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.4913 | 336 | -0.29077 | -97.7
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5846 | 180 | -0.29077 | -52.3393
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7293 | 0 | -0.29079 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7753 | 0 | -0.29079 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.4497 | 0 | -0.29079 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15329 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5931 | 180 | -0.29082 | -52.3477
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -51.2994 | 334 | -0.29112 | -97.233
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -52.2209 | 340 | -0.29112 | -98.9797
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6464 | 180 | -0.29112 | -52.401
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6464 | 180 | -0.29112 | -52.401
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8411 | 0 | -0.29117 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8411 | 0 | -0.29117 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.15379 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.8441 | 0 | -0.29132 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.1538 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.8445 | 0 | -0.29133 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.15452 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.4811 | 0 | -0.29204 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.5472 | 94 | -0.29228 | -27.4746
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.345 | 41 | -0.29228 | -11.9836
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8808 | 38 | -0.29228 | -11.1067
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9404 | 19 | -0.29228 | -5.5534
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.5472 | 94 | -0.29228 | -27.4746
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5713 | 36 | -0.29228 | -10.5222
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6546 | 43 | -0.29228 | -12.5682
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4047 | 22 | -0.29228 | -6.4302
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.904 | 148 | -0.29228 | -43.2578
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.7378 | 50 | -0.29228 | -14.6141
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.5116 | 55 | -0.29228 | -16.0755
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.7378 | 50 | -0.29228 | -14.6141
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.15486 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29238 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.8846 | 38 | -0.29238 | -11.1105
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9887 | 19.3 | -0.29238 | -5.643
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3229 | 15 | -0.29238 | -4.3857
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.15486 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.2783 | 47 | -0.29238 | -13.742
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3402 | 144 | -0.29267 | -42.1439
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3402 | 144 | -0.29267 | -42.1439
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5289 | 171 | -0.29267 | -50.0458
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.115 | 207 | -0.29267 | -60.5828
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.6199 | 216.7 | -0.29267 | -63.4217
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.5451 | 242 | -0.29267 | -70.8263
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7708 | 146.5 | -0.29296 | -42.9183
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.9884 | 147.9 | -0.29296 | -43.3284
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.8897 | 173 | -0.29296 | -50.6817
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8867 | 0 | -0.29475 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7295 | 0 | -0.29475 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8867 | 0 | -0.29475 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15731 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29483 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15894 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29646 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -100.4588 | 629 | -0.29724 | -186.9625
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.16173 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29925 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.16289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30042 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.2904 | 100 | -0.30043 | -30.043
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.2904 | 100 | -0.30043 | -30.043
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16385 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9324 | 24 | -0.30138 | -7.2331
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.9324 | 24 | -0.30138 | -7.2331
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.7686 | 23 | -0.30138 | -6.9317
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.17391 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -68.868 | 396 | -0.31143 | -123.3281
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.18285 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1942 | 0 | -0.32038 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.18349 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5138 | 0 | -0.32101 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -100.2298 | 546 | -0.3211 | -175.3188
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -137.6782 | 750 | -0.3211 | -240.8225
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6535 | 58 | -0.32121 | -18.63
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.3476 | 89 | -0.32121 | -28.5874
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.082 | 44 | -0.32121 | -14.1331
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.082 | 44 | -0.32121 | -14.1331
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8983 | 43 | -0.32121 | -13.8119
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2656 | 45 | -0.32121 | -14.4543
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5857 | 155 | -0.32195 | -49.9022
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.3521 | 170 | -0.32195 | -54.7314
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5857 | 155 | -0.32195 | -49.9022
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.3197 | 0 | -0.32195 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.3197 | 0 | -0.32195 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7664 | 0 | -0.32195 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -75.1827 | 407 | -0.32225 | -131.1556
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.6272 | 209 | -0.32234 | -67.37
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -39.9209 | 216 | -0.32234 | -69.6265
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.6865 | 47 | -0.32234 | -15.1502
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -76.2295 | 412 | -0.32255 | -132.8901
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.0092 | 400 | -0.32255 | -129.0195
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -78.5112 | 424 | -0.32269 | -136.8221
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -78.6964 | 425 | -0.32269 | -137.1448
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9396 | 147 | -0.32759 | -48.1558
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.229 | 138 | -0.32759 | -45.2075
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6091 | 140 | -0.32759 | -45.8627
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9396 | 147 | -0.32759 | -48.1558
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5918 | 182 | -0.32759 | -59.6215
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.6329 | 198 | -0.32759 | -64.863
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.19242 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -81.2029 | 422 | -0.32995 | -139.2388
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.953 | 114 | -0.3301 | -37.6309
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.7505 | 222 | -0.3301 | -73.2812
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.4329 | 184 | -0.3301 | -60.7376
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -43.1357 | 224 | -0.3301 | -73.9414
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.1456 | 115 | -0.3301 | -37.961
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.4236 | 0 | -0.33123 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.6173 | 0 | -0.33123 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46646 | 0 | -0.33189 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46646 | 0 | -0.33189 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19451 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.77802 | 0 | -0.33203 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9754 | 142 | -0.33454 | -47.5041
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5664 | 145 | -0.33454 | -48.5077
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.7485 | 151 | -0.33454 | -50.5149
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -57.1329 | 290 | -0.33454 | -97.0154
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.47318 | 0 | -0.33468 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.47318 | 0 | -0.33468 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55205 | 0 | -0.33468 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6309 | 0 | -0.33924 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6309 | 0 | -0.33924 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.7555 | 223.9 | -0.34188 | -76.5475
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.9803 | 225 | -0.34188 | -76.9236
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.8986 | 224.6 | -0.34188 | -76.7869
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -46.3277 | 226.7 | -0.34188 | -77.5048
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20737 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2442 | 0 | -0.34489 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.21002 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -90.9404 | 433 | -0.34755 | -150.489
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -122.779 | 584 | -0.34776 | -203.094
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -125.0916 | 595 | -0.34776 | -206.9194
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7975 | 0 | -0.36031 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.5748 | 0 | -0.36031 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7975 | 0 | -0.36031 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.2085 | 132 | -0.36638 | -48.3619
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.6662 | 134 | -0.36638 | -49.0946
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.9192 | 323 | -0.36638 | -118.34
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.4872 | 49 | -0.37196 | -18.226
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7839 | 46 | -0.37196 | -17.1101
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7839 | 46 | -0.37196 | -17.1101
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.0184 | 47 | -0.37196 | -17.4821
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.1027 | 154 | -0.37196 | -57.2816
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6961 | 148 | -0.37196 | -55.0499
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2528 | 48 | -0.37196 | -17.854
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2528 | 48 | -0.37196 | -17.854
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8755 | 0 | -0.37197 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8755 | 0 | -0.37197 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.2555 | 310 | -0.37383 | -115.8884
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -97.5952 | 413 | -0.37383 | -154.3933
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.4248 | 158 | -0.37439 | -59.1539
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.8986 | 160 | -0.37439 | -59.9027
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -41.4515 | 175 | -0.37439 | -65.5185
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.2188 | 152.5 | -0.37503 | -57.1914
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.5063 | 149.5 | -0.37503 | -56.0663
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -55.2425 | 232.6 | -0.37503 | -87.231
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0428 | 42 | -0.37664 | -15.8189
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.521 | 44 | -0.37664 | -16.5721
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.521 | 44 | -0.37664 | -16.5721
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2384 | 47 | -0.37664 | -17.7021
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -160.0597 | 569 | -0.41883 | -238.3118
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -163.4353 | 581 | -0.41883 | -243.3377

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Temple Pecan Creek - Temple Switch 345 kV [3412 - 3414] C: Lake Creek - Temple Switch 345kV [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -160.0597 | 0 | -0.41883 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.2813 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -163.4353 | 0 | -0.41883 | 0 | 0 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0428 | 42 | -0.37664 | -15.8189 | 42 | 15.8189
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.521 | 44 | -0.37664 | -16.5721 | 86 | 32.391 | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.521 | 44 | -0.37664 | -16.5721 | 130 | 48.9632 | North | 0.13753
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.23911 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2384 | 47 | -0.37664 | -17.7021 | 177 | 66.6652 | South | -0.18938
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.2188 | 152.5 | -0.37503 | -57.1914 | 329.5 | 123.8566 |  | 0.32691
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.5063 | 149.5 | -0.37503 | -56.0663 | 479 | 179.923
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.2375 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -55.2425 | 232.6 | -0.37503 | -87.231 | 711.6 | 267.154 | Line Rating | 1072
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.4248 | 158 | -0.37439 | -59.1539 | 869.6 | 326.3079 | Conc Gen | 2115.6
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.8986 | 160 | -0.37439 | -59.9027 | 1029.6 | 386.2105 | Weighted Imp. | 791.9391
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.23687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -41.4515 | 175 | -0.37439 | -65.5185 | 1204.6 | 451.7291 | PTDF | 0.37433
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.2555 | 310 | -0.37383 | -115.8884 | 1514.6 | 567.6175
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.23631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -97.5952 | 413 | -0.37383 | -154.3933 | 1927.6 | 722.0108 | Concentration | 1.1451
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8755 | 0 | -0.37197 | 0 | 1927.6 | 722.0108
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23444 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8755 | 0 | -0.37197 | 0 | 1927.6 | 722.0108
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.4872 | 49 | -0.37196 | -18.226 | 1976.6 | 740.2368
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7839 | 46 | -0.37196 | -17.1101 | 2022.6 | 757.3469
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7839 | 46 | -0.37196 | -17.1101 | 2068.6 | 774.457
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.0184 | 47 | -0.37196 | -17.4821 | 2115.6 | 791.9391
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.1027 | 154 | -0.37196 | -57.2816
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23443 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6961 | 148 | -0.37196 | -55.0499
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2528 | 48 | -0.37196 | -17.854
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23443 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2528 | 48 | -0.37196 | -17.854
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.2085 | 132 | -0.36638 | -48.3619
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.6662 | 134 | -0.36638 | -49.0946
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.22885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.9192 | 323 | -0.36638 | -118.34
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7975 | 0 | -0.36031 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.5748 | 0 | -0.36031 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.22279 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7975 | 0 | -0.36031 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -122.779 | 0 | -0.34776 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.21024 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -125.0916 | 0 | -0.34776 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.21011 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5056 | 50 | -0.34764 | -17.3819
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.21002 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -90.9404 | 0 | -0.34755 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20737 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2442 | 0 | -0.34489 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.7555 | 223.9 | -0.34188 | -76.5475
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.9803 | 225 | -0.34188 | -76.9236
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.8986 | 224.6 | -0.34188 | -76.7869
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.20436 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -46.3277 | 226.7 | -0.34188 | -77.5048
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6309 | 0 | -0.33924 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20172 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6309 | 0 | -0.33924 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.47318 | 0 | -0.33468 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.47318 | 0 | -0.33468 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19716 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55205 | 0 | -0.33468 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9754 | 142 | -0.33454 | -47.5041
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5664 | 145 | -0.33454 | -48.5077
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.7485 | 151 | -0.33454 | -50.5149
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.19701 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -57.1329 | 290 | -0.33454 | -97.0154
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19451 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.77802 | 0 | -0.33203 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46646 | 0 | -0.33189 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19436 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46646 | 0 | -0.33189 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.4236 | 0 | -0.33123 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.1937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.6173 | 0 | -0.33123 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.953 | 0 | -0.3301 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.7505 | 0 | -0.3301 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.4329 | 0 | -0.3301 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -43.1357 | 0 | -0.3301 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.1456 | 0 | -0.3301 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.19242 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -81.2029 | 422 | -0.32995 | -139.2388
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9396 | 147 | -0.32759 | -48.1558
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.229 | 138 | -0.32759 | -45.2075
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6091 | 140 | -0.32759 | -45.8627
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.9396 | 147 | -0.32759 | -48.1558
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5918 | 182 | -0.32759 | -59.6215
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.19007 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.6329 | 198 | -0.32759 | -64.863
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18574 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32326 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -78.5112 | 0 | -0.32269 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.18517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -78.6964 | 0 | -0.32269 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -76.2295 | 412 | -0.32255 | -132.8901
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18502 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.0092 | 400 | -0.32255 | -129.0195
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.6272 | 209 | -0.32234 | -67.37
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18482 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -39.9209 | 216 | -0.32234 | -69.6265
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.6865 | 47 | -0.32234 | -15.1502
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.5017 | 46 | -0.32234 | -14.8279
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -75.1827 | 407 | -0.32225 | -131.1556
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.3197 | 0 | -0.32195 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.3197 | 0 | -0.32195 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.18443 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7664 | 0 | -0.32195 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5857 | 155 | -0.32195 | -49.9022
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.3521 | 170 | -0.32195 | -54.7314
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.18442 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.5857 | 155 | -0.32195 | -49.9022
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.6535 | 58 | -0.32121 | -18.63
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.18368 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.3476 | 89 | -0.32121 | -28.5874
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.082 | 44 | -0.32121 | -14.1331
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.082 | 44 | -0.32121 | -14.1331
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8983 | 43 | -0.32121 | -13.8119
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.18368 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2656 | 45 | -0.32121 | -14.4543
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -100.2298 | 0 | -0.3211 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.18357 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -137.6782 | 0 | -0.3211 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.18349 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5138 | 0 | -0.32101 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.18285 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1942 | 0 | -0.32038 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.17391 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -68.868 | 0 | -0.31143 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16385 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.9324 | 24 | -0.30138 | -7.2331
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.9324 | 24 | -0.30138 | -7.2331
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.16385 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.7686 | 23 | -0.30138 | -6.9317
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.2904 | 100 | -0.30043 | -30.043
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -16.2904 | 100 | -0.30043 | -30.043
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1629 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30043 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.16289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.30042 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.16198 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3606 | 8.4 | -0.2995 | -2.5158
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.16173 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29925 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -100.4588 | 0 | -0.29724 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15894 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29646 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15731 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29483 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8867 | 0 | -0.29475 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7295 | 0 | -0.29475 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15722 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8867 | 0 | -0.29475 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7708 | 146.5 | -0.29296 | -42.9183
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.9884 | 147.9 | -0.29296 | -43.3284
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15543 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.8897 | 173 | -0.29296 | -50.6817
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.115 | 207 | -0.29267 | -60.5828
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.6199 | 216.7 | -0.29267 | -63.4217
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.5451 | 242 | -0.29267 | -70.8263
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3402 | 144 | -0.29267 | -42.1439
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3402 | 144 | -0.29267 | -42.1439
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15514 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5289 | 171 | -0.29267 | -50.0458
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.8846 | 38 | -0.29238 | -11.1105
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9887 | 19.3 | -0.29238 | -5.643
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.15486 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3229 | 15 | -0.29238 | -4.3857
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.15486 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.2783 | 47 | -0.29238 | -13.742
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.15486 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29238 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.5472 | 0 | -0.29228 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.345 | 0 | -0.29228 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8808 | 0 | -0.29228 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9404 | 0 | -0.29228 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.5472 | 0 | -0.29228 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5713 | 0 | -0.29228 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6546 | 0 | -0.29228 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4047 | 0 | -0.29228 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.904 | 0 | -0.29228 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.7378 | 0 | -0.29228 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.5116 | 0 | -0.29228 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.15476 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.7378 | 0 | -0.29228 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.15452 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.4811 | 0 | -0.29204 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.1538 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.8445 | 0 | -0.29133 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.15379 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.8441 | 0 | -0.29132 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8411 | 0 | -0.29117 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.15364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8411 | 0 | -0.29117 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -51.2994 | 334 | -0.29112 | -97.233
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.15359 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -52.2209 | 340 | -0.29112 | -98.9797
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6464 | 180 | -0.29112 | -52.401
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.15359 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6464 | 180 | -0.29112 | -52.401
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15329 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5931 | 180 | -0.29082 | -52.3477
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7293 | 0 | -0.29079 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.7753 | 0 | -0.29079 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.15327 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.4497 | 0 | -0.29079 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.4913 | 336 | -0.29077 | -97.7
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.15325 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5846 | 180 | -0.29077 | -52.3393
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9767 | 144 | -0.29014 | -41.7804
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.15262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.6918 | 188 | -0.29014 | -54.5466
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.437 | 0 | -0.28984 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8078 | 0 | -0.28984 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.15231 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2847 | 0 | -0.28984 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.9689 | 0 | -0.28923 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.2104 | 0 | -0.28923 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -15.1702 | 0 | -0.28923 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.9968 | 0 | -0.28923 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.3002 | 0 | -0.28923 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.1517 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.2662 | 0 | -0.28923 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.1517 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8204 | 0 | -0.28923 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.15096 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0202 | 0 | -0.28849 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1863 | 47.7 | -0.28818 | -13.7463
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.6195 | 37.3 | -0.28818 | -10.7492
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9302 | 46 | -0.28818 | -13.2564
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.15066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2315 | 48 | -0.28818 | -13.8327
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14932 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.285 | 22 | -0.28685 | -6.3106
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6425 | 11 | -0.28685 | -3.1553
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14932 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6425 | 11 | -0.28685 | -3.1553
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.221 | 0 | -0.28559 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14807 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4055 | 0 | -0.28559 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.147 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.176 | 0 | -0.28453 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.0998 | 0 | -0.28395 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0249 | 0 | -0.28395 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1963 | 0 | -0.28395 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0249 | 0 | -0.28395 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1963 | 0 | -0.28395 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14642 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.7104 | 0 | -0.28395 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.1425 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.8399 | 0 | -0.28002 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1618 | 0 | -0.27881 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.4443 | 0 | -0.27881 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.1618 | 0 | -0.27881 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.303 | 0 | -0.27881 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.077 | 0 | -0.27881 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5322 | 0 | -0.27881 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.4992 | 0 | -0.27881 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9561 | 0 | -0.27881 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1602 | 0 | -0.27881 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.14129 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4553 | 0 | -0.27881 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11768 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25521 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.11226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.67358 | 0 | -0.24979 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -130.1115 | 0 | -0.23513 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.097608 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -129.6234 | 0 | -0.23513 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.369 | 76 | -0.23449 | -17.821
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.369 | 76 | -0.23449 | -17.821
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.1809 | 105 | -0.23449 | -24.6211
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.1751 | 74 | -0.23449 | -17.352
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.1751 | 74 | -0.23449 | -17.352
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.096961 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.89 | 102 | -0.23449 | -23.9176
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.091624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0472 | 66 | -0.22915 | -15.1239
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9356 | 0 | -0.22648 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.088959 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.224 | 0 | -0.22648 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.088959 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22648 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.644 | 0 | -0.21243 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3481 | 0 | -0.21243 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3706 | 0 | -0.21243 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5652 | 0 | -0.21243 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4417 | 0 | -0.21243 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5915 | 0 | -0.21243 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7452 | 0 | -0.21243 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3483 | 0 | -0.21243 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0409 | 0 | -0.21243 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2432 | 0 | -0.21243 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7189 | 0 | -0.21243 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.393 | 0 | -0.21243 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8537 | 0 | -0.21243 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5652 | 0 | -0.21243 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2656 | 0 | -0.21243 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.715 | 0 | -0.21243 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6926 | 0 | -0.21243 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9922 | 0 | -0.21243 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9922 | 0 | -0.21243 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.074903 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.8084 | 0 | -0.21243 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0293 | 0 | -0.20836 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.070835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70835 | 0 | -0.20836 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.5058 | 0 | -0.20515 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.5058 | 0 | -0.20515 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0468 | 0 | -0.20515 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.06762 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.4044 | 0 | -0.20515 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.056004 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5818 | 0 | -0.19353 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -36.1949 | 0 | -0.19312 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.3578 | 0 | -0.19312 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.055599 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -33.3594 | 0 | -0.19312 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.0467 | 0 | -0.19303 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.0467 | 0 | -0.19303 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.055501 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.5977 | 0 | -0.19303 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.054269 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7909 | 0 | -0.19179 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.6542 | 161 | -0.19128 | -30.7959
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.923 | 166 | -0.19128 | -31.7523
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053753 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3307 | 248 | -0.19128 | -47.4371
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053753 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -29.3491 | 546 | -0.19128 | -104.4382
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053753 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.5632 | 0 | -0.19128 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053753 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.69879 | 13 | -0.19128 | -2.4866
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7775 | 0 | -0.18516 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.425 | 0 | -0.18516 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8918 | 0 | -0.18516 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.047632 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8585 | 0 | -0.18516 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5242 | 0 | -0.18516 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.04763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4289 | 0 | -0.18516 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.37 | 0 | -0.18512 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1749 | 0 | -0.18512 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5227 | 0 | -0.18512 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2922 | 0 | -0.18512 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3064 | 0 | -0.18512 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2493 | 0 | -0.18512 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.5695 | 0 | -0.18512 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.047599 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6142 | 0 | -0.18512 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.047599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.904 | 0 | -0.18512 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.045093 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2546 | 50 | -0.18262 | -9.1309
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.043134 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18066 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7175 | 0 | -0.17838 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5786 | 0 | -0.17838 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5541 | 0 | -0.17838 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2264 | 0 | -0.17838 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.040852 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49839 | 0 | -0.17838 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3974 | 0 | -0.17748 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.039957 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5972 | 0 | -0.17748 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7769 | 46 | -0.17615 | -8.1031
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1246 | 55 | -0.17615 | -9.6885
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1246 | 55 | -0.17615 | -9.6885
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.038629 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.086 | 54 | -0.17615 | -9.5124
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.987 | 0 | -0.17582 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.038295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0636 | 0 | -0.17582 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1748 | 0 | -0.17536 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.944 | 0 | -0.17536 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.9592 | 0 | -0.17536 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.9403 | 0 | -0.17536 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.037836 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.1779 | 0 | -0.17536 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.037465 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3113 | 0 | -0.17499 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.037066 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.44479 | 12 | -0.17459 | -2.0951
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.037066 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17459 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.037043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.2603 | 169 | -0.17457 | -29.5021
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.037012 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.107 | 165 | -0.17454 | -28.7987
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5112 | 0 | -0.17451 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.036988 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4079 | 0 | -0.17451 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.036905 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.8608 | 213 | -0.17443 | -37.1537
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.036896 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59772 | 0 | -0.17442 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3608 | 0 | -0.17441 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3313 | 0 | -0.17441 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0469 | 0 | -0.17441 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.036888 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.715 | 0 | -0.17441 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.036874 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.4073 | 228 | -0.1744 | -39.7631
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6348 | 0 | -0.17439 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.846 | 0 | -0.17439 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.03686 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.787 | 0 | -0.17439 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5771 | 0 | -0.17382 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6134 | 0 | -0.17382 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4156 | 0 | -0.17382 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.036297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0889 | 0 | -0.17382 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.035405 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8151 | 0 | -0.17293 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.484 | 42 | -0.17286 | -7.2601
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.484 | 42 | -0.17286 | -7.2601
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3427 | 38 | -0.17286 | -6.5686
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.035333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3427 | 38 | -0.17286 | -6.5686
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.035104 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.073 | 0 | -0.17263 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.035104 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.739 | 0 | -0.17263 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5019 | 104 | -0.1712 | -17.8046
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5019 | 104 | -0.1712 | -17.8046
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.7846 | 53 | -0.1712 | -9.0735
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9193 | 57 | -0.1712 | -9.7583
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8183 | 54 | -0.1712 | -9.2447
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.953 | 58 | -0.1712 | -9.9295
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.033672 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.953 | 58 | -0.1712 | -9.9295
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.033118 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -24.3417 | 735 | -0.17064 | -125.4231
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1135 | 0 | -0.17028 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1364 | 0 | -0.17028 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0709 | 0 | -0.17028 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5032 | 0 | -0.17028 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57968 | 0 | -0.17028 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6681 | 0 | -0.17028 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65172 | 0 | -0.17028 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1462 | 0 | -0.17028 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5895 | 0 | -0.17028 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7969 | 0 | -0.17028 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.03275 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.847 | 0 | -0.17028 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.032283 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3874 | 12 | -0.16981 | -2.0377
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15843 | 0 | -0.16921 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.031685 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66539 | 0 | -0.16921 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0589 | 0 | -0.1692 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0906 | 0 | -0.1692 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2173 | 0 | -0.1692 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9956 | 0 | -0.1692 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9639 | 0 | -0.1692 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2943 | 0 | -0.1692 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.031676 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8689 | 0 | -0.1692 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.031647 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.37976 | 0 | -0.16917 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.031605 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -23.4825 | 743 | -0.16913 | -125.6641
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.03133 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9188 | 0 | -0.16886 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.031149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.3576 | 172 | -0.16867 | -29.012
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.897 | 0 | -0.16761 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8549 | 0 | -0.16761 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7797 | 0 | -0.16761 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.03008 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.0975 | 0 | -0.16761 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.8246 | 398 | -0.16724 | -66.5598
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7145 | 59 | -0.16659 | -9.8286
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7145 | 59 | -0.16659 | -9.8286
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.02906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6274 | 56 | -0.16659 | -9.3288
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.937 | 0 | -0.16028 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5501 | 0 | -0.16028 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5046 | 0 | -0.16028 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.022757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5046 | 0 | -0.16028 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.022757 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6866 | 0 | -0.16028 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13753 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13753 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13753 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.19257 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -19.257 | 0 | -0.0031876 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.095774 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.093608 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.18938 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.18938 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6172 | 0 | 0.22581 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6828 | 0 | 0.22581 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6828 | 0 | 0.22581 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.036428 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.8426 | 0 | 0.22581 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7544 | 48 | 0.22593 | 10.8448
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.036551 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6813 | 46 | 0.22593 | 10.3929
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.036551 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.8379 | 105 | 0.22593 | 23.723
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.040111 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.2836 | 0 | 0.22949 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.040218 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.68371 | 17 | 0.2296 | 3.9032
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.040218 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2296 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.047651 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.0624 | 0 | 0.23703 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.056431 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4647 | 0 | 0.24581 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078876 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26826 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.6283 | 0 | 0.2755 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.6283 | 0 | 0.2755 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1153 | 0 | 0.2755 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.086115 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1756 | 0 | 0.2755 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.7129 | 0 | 0.29182 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10243 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.8934 | 0 | 0.29182 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10372 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7127 | 0 | 0.29311 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10448 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9931 | 0 | 0.29387 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.4226 | 0 | 0.29466 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.4853 | 0 | 0.29928 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.1099 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.4853 | 0 | 0.29928 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11002 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8015 | 0 | 0.2994 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11005 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8037 | 0 | 0.29943 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2685 | 0 | 0.29963 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8198 | 0 | 0.29963 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11025 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4099 | 0 | 0.29963 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8937 | 0 | 0.30055 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8937 | 0 | 0.30055 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11461 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.55013 | 0 | 0.30399 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12259 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.7783 | 0 | 0.31197 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1125 | 66 | 0.3123 | 20.6118
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9896 | 65 | 0.3123 | 20.2995
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12292 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2354 | 67 | 0.3123 | 20.9241
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12292 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12292 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3123 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3061 | 0 | 0.31241 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12303 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6909 | 0 | 0.31241 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12342 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.3896 | 0 | 0.3128 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.81723 | 0 | 0.3132 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12382 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2471 | 0 | 0.3132 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0017 | 0 | 0.31384 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.6068 | 0 | 0.31384 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1496 | 0 | 0.31384 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12446 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.6967 | 0 | 0.31384 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12499 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7487 | 0 | 0.31437 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.0619 | 208.2 | 0.31456 | 65.4913
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.7877 | 142.1 | 0.31456 | 44.6989
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.5734 | 132.4 | 0.31456 | 41.6477
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.0241 | 136 | 0.31456 | 42.7801
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.401 | 147 | 0.31456 | 46.2402
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12518 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.2872 | 210 | 0.31456 | 66.0575
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7639 | 70 | 0.31458 | 22.0207
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7639 | 70 | 0.31458 | 22.0207
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.6185 | 92.8 | 0.31458 | 29.1932
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0159 | 80 | 0.31458 | 25.1665
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0159 | 80 | 0.31458 | 25.1665
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.1252 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3979 | 115 | 0.31458 | 36.1769
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12527 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2655 | 0 | 0.31465 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5918 | 0 | 0.31467 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12558 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8986 | 0 | 0.31496 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12563 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2412 | 0 | 0.31501 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4445 | 0 | 0.31531 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12593 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.9186 | 0 | 0.31531 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12641 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1688 | 0 | 0.31579 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1718 | 0 | 0.31581 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.4587 | 0 | 0.31581 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12643 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.5187 | 0 | 0.31581 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1754 | 0 | 0.31584 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12672 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.512 | 0 | 0.3161 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8771 | 0 | 0.3162 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 9.3083 | 0 | 0.3162 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12682 | west | 8 | N | N | Nwest | Nwest | 1 | 8.9278 | 0 | 0.3162 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.8312 | 0 | 0.31622 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12684 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.8312 | 0 | 0.31622 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0774 | 0 | 0.31657 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9803 | 0 | 0.31657 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.4366 | 0 | 0.31657 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12718 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.5036 | 0 | 0.31657 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4136 | 66 | 0.31686 | 20.9129
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 69 | 0.31686 | 21.8634
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 69 | 0.31686 | 21.8634
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 67 | 0.31686 | 21.2297
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5411 | 67 | 0.31686 | 21.2297
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12748 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2861 | 65 | 0.31686 | 20.596
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.1276 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0389 | 0 | 0.31698 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2418 | 150.7 | 0.31707 | 47.7818
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2801 | 151 | 0.31707 | 47.8769
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12768 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.651 | 177.4 | 0.31707 | 56.2474
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0067 | 0 | 0.31709 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12771 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3248 | 0 | 0.31709 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6467 | 0 | 0.31713 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12774 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7924 | 0 | 0.31713 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 3.1936 | 0 | 0.31713 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8379 | 0 | 0.31713 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12774 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8379 | 0 | 0.31713 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.3864 | 151.5 | 0.31735 | 48.0778
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.4888 | 152.3 | 0.31735 | 48.3317
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12796 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7134 | 177.5 | 0.31735 | 56.3288
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12808 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7586 | 0 | 0.31746 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.245 | 0 | 0.31768 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.1283 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.9583 | 0 | 0.31768 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0525 | 0 | 0.3178 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12842 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0525 | 0 | 0.3178 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8407 | 0 | 0.31847 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8766 | 0 | 0.31847 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.4265 | 0 | 0.31847 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3611 | 0 | 0.31847 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.5539 | 0 | 0.31847 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12909 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3913 | 0 | 0.31847 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.0268 | 0 | 0.3187 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3583 | 0 | 0.3187 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1994 | 0 | 0.3187 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12932 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.4751 | 0 | 0.3187 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12954 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4318 | 0 | 0.31893 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.13136 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8817 | 0 | 0.32074 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13371 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.4844 | 0 | 0.32309 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13372 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.5579 | 0 | 0.3231 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.4282 | 182 | 0.3236 | 58.8958
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13422 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 64.963 | 484 | 0.3236 | 156.6241
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13483 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7413 | 0 | 0.32421 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13489 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32427 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13523 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3128 | 0 | 0.32461 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.0877 | 0 | 0.32511 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.6446 | 0 | 0.32511 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.6806 | 0 | 0.32511 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13573 | north | 1 | N | N | Nnorth | Nnorth | 1 | 54.1555 | 0 | 0.32511 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13639 | west | 4 | Y | N | Ywest | Nwest | 1 | 88.6158 | 0 | 0.32578 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 107.0881 | 0 | 0.3258 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.4523 | 0 | 0.3258 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 106.406 | 0 | 0.3258 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13972 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.813 | 242 | 0.32911 | 79.6435
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.14001 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 51.2426 | 366 | 0.32939 | 120.5565
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8036 | 20 | 0.32956 | 6.5912
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.14018 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.383 | 17 | 0.32956 | 5.6025
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.1408 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.5392 | 224 | 0.33018 | 73.9609
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.14151 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.4905 | 0 | 0.33089 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8155 | 161 | 0.33109 | 53.306
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2406 | 164 | 0.33109 | 54.2993
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2406 | 164 | 0.33109 | 54.2993
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.6684 | 414 | 0.33109 | 137.0727
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9572 | 162 | 0.33109 | 53.6371
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8155 | 161 | 0.33109 | 53.306
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0989 | 163 | 0.33109 | 53.9682
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 57.9598 | 409 | 0.33109 | 135.4172
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8567 | 20 | 0.33222 | 6.6443
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5709 | 25 | 0.33222 | 8.3054
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14283 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.8562 | 41 | 0.33222 | 13.6209
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14284 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 17.1414 | 0 | 0.33223 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7154 | 0 | 0.33233 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14295 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.7154 | 0 | 0.33233 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.143 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 55.4824 | 388 | 0.33238 | 128.9628
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.143 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.6429 | 515 | 0.33238 | 171.1749
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.8013 | 0 | 0.3324 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.8045 | 0 | 0.3324 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14301 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 115.5545 | 0 | 0.3324 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.3001 | 79 | 0.33242 | 26.2613
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.1621 | 106 | 0.33242 | 35.2367
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.8837 | 146 | 0.33242 | 48.5335
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14304 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.871 | 76 | 0.33242 | 25.264
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14307 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7227 | 40 | 0.33245 | 13.298
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.7309 | 0 | 0.33246 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.389 | 0 | 0.33246 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14308 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.6481 | 0 | 0.33246 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9101 | 160 | 0.33257 | 53.2113
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3373 | 156 | 0.33257 | 51.881
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0648 | 196 | 0.33257 | 65.1838
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.3373 | 156 | 0.33257 | 51.881
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4805 | 157 | 0.33257 | 52.2136
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14319 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3512 | 198 | 0.33257 | 65.8489
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.1433 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.021 | 370 | 0.33268 | 123.0925
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.062 | 0 | 0.33268 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.2053 | 0 | 0.33268 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.2797 | 0 | 0.33268 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.4919 | 0 | 0.33268 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.6352 | 0 | 0.33268 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.1433 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.423 | 0 | 0.33268 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.3867 | 170 | 0.33283 | 56.5817
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14345 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.5945 | 520 | 0.33283 | 173.0734
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2799 | 204 | 0.33291 | 67.9139
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8493 | 201 | 0.33291 | 66.9152
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14353 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.734 | 242 | 0.33291 | 80.5646
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33295 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14356 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33295 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7437 | 0 | 0.33298 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14359 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.7437 | 0 | 0.33298 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14433 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33371 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14436 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33375 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14461 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.2691 | 0 | 0.334 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7026 | 60 | 0.33443 | 20.0656
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.1378 | 63 | 0.33443 | 21.0689
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.8977 | 288 | 0.33486 | 96.4398
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3853 | 147 | 0.33486 | 49.2245
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14548 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3853 | 147 | 0.33486 | 49.2245
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.1992 | 118 | 0.33514 | 39.5463
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14576 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.7619 | 115 | 0.33514 | 38.5409
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 81.0403 | 556 | 0.33514 | 186.337
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14582 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.6449 | 73 | 0.3352 | 24.4699
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3527 | 119 | 0.3352 | 39.8892
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14582 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.8933 | 205 | 0.3352 | 68.7167
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.8737 | 102 | 0.3352 | 34.1908
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14582 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9988 | 96 | 0.3352 | 32.1795
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6295 | 18 | 0.33547 | 6.0384
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6295 | 18 | 0.33547 | 6.0384
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.14608 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.5512 | 38 | 0.33547 | 12.7478
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.7779 | 196 | 0.33621 | 65.8969
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14683 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2977 | 111 | 0.33621 | 37.3191
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.147 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.147 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33638 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.7639 | 0 | 0.33697 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14759 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.9115 | 0 | 0.33697 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.185 | 217.3 | 0.3375 | 73.3378
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.3632 | 205 | 0.3375 | 69.1866
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14811 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 40.346 | 272.4 | 0.3375 | 91.9338
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1486 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33798 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.14957 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.0612 | 435 | 0.33895 | 147.4426
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.4706 | 70 | 0.33896 | 23.7274
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.321 | 69 | 0.33896 | 23.3884
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.321 | 69 | 0.33896 | 23.3884
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14958 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1714 | 68 | 0.33896 | 23.0494
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.14987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 59.1987 | 395 | 0.33925 | 134.0047
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.14987 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.1934 | 435 | 0.33925 | 147.5748
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.8712 | 168 | 0.34338 | 57.6874
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.15399 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.8596 | 90 | 0.34338 | 30.904
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.864 | 216.4 | 0.34587 | 74.8464
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.8171 | 216.1 | 0.34587 | 74.7426
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.0815 | 224 | 0.346 | 77.5032
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.3948 | 226 | 0.346 | 78.1952
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.2022 | 212 | 0.346 | 73.3512
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15661 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.0456 | 211 | 0.346 | 73.0053
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.697 | 0 | 0.36918 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.1798 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.697 | 0 | 0.36918 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0908 | 150 | 0.37665 | 56.4982
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.18727 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.9818 | 80 | 0.37665 | 30.1324
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.38835 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.19897 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.38835 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.20866 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 53.2083 | 255 | 0.39804 | 101.5008
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 31.0903 | 149 | 0.39804 | 59.3083
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.20866 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 31.925 | 153 | 0.39804 | 60.9005
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.23958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42896 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.23958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 188.5495 | 787 | 0.42896 | 337.5934

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Dynamic line rating
F | Rating
20 | 1340
25 | 1340
30 | 1340
35 | 1340
40 | 1340
45 | 1340
50 | 1340
55 | 1340
60 | 1334
65 | 1307
70 | 1280
75 | 1251
80 | 1223
85 | 1194
90 | 1163
95 | 1132
100 | 1098
105 | 1065
110 | 1031
115 | 994