ERCOT Operating Guides

Section 6:  Reports and Forms

October 1, 2009

Contents

6	Reports and Forms	6-3

6.1	Reports	6-3

6.1.1	Disturbance Report	6-3

6.1.2	Relay Misoperation Report	6-4

6.2	Forms	6-6

6.2.1	Turbine Governor Speed Regulation Tests	6-6

6.2.2	Seasonal Unit Net Real Power Capability Verification	6-19

6.2.3	Biennial Unit Reactive Limits (Lead and Lag) Verification	6-21

6.2.4	Seasonal Hydro Responsive Reserve Net Capability Verification	6-25

6.2.5	Annual LaaR Telemetry Test	6-26

6.2.6	Biennial Test for LaaRs Providing Responsive Reserve Service	6-27

6.2.7	Unit Alternative Fuel Capability	6-28

6.3	Document Control	6-32

# Reports and Forms

## 6.1	Reports

### 6.1.1	Disturbance Report

#### 6.1.1.1	ERCOT Data

ERCOT will record the following data when frequency deviations of 0.175 Hz or greater occur and will use this information to generate the ERCOT initial Disturbance Report:

- Net interchange (MW) immediately before the disturbance.

- Net interchange (MW) immediately after the disturbance.

- Control Bias.

- Net MW Capability (including any capability lost) at the time of the disturbance.

- Net System Load (MW) for the hour ending closest to the time of the disturbance.

- Scheduled Net Interchange (MW) at the time of the disturbance.

- Amount of interruptible load (MW) tripped.

#### 6.1.1.2	PGC Data

The PGC losing the unit will provide the following data to the ERCOT Operator as soon as possible after the disturbance:

- Unit Lost.

- Released net dependable capability (MW).

- Net generation at time of loss.

- Nature of trouble/Reason for loss.

- Time/Date of loss.

The above information, plus unit performance data, will be used by ERCOT to generate detailed reports for the PDC Task Force and will be submitted to the PDC Task Force at the next regularly scheduled meeting.

### 6.1.2	Relay Misoperation Report

Relay misoperations shall be reported in any format compatible with ERCOT (i.e., Microsoft Excel, Microsoft Word, or PDF) except where a specific format is requested.  All fields of data specified in the table below shall be included in the report.  The file shall include the "Field Names" listed in the table below as headers for each field and the data size/format shall match "Size or Format" specified in the table below.

| Field Name | Type | Size or Format | Description |
| --- | --- | --- | --- |
| Misop_Date | Date | mm/dd/yyyy | The date that misoperation occurred. |
| Misop_Time | Time | hh:nn:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| Time_Zone | Text | 50 | Define the standard time of the misoperation time noted (i.e. GMT, CT, EST, etc.). |
| Utility | Text | 25 | Name of the facility owner |
| Voltage | Text | 10 | Transmission voltage (345 kV, 138 kV, 69 kV, etc.). |
| Protected_Equipment | Text | 25 | The transmission element (line, autotransformer, bus, etc.) protected by the protection scheme. |
| Substation | Text | 50 | Name of the substation where the misoperated element or equipment located. |
| Protection_Scheme | Text | 25 | Type of protection scheme applied (i.e. Differential, DCB, SPS, Step distance, etc.). |
| Equipment_Name | Text | 50 | Specific description of the protected transmission. |
| CB_Number | Text | 50 | equipment Unique circuit breaker number assigned or used by the facility owner that effected the actual isolation. |
| Fault_Type | Text | 50 | Type of fault occurred (L-L, L-G, L-L-G, 3L-G, etc. If the misoperation occurred for a non-fault condition, note this field with ‘N/A’). |
| Communication_Method | Text | 50 | Type of communication method used for the protection scheme (i.e. Pilot wire, fiber, power-line carrier, etc.). |
| Manufacturer | Text | 50 | Relay Manufacturer’s name. |
| Relay_Type | Text | 50 | Relay Type or style name (i.e. SEL-321, REL-512, CO-9, etc.). |
| Relay_Style | Text | 50 | Relay model number. |
| Misop_Category | Text | 50 | Relay events constitute as reportable protective relay system misoperation as detailed in ERCOT Operating Guide 7, Section 7.2.3, Performance Analysis Requirements for ERCOT System Facilities. |
| Misop_Description | Text | 32,767 | Description of the protective element/scheme failure that caused the misoperation. |
| Investigation_Results | Text | 32,767 | Description of the analysis results from the misoperation review and any deficiencies identified. |
| Corrective_Action | Text | 32,767 | An action plan to correct any deficiencies identified in the investigation results or any additional action plan to avoid similar operations in the future. |
| Target_Date | Date | mm/dd/yyyy | Target date to implement the corrective action plan at the terminal(s) where the misoperation(s) occurred. This could also be the date that the corrective action plan was implemented. |
| Recommendation | Text | 32,767 | System wide corrective action plan or long term solution to avoid similar misoperations (i.e. design changes, equipment replacements, etc.). |
| Report_By | Text | 25 | Individual who completed the report. |
| Phone | Text | 50 | Business phone number of the individual who completed the report. |
| Report_Date | Date | mm/dd/yyyy | The date at which the report was completed (i.e. when corrective action was implemented). |

## 6.2	Forms

### 6.2.1	Turbine Governor Speed Regulation Tests

#### 6.2.1.1	Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

QSE:						Resource Entity:

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM |  |  |  |  |  |  |
| Frequency Hz |  |  |  |  |  |  |

Speed Changer Travel Time:

a.	From Low-Speed Stop to High-Speed Stop in _________seconds.

b.	From High-Speed Stop to Low-Speed Stop in _________seconds.

Over-speed Trip Test Speed at _________rpm.

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

#### 6.2.1.2	Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600=3850−3570×1003600=7.78%

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600=3600−3310×1003600=8.06%

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600=3500−3210×1003600=8.06%

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM | 3850 | 3570 | 3600 | 3310 | 3500 | 3210 |
| Frequency Hz | 64.2 | 59.5 | 60.0 | 55.0 | 58.3 | 53.5 |

Speed Changer Travel Time:

a.	From Low-Speed Stop to High-Speed Stop in 	73	seconds.

b.	From High-Speed Stop to Low-Speed Stop in 	74	seconds.

Over-speed Trip Test Speed at 	3965	rpm.

Comments:

#### 6.2.1.3	Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

QSE:						Resource Entity:

Turbine Governor Speed Regulation Test Procedures

- Simulate unit on line and turbine speed at 3600 RPM.

- Set load reference at minimum value.

- Monitor valve demand signal and record as value 'A' (in %).

- Reduce speed until valve demand just reaches maximum value.
Record valve demand as value 'B' (in %) and speed as value 'C' (in RPM).

- Set speed at 3600 and load reference at maximum value.

- Monitor valve demand signal and record as value 'D' (in %).

- Increase speed until valve demand just reaches minimum value.
Record valve demand as value 'E' (in %) and speed as value 'F' (in RPM).

Turbine Governor Speed Regulation Test Results

|  | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Valve Demand (%) |  |  |  |  |  |  |
| Speed (rpm) |  |  |  |  |  |  |

Speed Regulation With Decreasing Speed

RD=100B−A×3600−C3600×100

Speed Regulation With Increasing Speed

RI=100D−E×F−36003600×100

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

#### 6.2.1.4	Definitions

| System Frequency Response | This response is a function of three key variables; the system's composite governor droop, the percent of spinning capacity which is actually providing governor response, and the frequency response characteristic of the connected load. |
| --- | --- |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no load to full load. It is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead Band | The range of deviations of system frequency (+/-) that produces no turbine governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| Valve Position Limiter | A device that acts on the speed and load governing system to prevent the governor-controlled valves from opening beyond a pre-set limit. |
| Blocked Governor Operation | Operating the generating unit with the control system adjusted to prevent the turbine governor from responding to system frequency (speed) variations. In an effort to reduce speed governor operation in some generating units, turbine control systems can be adjusted to block the operation of the governor after the unit is in parallel with the system and is running at its desired output. Selection of a high percent droop characteristic or a large dead band constitutes a form of blocked governor action. |
| Variable Pressure Operation | Varying the boiler pressure to improve turbine efficiency at lower loads. Two methods are normally used. With one method, the turbine governor (G.E.) or control (Westinghouse) valves are positioned in the wide-open position and the generator is changed by changing the boiler pressure. With this method, there is very little, if any response to frequency excursions. With the other method, the valves are positioned at approximately 50% open. The valves are still able to respond to system disturbances. Normal changes in generation requirements are made by varying the boiler pressure until the unit is at rated pressure. After full pressure is reached, the turbine valves are used to make the required generation changes. |

6.2.1.5		Combustion Turbine Frequency Response Test Procedure

Description of the test

- The frequency response function of the combustion turbine is tested On-line at a Load level that allows combustion turbine to increase or decrease Load without reaching Low or High Operating Limits.  The recommended level is 92% Base Load or below.

- The test is performed by adding a frequency offset signal that exceeds the governor dead band value to the measured frequency signal. This should create immediate step change in the measured frequency signal.

- The test starts at time t0 when the frequency dead-band is exceeded and signal ”Combustion Turbine Frequency Response On” becomes active.

- The following signals should be recorded at least every two (2) seconds: Unit MW Output, ”Combustion Turbine Frequency Response On”.

- The duration of the test is one-hundred (100) seconds. After one-hundred (100) seconds, the offset signal should be removed and combustion turbine should return to pretest power output.

- The test should be conducted both with positive and negative frequency offsets.

- The test is considered successful after the signal “Combustion Turbine Frequency Response On” becomes active and maintained for thirty (30) seconds if 70% of the calculated MW contribution is delivered within sixteen (16) seconds.

- Droop shall be set not to exceed 5% with a maximum frequency dead-band of +/- 0.036Hz.

Definitions

Combustion Turbine Base Load = maximum load capability for the season when frequency response test is performed

Gain MW for 0.1Hz = P∗10Droop∗60

, where 	P = Combustion Turbine Base Load (MW)

Droop 	= droop (%)

Frequency Offset = +0.2Hz and -0.2Hz (+12 rpm and -12 rpm, for 3600 sync speed machines)

Test frequency = Measured Frequency + Frequency Offset

MW Contribution = Gain MW to 0.1Hz * 10*Frequency Offset

Calculated droop = - P∗ΔHz60∗ΔMW

, where 	P = Combustion Turbine Base Load (MW)

ΔHz = Change in frequency (Hz)

ΔMW = Change in power output (MW)

Example

Combustion Turbine Base Load = 150MW

Droop = 5%

Gain MW to 0.1Hz = 150∗105∗60 = +/- 5 MW/0.1Hz

MW Contribution = 5 * 10*+/-0.2 = +/-10MW

Expected under-frequency response:	 +10MW in 15 sec. for -0.2Hz offset

Expected over-frequency response: 	-10MW in 15 sec. for +0.2Hz offset

Minimum accepted under-frequency response: +7MW in 15 sec. for -0.2Hz offset

Minimum accepted over-frequency response:    -7MW in 15 sec. for +0.2Hz offset

Calculated droop for 8MW increase in power output in 15 sec. for -0.2Hz offset:

Calculated droop = -150∗−0.260∗8 = 0.0625 or 6.25%

COMBUSTION TURBINE FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 characters): 				Location (County):

Unit Name: 						Date of Test:

QSE: 							Resource Entity:

Test Results

|  |  | Test with +0.2 Hz | Test with -0.2 Hz |
| --- | --- | --- | --- |
| 1 | CT Base load |  |  |
| 2 | GAIN MW to 0.1Hz |  |  |
| 3 | Calculated MW Contribution |  |  |
| 4 | MW at test start (t0) |  |  |
| 5 | MW at t0 + 16 sec |  |  |
| 6 | MW Contribution at t0 + 16 sec |  |  |
| 7 | MW at t0 + 46 sec |  |  |
| 8 | Calculated droop |  |  |
| 9 | CONCLUSION (PASSED/FAILED) |  |  |

Comments: ______________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  ____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep.: __________________________

6.2.1.6	  Combustion Turbine Frequency Response Procedures Based on Historical Data

Description of historical verification

The purpose of this template is to allow the QSE to demonstrate acceptable frequency response of their combustion turbines based on historical data in order to minimize testing costs, scheduling conflicts and the risk of damage to equipment or Forced Outage.

1.  All verifications will be based on at least one of the Performance, Disturbance, Compliance Working Group’s (PDCWG) list of “Measurable Events” as defined in the ERCOT Protocols.  Different turbines can be tested using different events.

2.  For clarification purposes, the A, B, B+30 and C points are defined in Protocol Section 5.9.2, Primary Frequency Control Measurements. Point A will be considered the start of the verification process.  The exact time of each Point is identified in the PDCWG Disturbance Report on the event.

3.  The following signals should be recorded at EMS scan rate: Unit MW Output and ERCOT Actual Frequency from the PDCWG Disturbance Report on the event.

4. The verification is considered successful if 70% of the calculated MW contribution is delivered within 16 seconds after the C point and maintained for 30 seconds.

5.  Droop should be set not to exceed 5% and a maximum frequency deadband of +/- 0.036Hz.

6.  ERCOT Operations will supply frequency data and time of each evaluation point (A, C, B & B+30) for the event data chosen for the test.

Definitions

Combustion Turbine Base Load = maximum load capability for the season when frequency response test is performed

Gain MW for 0.1Hz = P∗10Droop∗60

, where 	P = Combustion Turbine Base Load (MW)

Droop 	= droop (%)

Calculated droop = - P∗ΔHzC,B,B+3060∗ΔMWC,B,B+30

, where 	P = Combustion Turbine Base Load (MW)

ΔHz = Change in frequency (Hz) between Point A and

Point C, B or B+30

ΔMW = Change in power output (MW) between Point A

and Point C, B or B+30

Adjusted droop = - P∗ΔHzC,B,B+3060∗(ΔMWC,B,B+30+OCC,B,B+30)

, where 	OC = Obligation Change

Obligation Change = ∆ MW Schedule from Point A to Point B + 30 if negative in an under-frequency event or if positive in an over-frequency event, else 0.

Example

CT Base Load = 150MW

Droop = 5%

Gain MW to 0.1Hz = 150∗105∗60 = +/-5 MW/0.1Hz

Expected under-frequency response:	 +5MW in 15 sec. for -0.1Hz offset

Expected over-frequency response: 	-5MW in 15 sec. for +0.1Hz offset

Minimum accepted under-frequency response: +3.5MW in 15 sec. for -0.1Hz offset

Minimum accepted over-frequency response:    -3.5MW in 15 sec. for +0.1Hz offset

Calculated droop for 5 MW increase in power output in 15 sec. for -0.1Hz offset:                  Calculated droop = -150∗−0.160∗5 = 0.05 or 5.00%

Schedule drop of 10 MW from point A to B + 30 with 10 frequency responsive units:

OC = 10/10 = 1 MW

Adjusted droop = -150∗−0.160∗(5+1) = 0.0416 or 4.16%

Reference:  Protocol Section 5.9.2, Primary Frequency Control Measurements

For the purposes of this section, the A Point is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this section, the C Point is the lowest frequency value during the first five seconds of the event.

For the purposes of this section, the B Point is the “recovery” frequency value after the C Point.   The B Point should occur after full governor response of the turbines has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty Seconds: At thirty seconds following the B Point, an analysis will be performed by ERCOT with the assistance of the appropriate ERCOT subcommittee to determine if primary frequency control response is sustained.

For the purposes of this section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

HISTORICAL COMBUSTION TURBINE FREQUENCY RESPONSE TEST FORM

General Information

Unit Code (16 character): 				Location (County):

Unit Name: 						Date of Event:

QSE: 							Resource Entity:

Historical Results

| Evaluation Point | Time | Frequency |
| --- | --- | --- |
| Point A |  |  |
| Point C |  |  |
| Point B |  |  |
| Point B+30 |  |  |

| 2 | CT Base load |  |
| --- | --- | --- |
| 3 | MW at A Point |  |
| 4 | MW at B Point |  |
| 5 | MW at B + 30 Point |  |
| 6 | MW at C Point |  |
| 7 | Calculated Droop at B Point |  |
| 8 8A | Compensation for Obligation Change: Number of Freq. Resp. Units |  |
| 8B | Schedule ∆ from Point A to Point B + 30 |  |
| 8C | Schedule ∆ for Observed Unit (8B/8A) |  |
| 9 | Adjusted droop at B + 30 |  |
| 10 | (PASSED/FAILED) Pass if #7 & #9 < 7.14%, else Fail |  |

Comments: ______________________________________________________________________________________________________________________________________________________________________________________________________________

Submittal

Resource Entity Representative:  _____________________________________________

QSE Representative:  ______________________________________________________

Date submitted to ERCOT Control Area Authority Rep:

### 6.2.2	Seasonal Unit Net Real Power Capability Verification

General Information

Unit Code (16 character):   			Location (County):

Unit Name:  					Date of test:

Generator’s QSE:  				Resource Entity:

Test Results

Start Time:  		Start MW:

MW 10 Minutes after Start Time:  		Time to Reach Maximum Generation:

Temperature at Plant (F):  			MW at Maximum Generation:

MWH Net during the First Full Clock Hour after Maximum Generation is reached:

Limiting Factors:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

### 6.2.3	Biennial Unit Reactive Limits (Lead and Lag) Verification

General Information

Unit Code :  *			Location (County):  *

Unit Name:  *					Date of test:  *

Generator’s QSE:  *				Resource Entity:  *

Test Details

Instructions:

Maximum lagging reactive tests should be performed with the unit at or above 95% of the current dependable MW capability.  Leading reactive tests may be performed during light Load conditions of the ERCOT System or at a normal operating real output (MW) that leading reactive capability can be measured and tested within the limits established by the Corrected Unit Reactive Limit (CURL) curve.  This form is to be submitted by the QSE to ERCOT with a copy of the generator reactive capability design curve or the CURL curve as described in Section 3.1.4.3, Unit Reactive Capability Testing, marking the measured maximum output capability.  This measured capability must be equal to or greater than 90% of the established CURL on the submitted generator reactive capability design curve or the CURL curve.  Inability to reach the value described above must be noted with an explanation of the limiting factor, which prevented design capability or CURL capability performance.  The inability to reach the measurement criteria may be cause for ERCOT 1) to require the Resource Entity to retest the generator’s performance for a lagging test only or 2) to require the Resource Entity to produce a CURL curve that reflects current operating limits.  The Resource Entity shall verify that the Automatic Voltage Regulator is in service.  The minimum acceptable test duration is 15 minutes.  During a Coordinated Test, as described in Section 3.1.4.3 of these Operating Guides, the normally specified switchyard voltage should be maintained by adjusting voltage control devices/units in so far as possible.  Show leading reactive value as a negative (-) number.

* This entry is required for all tests

*CORRECTED UNIT REACTIVE LIMIT (CURL) CURVE: (1)

Maximum Lagging Reactive at current Gross Dependable MW Output			 MVAR(Gross) at 	 MW(Gross) (1)

Maximum Lagging Reactive at current Gross Low Sustained Limit MW Output		 MVAR(Gross) at 	 MW(Gross) (1)

Maximum Leading Reactive at current Gross Dependable MW Output			 MVAR(Gross) at 	 MW (Gross) (1)

Maximum Leading Reactive at current Gross Low Sustained Limit MW Output	_______ MVAR(Gross) at 	 MW(Gross) (1)

* Defined Test:

 Coordinated Test

 Non-Coordinated Test

*Test Performed:			*Location at which data observed (specify all that apply):

 Maximum Leading Reactive		 Generator Terminals (preferred)

 Maximum Lagging Reactive		 High Voltage side of Generator Step-Up (GSU) Transformer

 Other (specify location):

TESTED REACTIVE CAPABILITY

*Generator Gross Reactive (MVAR): (+/-) _____ (2)

*Auxiliary Reactive Load (MVAR): _____ (3)	 Observed     Calculated

*Net Reactive to the Transmission System (MVAR): (+/-) _____ (5)   Observed     Calculated

*Net Generator Reactive (MVAR): _______ (6)   Observed     Calculated

TEST CONDITIONS:

*Start Time: ________________	*Stop Time: ______________

*Generator Gross Generation (MW): _____ (7)

*Net Dependable Unit Generation (MW): _____ (8)

*Auxiliary Load (MW): _____ (4)		*Generator Terminal Power Factor: _____

*Transmission Bus Voltage (kV): _____ (9)	*Nominal Transmission Bus Voltage (kV): _____

*Generator Terminal Voltage (kV): _____	Auxiliary Bus Voltage (kV): _____ (10)

Ambient Air Temperature (°F): _____ (10)

*Generator Hydrogen Pressure, if applicable (psig): _____ (11)

*Generator Step Up transformer tap setting: _____Ratio: HV _____kV/ LV ______kV (12)

*Abnormal Conditions at Time of Test: (13)

*Briefly describe factors that limited reactive capability during test:

 Maximum Generator Voltage with Auxiliary loads		 Steady State Stability Limit

 Maximum Generator Voltage without Auxiliary loads	 Maximum Gross MW capability

 Minimum Generator Voltage with Auxiliary loads		 Minimum Gross MW capability

 Minimum Generator Voltage without Auxiliary loads	 Minimum Excitation Limiter

 Main transformer capability plus Auxiliary loads		 Loss of Field Relay

 Other:

Submittal

*Resource Entity Representative:

*QSE Representative:

*QSE/Resource Entity Contact Phone Number: 			Email Address:

*Date submitted to ERCOT Control Area Authority Rep.:

Notes:	Maximum Leading and Maximum Lagging tests may be conducted at different times of the year.

Metered Auxiliary

Load

Generator Terminal

(Gross)

MVAR    (2)

MW        (7)

(5)  Location Where Net Reactive to the

Transmission System is to be determined.

Generator Step Up Transformer

(6)  Location Where Net Generator Reactive is to be determined.

MVAR   (3)

MW       (4)

Load Host

Consumption

Low Side (14)

Transmission Bus

(10) Auxiliary

Bus Voltage

G

W

W

W

(9)  Transmission Bus Voltage

Load Host

Consumption

High Side (14)

NOTES

(1)	These quantities are taken directly from the Corrected Machine Capability Curve. The MVAR reactive maximum lagging value is the expected output at the generator terminal (gross output) with the generating unit at the Gross Dependable MW Output. This is the Gross equivalent of the Net Dependable Output. The MVAR reactive maximum leading value is the expected output at the generator terminal (gross output) with the generating unit at the Gross Low Sustained Limit MW output. This is the Gross equivalent of the Net Low Sustained Limit.  The Maximum Lagging Reactive at current Gross Low Sustained Limit and Maximum Leading Reactive at current Gross Low Sustained Limit are used for curve validation only.

(2)	Metered reactive at the generator’s terminals,

(3)	Auxiliary Reactive Load (Load only associated with Generator such as fans, boiler pumps etc.),

(4)	Metered Auxiliary Real Load (Load only associated with Generator),

(5)	Observed – metered reactive on the high side of the generator step up transformer to the transmission system,
Calculated - (+/-) metered reactive at the generator’s terminals minus metered Auxiliary Reactive consumption minus generator step up transformer reactive losses minus Load host reactive consumption (Load host does not apply to most generators but only pertains to generators with self serve load),

(6)	Observed - (+/-) as metered, Gross generator reactive minus metered Auxiliary Reactive consumption,
Calculated - (+/-) metered net reactive to the transmission system minus generator step up transformer reactive losses minus Load host reactive consumption (Load host does not apply to most generators but only pertains to generators with self serve load),

(7)	Metered at the generator terminals,

(8)	Most current tested value on record at ERCOT,

(9)	Required for Coordinated Test,

(10)	(if limiting),

(11)	PSIG can be determined from PSIA by subtracting 14.7 from the PSIA gauge reading

(12)	Actual tap setting – not nominal tap setting,

(13)	Describe fully.

(14)	Load Host consumption exists on either the low side or the high side of the step up transformer but typically not both.

### 6.2.4	Seasonal Hydro Responsive Reserve Net Capability Verification

General Information

Unit Code (16 character):   			Location (County):

Unit Name:  					Date of test:

Generator’s QSE:  				Resource Entity:

Test Details

Start Time

Start MW 			MW at 4 seconds 			MW at 10 seconds

Max MW

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.:

### 6.2.5	Annual LaaR Telemetry Test

General Information

Date:					Location (County):

ERCOT Asset Code:			LaaR’s QSE:

Load Resource Name:			Load Point Name:

(multiple points only)

Instructions

As specified in Protocol Section 6.10.2, General Capacity Testing Requirements, a Load acting as a Resource that is providing Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  This annual verification is performed between the Load acting as a Resource and the QSE representing the Resource.  The Telemetry Test Results should reflect the actual status of each of the telemetered points being submitted to ERCOT during a specified interval.  If the LaaR consists of more than one Load point with multiple breakers and/or under frequency relays (the latter applicable to LaaRs providing Responsive Reserve Service), please submit one form per Load point.  ERCOT will perform a comparison of the data provided on this form to the actual telemetered values received by ERCOT.  Any significant variances will be reported back to the QSE to investigate and correct.  ERCOT will send the QSE a copy of each validated test form.

Telemetry Test Results

Start Time Interval:

LaaR Breaker Status:		Response MW:

UFR Status*:			MW at Maximum Load**:

Note:	*	Only applicable to LaaRs providing Responsive Reserve Service

**	Maximum available capacity for each LaaR will be capped to the Maximum Load test level

By signature below, the LaaR Representative certifies that the telemetry and high set under frequency relays, where applicable, are in place and fully functional.

Submittal

LaaR Representative Name:			Signature:

QSE Representative:				Date submitted to ERCOT:

ERCOT Validation By:			Date:

### 6.2.6	Biennial Test for LaaRs Providing Responsive Reserve Service

General Information

Date:						Location (County):

ERCOT Asset Code:				LaaR’s QSE:

Load Resource Name:				Load Point Name:

(multiple points only)

Instructions

As specified in Protocol Section 6.10.2, General Capacity Testing Requirements, a Load acting as a Resource providing Responsive Reserve Service shall test each under frequency relay or solid state controller, whichever applies, for correct operation.  A separate certified relay test results sheet is to be attached for each relay tested.  Please provide sufficient notation on each test sheet to assist ERCOT in matching up the sheet to individual relays.  This test of the under frequency relay does not require the Load to be interrupted.  If, within the biennial testing period, the Load’s performance has been verified through the correct response to an actual event, the data from that event can be supplied to meet this requirement and the required annual telemetry test.  The date, interval, and other information associated with the event are to be noted below.  ERCOT will return a copy of the validated test form to the QSE.

Verification of telemtered Response to an Actual Event

Date of event:					Interval of event:

LaaR Breaker Status :				MW Load Prior to Event:

UFR Status:		Instantaneous Response MW:		Frequency deviation Hz:

Time Load restored:		ERCOT Operator:

Submittal

By signature below the LaaR representative certifies the high set under frequency relay(s) are in place and fully functional.

LaaR Representative Name:				Signature:

Name of Company Performing Relay Test:

QSE Representative:				Date submitted to ERCOT:

ERCOT Validation By:				Date:

Note: Please attach certified relay test results sheet(s) to this form when submitting to ERCOT

### 6.2.7	Unit Alternative Fuel Capability

MARKET PARTICIPANT - PROTECTED INFORMATION

THIS INFORMATION IS PROTECTED INFORMATION PURSUANT TO SECTION 1.3.1.1(24) OF THE ERCOT
 PROTOCOLS AND CONTAINS CONFIDENTIAL/PROPRIETARY INFORMATION OF THE MARKET PARTICIPANT.

THIS INFORMATION MUST BE KEPT STRICTLY CONFIDENTIAL AND IS PROVIDED TO ERCOT EMPLOYEES
ONLY ON A"NEED TO KNOW" BASIS AND WILL NOT BE SHARED WITH ANYONE OUTSIDE ERCOT.

| General Information |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Unit Code | Primary Fuel1 | Alternative Fuel1 | Alt Source - Pipeline, Truck, etc… | Date of Last MW Curtailmenton Primary Fuel | MW Curtailed | Reason for Curtailment/Comments |

1Indicate one of the following Fuel Types:

BITUMINOUS COAL	Butane	Coal Processes	Coke-even coal	Diesel	JET FUEL

LANDFILL GAS	LIGNITE	Methanol	NATURAL GAS	No 1 Fuel Oil	No 2 Fuel Oil

No 4 Fuel Oil	No 5 FUEL OIL	No 6 Fuel Oil	NUCLEAR	PETROLEUM COKE	PROPANE

PURCHASED STEAM WATER-Conventional	PURCHASED STEAM WATER-Pumped Storage	Refinery gas	SUB-BITUMINOUS COAL

WIND

6.2.7	Unit Alternative Fuel Capability

MARKET PARTICIPANT - PROTECTED INFORMATION

THIS INFORMATION IS PROTECTED INFORMATION PURSUANT TO SECTION 1.3.1.1(24) OF THE ERCOT
 PROTOCOLS AND CONTAINS CONFIDENTIAL/PROPRIETARY INFORMATION OF THE MARKET PARTICIPANT.

THIS INFORMATION MUST BE KEPT STRICTLY CONFIDENTIAL AND IS PROVIDED TO ERCOT EMPLOYEES
ONLY ON A"NEED TO KNOW" BASIS AND WILL NOT BE SHARED WITH ANYONE OUTSIDE ERCOT.

| Alternative Fuel |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Unit Code | Capable of using 100% Alternative Fuel – (Yes/No) | Maximum % Alternative Blend | No. Hours to Transition to Alternative Fuel | No. Hours @ HSL using Alternative Fuel | Comments |

6.2.7	Unit Alternative Fuel Capability

MARKET PARTICIPANT - PROTECTED INFORMATION

THIS INFORMATION IS PROTECTED INFORMATION PURSUANT TO SECTION 1.3.1.1(24) OF THE ERCOT
 PROTOCOLS AND CONTAINS CONFIDENTIAL/PROPRIETARY INFORMATION OF THE MARKET PARTICIPANT.

THIS INFORMATION MUST BE KEPT STRICTLY CONFIDENTIAL AND IS PROVIDED TO ERCOT EMPLOYEES
ONLY ON A"NEED TO KNOW" BASIS AND WILL NOT BE SHARED WITH ANYONE OUTSIDE ERCOT.

| Natural Gas Fuel |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Column 1 | Column 2 | Column 3 | Column 4 | Column 5 | Column 6 | Col 7 | Col 8 | Column 9 |
| Unit Code | Planned Average MWh/day (firm+ nonfirm gas) | Average MWh/day firm gas only | Maximum MW instantaneous firm + non-firm gas | Maximum MW instantaneous firm gas only | Date Range - (e.g. Nov. 07 - 14) | Delivery (Excluding Force Majeure) |  | Comments |
|  |  |  |  |  |  | Firm% | Non Firm% |  |

Note:  See example on the following page.

In column 2 enter the sum of MWh projected to run over the day, divided by 24

In column 3, enter the sum of MWh projected to run over the day supported by FIRM GAS only, divided by 24

In column 4, enter the maximum MW projected to run instantaneously

In column 5, enter the maximum MW projected to run instantaneously that can be supported by FIRM gas and firm delivery

In column 6, enter the date range this data covers.  If it changes, provide multiple date range entries for each unique occurrence.

In column 7, enter the column 3 entry divided by the column 2 entry.

In column 8, enter the column 2 entry, minus the column 3 entry, divided by the column 2 entry (2-3)/2

6.2.7	Unit Alternative Fuel Capability

MARKET PARTICIPANT - PROTECTED INFORMATION

THIS INFORMATION IS PROTECTED INFORMATION PURSUANT TO SECTION 1.3.1.1(24) OF THE ERCOT
 PROTOCOLS AND CONTAINS CONFIDENTIAL/PROPRIETARY INFORMATION OF THE MARKET PARTICIPANT.

THIS INFORMATION MUST BE KEPT STRICTLY CONFIDENTIAL AND IS PROVIDED TO ERCOT EMPLOYEES
ONLY ON A"NEED TO KNOW" BASIS AND WILL NOT BE SHARED WITH ANYONE OUTSIDE ERCOT.

| Natural Gas Fuel |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Column 1 | Column 2 | Column 3 | Column 4 | Column 5 | Column 6 | Col 7 | Col 8 | Column 9 |
| Unit Code | Planned Average MWh/day (firm+ nonfirm gas) | Average MWh/day firm gas only | Maximum MW instantaneous firm + non-firm gas | Maximum MW instantaneous firm gas only | Date Range - (e.g. Nov. 07 - 14) | Delivery (Excluding Force Majeure) |  | Comments |
|  |  |  |  |  |  | Firm% | Non Firm% |  |
| Unit A | 2 | 0 | 100 | 0 | December 7-9 | 0% | 100% |  |
| Unit B | 290 | 0 | 600 | 0 | December 7-9 |  | 100% |  |
| Unit C | 0 | 0 | 0 | 0 | December 7-9 | 0 | 0 | Available but not planned on |
| Unit D | 79 | 40 | 650 | 100 | December 7-9 | 51% | 49% |  |
| Unit E |  |  |  |  | December 7-9 |  |  | Forced off until December 15 |
| Unit F | 33 | 33 | 190 | 0 | December 7-9 | 100% | 0% |  |
| Unit G | 0 | 0 | 0 | 0 | December 7-9 |  |  |  |

Note:  The form is filled out with examples to help clarify.

In column 2 enter the sum of MWh projected to run over the day, divided by 24

In column 3, enter the sum of MWh projected to run over the day supported by FIRM GAS only, divided by 24

In column 4, enter the maximum MW projected to run instantaneously

In column 5, enter the maximum MW projected to run instantaneously that can be supported by FIRM gas and firm delivery

In column 6, enter the date range this data covers.  If it changes, provide multiple date range entries for each unique occurrence.

In column 7, enter the column 3 entry divided by the column 2 entry.

In column 8, enter the column 2 entry, minus the column 3 entry, divided by the column 2 entry (2-3)/2

## 6.3	Document Control

Authorities

| Prepared by: | Date Completed: | Reviewed by: | Date Authorized: |
| --- | --- | --- | --- |
| E. Irwin, Technical Writer | 12/29/2000 | B. Garza, Chair Joint Operating Guides WG | December 29, 2000 |
| I. Flores | 4/17/2002 | OGRTF/ROS |  |
| I. Flores | 8/15/2002 | OGRTF/ROS | July 11, 2002 |
| I. Flores | 12/01/2002 | OGRTF | October 24, 2002 |

Distribution List

| Name | Organization |
| --- | --- |
| Operating Guide Revision Task Force (OGRTF) | Reliability Operations Subcommittee |
| Operations | ERCOT |
| Technical Advisory Committee | ERCOT |
| Reliability Operations Subcommittee | Technical Advisory Committee |

Change History

| Issue/Draft | Reason for issue | Date |
| --- | --- | --- |
| Version 0.1 | Draft for Review | December 29, 2000 |
| Version 0.2 | Not Issued |  |
| Version 0.3 | Include comments from seminar | January 19, 2001 |
| Version 0.4 | Include comments from second seminar | February 5, 2001 |
| Version 1.0 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee | February 28, 2001 |
| May 1, 2002 | OGRR106 | May 1, 2002 |
| September 1, 2002 | OGRR109; Subsection A.1.2. | September 1, 2002 |
| December 1, 2002 | Reformat section numbering from Appendix A to Section 6. | December 1, 2002 |
| November 1, 2003 | Deleted redundant signature lines from 6.2.3 | November 1, 2003 |
| May 1, 2004 | OGRR146 deleted Section 6.1.3 and added Sections 6.2.6 and 6.2.7 | May 1, 2004 |
| December 1, 2004 | OGRR153 | December 1, 2004 |
| February 1, 2005 | OGRR157 | February 1, 2005 |
| June 1, 2006 | OGRR169, OGRR178 | June 1, 2006 |
| May 1, 2008 | Admin OGRR207 | May 1, 2008 |
| October 1, 2009 | OGRR217 | October 1, 2009 |

Westinghouse recommends using only this test.

Westinghouse recommends using only this test.