## Instructions
ERCOT Confidential
GO TO MAP | RARF V4.01
ERCOT Nodal Resource Asset Registration Form (RARF)
"Network Model / System Planning / Data Aggregation / Settlements - Asset Registration / Resource Data Form"
A RARF should be submitted for each Generation Resource site that contains all generation at the site.
A RARF should be submitted for each Resource Entity covering all Load Resources represented by that entity.
The data form has been provided for ERCOT Resource Entities to properly register and submit data needed to register the assets
of Generation Resources and Load Resources. The form is to also be completed for all active and mothballed generation resources inside ERCOT.
Your organization must have submitted a market participant application as a Resource Entity prior to submission of this form.
If questions arise related to the completion of this form, please contact your designated ERCOT Account Manager or
email Wholesale Client Services at ClientRelations@ercot.com with the subject "Asset Registration / Resource Data Form".
Please keep in mind the following as you complete this form:
1. Please submit a single form for each 'Resource Site'. This form will accommodate Generation Resources located at a common site or
Load Resources represented by a common Resource Entity. Also, this form will accommodate generation load splitting.
2. After completion of this form, please submit electronically attached to a SERVICE REQUEST through TEXAS MARKET LINK (TML).
See explanation below for submitting form through TML. See the MP User Security Administrator to obtain a digital certificate.
INSTRUCTIONS FOR SUBMITTING RARF THROUGH TEXAS MARKET LINK:
1. ERCOT requests the Resource Entity attach the RARF to a Service Request through Texas Market Link by the Primary or Secondary
Authorized Representative of the Resource Entity.
2. Access to ERCOT TML requires a user digital certificate with minimal role that allows access to "Create Service Request" on the
"Market Activities" page. The "user digital certificate" is authorized by the Market Participant's User Security Administrator.
3. Upon accessing TML go to the "Market Activities" page and select "Create Service Request". Be advised that the Service Request
will display in a new window as a pop-up, which may be impacted by user's browser settings.
4. Complete the required fields on the "Service Request" screen (annotated by red asterisk).
The following Request Type and Sub-Type are essential to proper submittal.
Request Type: Select "MP Registration" from the drop-down list
Request Sub-Type: Select "Resource/Asset Registration" from the drop-down list
Short Description: Complete with a descriptive subject
Long Description: Complete with additional details if needed
Click "Submit" (you will add the RARF file on the next screen)
From the "Activities and Attachments" screen
Click "Add" under the Attachments heading of the Service Request
Select "Browse" icon and find the completed RARF file on your computer
Click "Submit" (comments are optional)

## Spreadsheet Map
ERCOT Confidential
Map of the ERCOT Nodal Resource Asset Registration Form
This worksheet tab identifies the necessary worksheets and provides links to the pages.
List of applicable worksheet tabs by Resource Type: Wind Generation Resources (WIND) Non-Wind, Non-CC Generation Resources (GEN) Combined Cycle Generation Resources (CC) Load Resources (LR)
WIND | RARF Guide / Protocol Reference | % Complete |  |  | Worksheets included in this form:
Instructions | RARF Guide: Section 3.0 |  |  |  | Instructions
Map (this page) | RARF Guide: Section 3.0 |  |  |  | Spreadsheet Map (this page)
General Information - ALL | RARF Guide: Section 4.0 |  |  |  | General Information
Site Information - GEN CC WIND | RARF Guide: Section 4.0 | #REF! |  |  | Site Information
Unit Info - WIND | RARF Guide: Section 5.3 | #REF! |  |  | Unit Information
Resource Parameters - WIND | RARF Guide: Section 6.3 | #REF! |  |  | Resource Parameters
Operational Resource Parameters - WIND | RARF Guide: Section 7.3 Nodal Protocols 3.7.1 | #REF! |  |  | Operational Resource Parameters
Reactive Capability - WIND | RARF Guide: Section 8.3 | #REF! |  |  | Reactive Capability
GSU Transformer - ALL | RARF Guide: Section 9.1 | #REF! |  |  | GSU Transformer
Ownership - WIND | RARF Guide: Section 10.3 |  |  |  | Ownership
Planning - WIND | RARF Guide: Section 12.1 | #REF! |  |  | Planning
Protection - WIND | RARF Guide: Section 12.3 | #REF! |  |  | Planning
Generation Owned Transmission Assets - ALL | RARF Guide: Section 14.0 |  |  |  | Generation Owned Transmission Assets
GEN
Instructions | RARF Guide: Section 3.0 |  |  |  | Instructions
Map (this page) | RARF Guide: Section 3.0 |  |  |  | Spreadsheet Map (this page)
General Information - ALL | RARF Guide: Section 4.0 |  |  |  | General Information
Site Information - GEN CC WIND | RARF Guide: Section 4.0 | #REF! |  |  | Site Information
Unit Info - GEN | RARF Guide: Section 5.1 | #REF! |  |  | Unit Information
Resource Parameters - GEN | RARF Guide: Section 6.1 | #REF! |  |  | Resource Parameters
Operational Resource Parameters - GEN | RARF Guide: Section 7.1 Nodal Protocols 3.7.1 | #REF! |  |  | Operational Resource Parameters
Reactive Capability - GEN | RARF Guide: Section 8.1 | #REF! |  |  | Reactive Capability
GSU Transformer - ALL | RARF Guide: Section 9.1 | #REF! |  |  | GSU Transformer
Ownership - GEN | RARF Guide: Section 10.1 |  |  |  | Ownership
Planning - GEN | RARF Guide: Section 12.1 | #REF! |  |  | Planning
Protection - GEN | RARF Guide: Section 12.2 | #REF! |  |  | Planning
Subsynchronous Resonance - GEN | RARF Guide: Section 12.3 |  |  |  | Planning
Private Network - PUN | RARF Guide: Section 13.0 |  |  |  | Private Use Network
Generation Owned Transmission Assets - ALL | RARF Guide: Section 14.0 |  |  |  | Generation Owned Transmission Assets
COMBINED CYCLE
Instructions | RARF Guide: Section 3.0 |  |  |  | Instructions
Map (this page) | RARF Guide: Section 3.0 |  |  |  | Spreadsheet Map (this page)
General Information - ALL | RARF Guide: Section 4.0 |  |  |  | General Information
Site Information - GEN CC WIND | RARF Guide: Section 4.0 | #REF! |  |  | Site Information
Unit Info - CC | RARF Guide: Section 5.2 | #REF! | #REF! | #REF! | Unit Information
Resource Parameters - CC | RARF Guide: Section 6.2 | #REF! | #REF! | #REF! | Resource Parameters
Resource Parameters - CC CFG (ensure configs are entered) | RARF Guide: Section 6.2 | #REF! | #REF! | #REF! | Resource Parameters
Operational Resource Parameters - CC CFG (ensure configs are entered) | RARF Guide: Section 7.2 Nodal Protocols 3.7.1 | #REF! | #REF! | #REF! | Operational Resource Parameters
Reactive Capability - CC | RARF Guide: Section 8.2 | #REF! | #REF! | #REF! | Reactive Capability
GSU Transformer - ALL | RARF Guide: Section 9.1 | #REF! |  |  | GSU Transformer
Ownership - CC | RARF Guide: Section 10.2 |  |  |  | Ownership
Configurations - CC1 | RARF Guide: Section 11.2 |  |  |  | Combined Cycle Configuration Details
Configurations - CC2 | RARF Guide: Section 11.2 |  |  |  | Combined Cycle Configuration Details
Configurations - CC3 | RARF Guide: Section 11.2 |  |  |  | Combined Cycle Configuration Details
Transitions - CC1 | RARF Guide: Section 11.3 |  |  |  | Combined Cycle Configuration Details
Transitions - CC2 | RARF Guide: Section 11.3 |  |  |  | Combined Cycle Configuration Details
Transitions - CC3 | RARF Guide: Section 11.3 |  |  |  | Combined Cycle Configuration Details
Planning - CC | RARF Guide: Section 12.1 | #REF! | #REF! | #REF! | Planning
Protection - CC | RARF Guide: Section 12.2 | #REF! | #REF! | #REF! | Planning
Subsynchronous Resonance - CC | RARF Guide: Section 12.3 |  |  |  | Planning
Private Network - PUN | RARF Guide: Section 13.0 |  |  |  | Private Use Network
Generation Owned Transmission Assets - ALL | RARF Guide: Section 14.0 |  |  |  | Generation Owned Transmission Assets

## General Information - All
ERCOT Confidential
General Information - All Resource Entities
This worksheet tab contains information on the Resource Entity responsible for submitting this form.
Please complete this section and select RETURN TO MAP
This submittal is for: | Table: | DB Field: | Rules: | Source | APPLICATIONS
Submittal Information
Date Form Completed: | SITECODE | FORM_COMP_DT | Optional | RARF Glossary | HUB
Resource Entity Submitting Form: | RE_RARF | RE_NAME | 1. Not null. 2. Name must match ERCOT records (SIEBEL) | RARF Glossary | EMS, MMS, NMMS, PLANNING
Resource Entity DUNS #: | SITECODE | RE_DUNS | 1. Not null. 2. DUNS number must match ERCOT records (SIEBEL) | RARF Glossary | EMS, MMS, NMMS, PLANNING
HUB
Resource Entity Authorized Representative (as registered with ERCOT) - NOT NEEDED |  |  |  |  | HUB
Signature: |  |  |  |  | HUB
Printed Name: |  |  |  |  | HUB
Title: |  |  |  |  | HUB
Phone Number: |  |  |  |  | HUB
E-mail Address: |  |  |  |  | HUB
Fax Number: |  |  |  |  | HUB
Primary Contact |  |  |  |  | HUB
Printed Name: | SITECODE | NAME_PC | Not null | RARF Glossary | HUB
Title: | SITECODE | TITLE_PC | Not null | RARF Glossary | HUB
Phone Number: | SITECODE | PHONE_PC | Not null | RARF Glossary | HUB
E-mail Address: | SITECODE | EMAIL_PC | Not null | RARF Glossary | HUB
Fax Number: | SITECODE | FAX_PC | Optional | RARF Glossary | HUB
Secondary Contact
Printed Name: | Not in table |  | Optional
Title: | Not in table |  | Optional
Phone Number: | Not in table |  | Optional
E-mail Address: | Not in table |  | Optional
Fax Number: | Not in table |  | Optional

## Site Information - All GEN RES
ERCOT Confidential
Site Information
This worksheet tab contains site-specific information.
Please complete this section and select RETURN TO MAP
All Generation Resources
| Site Info for Generation Resources | Table: | DB Field: | Rules: | Source | APPLICATIONS
| Resource Site Name: | SITECODE | SITE_NAME | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | RARF Glossary | EMS, SETTLEMENTS
| Resource Site Code: | SITECODE | SITE_CODE | 1. Not null. 2. Validate with ERCOT records (Lodestar). 3. All should be capital letters | RARF Glossary | ALL
| Street Address: | SITECODE | STREET_ADDRESS | Not null | RARF Glossary | SETTLEMENTS
| City: | SITECODE | CITY | Not null | RARF Glossary | SETTLEMENTS
| State: | SITECODE | STATE | Not null | RARF Glossary | SETTLEMENTS
| Zip: | SITECODE | ZIPCODE | Not null | RARF Glossary | SETTLEMENTS
| County: | SITECODE | COUNTY | Not null | RARF Glossary | SETTLEMENTS
| Site In-Service Date: | SITECODE | SITE_IN_SRVC_DT | 1. Must be earlier than Site-Stop Service Date. 2. mm/dd/yy format. 3. Not null. | SME | SETTLEMENTS, MMS
| Site Stop Service Date: | SITECODE | SITE_STOP_SRVC_DT | 1. Must be later than Site In-Service Date. 2. mm/dd/yy format. 3. Not null. | SME | SETTLEMENTS, MMS
| Congestion Management Zone for 2003: | SITECODE | CMZ_2003 | 1. Select from the list: North,South,Houston,West. 2. Not Null | SME
| Resource owned by NOIE? | SITECODE | RE_OWNED_NOIE_FLG | 1. Select from the list: Y or N 2. Not Null | RARF Glossary
| Is Resource behind a NOIE Settlement Meter Point? | SITECODE | RE_BHND_NOIE_SMP_FLG | 1. Select from the list: Y or N 2. Not Null | RARF Glossary
| Number of EPS Primary meters: | SITECODE | NUM_EPS_METERS | Not null | RARF Glossary
| Generation Load Split? | SITECODE | GEN_LOAD_SPLIT_FLG | 1. Select from the list: Y or N 2. Not Null | RARF Glossary | SETTLEMENTS
| ESI ID: | SITECODE | ESI_ID | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Not Required of Resource Behind NOIE Settlement point is 'Y' 2. Data type is character | RARF Glossary | SETTLEMENTS
| ERCOT Read Meter? | SITECODE | ERCOT_READ_FLG | 1. Select from the list: Y or N 2. Not Null | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITECODE | TDSP | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITECODE | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'N'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
Site Load Split
Complete this section if the Gen Site Load is split among multiple ESI IDs.
| ESI ID 1: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
| ESI ID 2: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
| ESI ID 3: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
| ESI ID 4: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
| ESI ID 5: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS
| ESI ID 6: |  |  | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Data type is character | RARF Glossary | SETTLEMENTS
| Fixed Load Splitting % | SITE_LOAD_SPLIT | FIXED_LD_SPLIT | 1.This field is conditional. Required only if Generation Load Split is 'Y' . 2. Must have minimum of 2 ESI ID's entered 3. Sum of Fixed Load Splitting % should be 100 | RARF Glossary | SETTLEMENTS
| Competitive Retailer | SITE_LOAD_SPLIT | COMP_RETAILER | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| Competitive Retailer DUNS # | SITE_LOAD_SPLIT | COMP_RETAILER_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of Competitive Retailer provided in cell above | RARF Glossary | SETTLEMENTS
| TDSP Providing Service To Resource: | SITE_LOAD_SPLIT | TDSP_PROVIDING_SVC | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Select From drop down list provided. | RARF Glossary | SETTLEMENTS
| TDSP DUNS Number: | SITE_LOAD_SPLIT | TDSP_DUNS | 1.This field is conditional. Required only if Generation Load Split is 'Y'. 2. Prepopulated with DUNS of TDSP provided in cell above | RARF Glossary | SETTLEMENTS

## Unit Info - GEN
ERCOT Confidential
Unit Information
This worksheet tab provides generator unit information for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GENERATION RESOURCES (non-WIND, non-CC)
| Unit Details | Table: | DB Field: | Rules: | Source | APPLICATION
| Unit Name | GENERATION | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | RARF Glossary | SETTLEMENTS, NMMS
| Resource Name (Unit Code/Mnemonic) | GENERATION | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | RARF Glossary | SETTLEMENTS, NMMS
| PUC Registration Number | GENERATION | PUC_NUM | 1. Optional. | RARF Glossary
| ERCOT Interconnection Project Number - only new units | GENERATION | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | RARF Glossary
| NERC Number | GENERATION | NERC_NUM | 1. Optional. | RARF Glossary
| Unit Commercial Date | GENERATION | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | RARF Glossary | SETTLEMENTS, NMMS
| Unit End Date | GENERATION | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | RARF Glossary | SETTLEMENTS, NMMS
| Physical Unit Type | GENERATION | PHYS_UNIT_TYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Primary Fuel Type | GENERATION | PRIM_FUELTYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Secondary Fuel Type | GENERATION | SEC_FUELTYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Fuel Transportation Type | GENERATION | FUEL_TRANSTYPE | 1. Select from the list 2. Not null. | RARF Glossary
| Renewable | GENERATION | RENEWABLE_FLG | 1. Not null. 2. Select Y or N | RARF Glossary | EMS, SETTLEMENTS
| Renewable/Offset | GENERATION | RENEWABLE_OFFSET | 1. Not null. 2. Select from the list | RARF Glossary | SETTLEMENTS
| Resource Category | GENERATION | RES_CATG | 1. Not null. 2. Select from the list | RARF Glossary
| Qualifying facility | GENERATION | QUAL_FACILITY_FLG | 1. Not null. 2. Select Y or N | RARF Glossary | SETTLEMENTS
| Name Plate Rating | GENERATION | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | SME | EMS, MMS, NMMS
| Real Power Rating | GENERATION | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | SME | MMS, NMMS
| Reactive Power Rating | GENERATION | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | SME | MMS, NMMS
| Turbine Rating | GENERATION | TURBINE_RTG | 1. Optional. | RARF Glossary
| Unit Generating Voltage | GENERATION | UNIT_KV | 1. Numeric entry only 2. Not null. | RARF Glossary | NMMS
20

## Unit Info - CC
ERCOT Confidential
Unit Information
This worksheet tab applies to all combined cycle generation resources. This information is UNIT and TRAIN specific.
Please complete this sections (one for each train at the facility) and select RETURN TO MAP
COMBINED-CYCLE GENERATION RESOURCES CC1
| Train Details | Table: | DB Field: | Rules: | Source | APPLICATIONS
| Name of Combined Cycle Train | Train | TRAIN_NAME | 1. Not Null. 2. Maximum of 4 character allowed | RARF Glossary | NMMS
| Mnemonic for Combined Cycle Train | Train | TRAIN_CODE | 1. Not Null. 2. Enter Site Code and Train Name for this field (Sitecode_Train_Name) 3. All letters must be capital | RARF Glossary | NMMS
| PUC Registration Number | Train | PUC_NUM | 1. Optional | RARF Glossary
| NERC Number | Train | NERC_NUM | 1. Optional | RARF Glossary
| Unit Commercial Date | Train | TRN_UNIT_START_DATE | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be >= Site In-Service Date | RARF Glossary | EMS. SETTLEMENTS, NMMS
| Unit End Date | Train | TRN_UNIT_END_DATE | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be > Unit Start Date | RARF Glossary | EMS. SETTLEMENTS, NMMS
| Fuel Transportation Type | Train | FUEL_TRANSTYPE_TRN | 1. Select from the list 2. Not null. | RARF Glossary
| Resource Category | Train | RES_CATG_TRN | 1. Select from the list 2. Not null. | RARF Glossary
| Qualifying Facility (Y/N)? | Train | TRN_QUAL_FACILITY_FLG | 1. Select from the list 2. Not null. | RARF Glossary | SETTLEMENTS
| Is train augmented with Duct Burner(s)? | Train | TRN_AUG_DUCTBRNRS_FLG | 1. Select from the list 2. Not null. | RARF Glossary
| Is train augmented with Evap Cooler(s)? | Train | TRN_AUG_EVAP_CLRS_FLG | 1. Select from the list 2. Not null. | RARF Glossary
| Is train augmented with Chiller(s)? | Train | TRN_AUG_CHILLERS_FLG | 1. Select from the list 2. Not null. | RARF Glossary
| Other augmentation? | Train | TRN_OTHER_AUG | 1. Select from the list 2. Not null. | RARF Glossary
Unit Details
| Unit Name | CCUNIT | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | RARF Glossary | SETTLEMENTS, NMMS
| Resource Name (Unit Code/Mnemonic) | CCUNIT | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | RARF Glossary | SETTLEMENTS, NMMS
| ERCOT Interconnection Project Number - only new units | CCUNIT | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | RARF Glossary
| Unit Commercial Date | CCUNIT | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | RARF Glossary | SETTLEMENTS, NMMS
| Unit End Date | CCUNIT | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | RARF Glossary | SETTLEMENTS, NMMS
| Physical Unit Type | CCUNIT | PHYS_UNIT_TYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Primary Fuel Type | CCUNIT | PRIM_FUELTYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Secondary Fuel Type | CCUNIT | SEC_FUELTYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Name Plate Rating | CCUNIT | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | SME | EMS, MMS, NMMS
| Real Power Rating | CCUNIT | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | SME | MMS, NMMS
| Reactive Power Rating | CCUNIT | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | SME | MMS, NMMS
| Turbine Rating | CCUNIT | TURBINE_RTG | 1. Optional. | RARF Glossary
| Unit Generating Voltage | CCUNIT | UNIT_KV | 1. Numeric entry only 2. Not null. | RARF Glossary | NMMS

## Unit Info - Wind
ERCOT Confidential
Unit Information
This worksheet tab applies only to Wind generation resources. This tab is UNIT specific for all Wind.
Please complete this section and select RETURN TO MAP
WIND GENERATION RESOURCES
| Unit Details | Table: | DB Field: | Rules: | Source | APPLICATIONS
| Unit Name | Wind | UNIT_NAME | 1. Not Null. 2. Must not exceed 4 characters for Jointly Owned Units 3. Maximum of 8 character allowed | RARF Glossary | SETTLEMENTS, NMMS
| Resource Name (Unit Code/Mnemonic) | Wind | UNIT_CODE | 1. Not Null. 2. Enter Site Code and Unit Name for this field (Sitecode_Unit Name) 3. All letters must be capital | RARF Glossary | SETTLEMENTS, NMMS
| PUC Registration Number (Docket Number) | Wind | PUC_NUM | 1. Optional. | RARF Glossary
| ERCOT Interconnection Project Number - only new units | Wind | ERCOT_INTRCONN_PROJ_NUM | 1. Required for new sites only | RARF Glossary
| NERC Number (NERC ID#) | Wind | NERC_NUM | 1. Optional. | RARF Glossary
| Unit Commercial Date | Wind | UNIT_START_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be equal to or greater than Site In-Service Date. | RARF Glossary | EMS. SETTLEMENTS, NMMS
| Unit End Date | Wind | UNIT_END_DT | 1. Not null. 2. Format should be: MM/DD/YYYY 3. Must be greater than Unit Start Date. | RARF Glossary | EMS. SETTLEMENTS, NMMS
| Physical Unit Type | Wind | PHYS_UNIT_TYPE | 1. Select from the list 2. Not null. | RARF Glossary | NMMS
| Renewable | Wind | RENEWABLE_FLG | 1. Not null. 2. Select Y or N | RARF Glossary | EMS, SETTLEMENTS
| Renewable/Offset | Wind | RENEWABLE_OFFSET | 1. Not null. 2. Select from the list | RARF Glossary | SETTLEMENTS
| Resource Category | Wind | RES_CATG | 1. Not null. 2. Select from the list | RARF Glossary
| Qualifying facility | Wind | QUAL_FACILITY_FLG | 1. Not null. 2. Select Y or N | RARF Glossary | SETTLEMENTS
| Eligible for McCamey Flowgate Rights (MCFRIs)? | Wind | ELGBL_MCFRI_FLG | 1. Not null. 2. Select Y or N | RARF Glossary
| Name Plate Rating | Wind | NAME_PLT_RTG | 1. Name Plate Rating must be >= Real Power Rating | SME | EMS, MMS, NMMS
| Real Power Rating | Wind | RTG_MW | 1. Real Power Rating must be > Reactive Power Rating | SME | MMS, NMMS
| Reactive Power Rating | Wind | RTG_MVAR | 1. Reactive Power Rating must be <= Name Plate Rating | SME | MMS, NMMS
| Unit Generating Voltage | Wind | UNIT_KV | 1. Numeric entry only 2. Not null. | RARF Glossary | NMMS
| Latitude of center of Wind Farm | Wind | LAT_CTR_WNDFARM | 1. Not null. 2. Latitude Must be >=25 degrees and <=37 decimal degrees | SME | NMMS
| Longitude of center of Wind Farm | Wind | LONG_CTR_WNDFARM | 1. Not null. 2. Longitude Must be >=92 decimal degrees and <= 107 decimal degrees | SME | NMMS
| Average Height above ground of Turbine Hub | Wind | AVG_HGHT_ABV_GRND | 1. Not null. | RARF Glossary
| Latitude of Meteorological Tower | Wind | LAT_METG_TOWER | 1. Not null. 2. Latitude Must be >=25 degrees and <=37 decimal degrees | SME | NMMS
| Longitude of Meteorological Tower | Wind | LONG_METG_TOWER | 1. Not null. 2. Longitude Must be >=92 decimal degrees and <= 107 decimal degrees | SME | NMMS
| Height of Meteorological Tower Instrumentation | Wind | HGHT_METG_TOW_INST | 1. Not null. | RARF Glossary
Turbine Details - Turbine Information by Model
| Group 1 - Type of Turbine (Manufacturer/Model) | Wind | GRP1_TUR_TYPE | 1. Not null. | RARF Glossary | NMMS
| Group 1 - MW Rating for this model of Turbine | Wind | GRP1_TUR_MW_MDL_RTG | 1. Not null. | RARF Glossary | NMMS
| Group 1 - Number of this type of Turbine | Wind | GRP1_TUR_NUM | 1. Not null. | RARF Glossary | NMMS
| Group 2 - Type of Turbine (Manufacturer/Model) | Wind | GRP2_TUR_TYPE | 1. Optional. 2. Group2 reactive capability-Wind Tab should have values for this group. | RARF Glossary | NMMS
| Group 2 - MW Rating for this model of Turbine | Wind | GRP2_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group2 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 2 - Number of this type of Turbine | Wind | GRP2_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group2 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 3 - Type of Turbine (Manufacturer/Model) | Wind | GRP3_TUR_TYPE | 1. Optional. 2. Group3 reactive capability-Wind Tab should have values for this group. | RARF Glossary | NMMS
| Group 3 - MW Rating for this model of Turbine | Wind | GRP3_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group3 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 3 - Number of this type of Turbine | Wind | GRP3_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group3 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 4 - Type of Turbine (Manufacturer/Model) | Wind | GRP4_TUR_TYPE | 1. Optional. 2. Group4 reactive capability-Wind Tab should have values for this group. | RARF Glossary | NMMS
| Group 4 - MW Rating for this model of Turbine | Wind | GRP4_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group4 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 4 - Number of this type of Turbine | Wind | GRP4_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group4 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 5 - Type of Turbine (Manufacturer/Model) | Wind | GRP5_TUR_TYPE | 1. Optional. 2. Group5 reactive capability-Wind Tab should have values for this group. | RARF Glossary | NMMS
| Group 5 - MW Rating for this model of Turbine | Wind | GRP5_TUR_MW_MDL_RTG | 1. Conditional required if Type of turbine info is entered for Group5 2. Data type should be numeric. | RARF Glossary | NMMS
| Group 5 - Number of this type of Turbine | Wind | GRP5_TUR_NUM | 1. Conditional required if Type of turbine info is entered for Group5 2. Data type should be numeric. | RARF Glossary | NMMS
| Total number of turbines | Wind | TOTNUM_TURBINES | 1. Numeric entry only 2. Not null. | RARF Glossary | NMMS
38

## Parameters - GEN
ERCOT Confidential
Resource Parameters
This worksheet tab provides resource parameters for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GENERATION RESOURCES (non-WIND, non-CC)
| Reasonability Limits | Table: | DB Field: | Rules: | Source | APPLICATION
| High Reasonability Limit | Generation | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null 4. HRL should be <= Real Power Rating (WARNING) | SME | MMS, NMMS
| Low Reasonability Limit | Generation | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. LRL must be zero for Private Use Network Sites 4. Not Null | SME | MMS, NMMS
| High Reasonability Ramp Rate Limit | Generation | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | SME | EMS, MMS, NMMS
| Low Reasonability Ramp Rate Limit | Generation | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null 3. | SME | EMS, MMS, NMMS
Seasonal Ratings
| Seasonal Net Max Sustainable Rating - Spring | Generation | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Spring | Generation | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Spring | Generation | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Spring | Generation | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Summer | Generation | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Summer | Generation | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Summer | Generation | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Summer | Generation | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Fall | Generation | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Fall | Generation | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Fall | Generation | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Fall | Generation | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Winter | Generation | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Winter | Generation | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Winter | Generation | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Winter | Generation | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS

## Parameters - CC
ERCOT Confidential
Resource Parameters
This worksheet tab provides resource parameters for Combined Cycle generation resources. This tab is UNIT specific for all CC.
Please complete this section and select RETURN TO MAP
CC GENERATION RESOURCES CC1
| Reasonability Limits | Table: | DB Field: | Rules: | Source | APPLICATION
| High Reasonability Limit | CCUNIT | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null 4. HRL should be <= Real Power Rating (WARNING) | SME | MMS, NMMS
| Low Reasonability Limit | CCUNIT | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. LRL must be zero for Private Use Network Sites 4. Not Null | SME | MMS, NMMS
| High Reasonability Ramp Rate Limit | CCUNIT | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null 3. Not Required if the Primary Fuel Type on the Unit Info – CC tab is 'STM' | SME | EMS, MMS, NMMS
| Low Reasonability Ramp Rate Limit | CCUNIT | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null 3. Not Required if the Primary Fuel Type on the Unit Info – CC tab is 'STM' | SME | EMS, MMS, NMMS
Seasonal Ratings
| Seasonal Net Max Sustainable Rating - Spring | CCUNIT | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Spring | CCUNIT | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Spring | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Spring | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Summer | CCUNIT | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Summer | CCUNIT | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Summer | CCUNIT | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Summer | CCUNIT | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Fall | CCUNIT | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Fall | CCUNIT | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Fall | CCUNIT | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Fall | CCUNIT | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Winter | CCUNIT | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Winter | CCUNIT | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Winter | CCUNIT | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Winter | CCUNIT | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS

## Parameters - CFG
ERCOT Confidential
Resource Parameters
This worksheet tab provides resource parameters for Combined Cycle generation resources. This tab is specific to all CC configurations.
Please complete this section and select RETURN TO MAP.
CC GENERATION RESOURCES CC1 CONFIGURATIONS
| Reasonability Limits | Table: | DB Field: | Rules: | Source | APPLICATION
| High Reasonability Limit | CONFIGURATION | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null 4. HRL should be <= Real Power Rating (WARNING) | SME | MMS, NMMS
| Low Reasonability Limit | CONFIGURATION | LR_LMT | 1. Low Reasonability Limit >0 for Non PUN sites 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. LRL must be zero for Private Use Network Sites 4. Not Null | SME | MMS, NMMS
| High Reasonability Ramp Rate Limit | CONFIGURATION | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | SME | EMS, MMS, NMMS
| Low Reasonability Ramp Rate Limit | CONFIGURATION | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | SME | EMS, MMS, NMMS
Seasonal Ratings
| Seasonal Net Max Sustainable Rating - Spring | CONFIGURATION | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Spring | CONFIGURATION | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Spring | CONFIGURATION | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Spring | CONFIGURATION | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Summer | CONFIGURATION | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Summer | CONFIGURATION | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Summer | CONFIGURATION | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Summer | CONFIGURATION | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Fall | CONFIGURATION | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Fall | CONFIGURATION | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Fall | CONFIGURATION | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Fall | CONFIGURATION | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Winter | CONFIGURATION | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Winter | CONFIGURATION | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Winter | CONFIGURATION | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Winter | CONFIGURATION | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS

## Parameters - WIND
ERCOT Confidential
Resource Parameters
This worksheet tab provides resource parameters for Wind generation resources. This tab is UNIT specific for all Wind.
Please complete this section and select RETURN TO MAP
WIND GENERATION RESOURCES
| Reasonability Limits | Table: | DB Field: | Rules: | Source | APPLICATION
| High Reasonability Limit | WIND | HR_LMT | 1. High Reasonability Limit >0 2. HighReasonabilityLimit >= LowReasonablityLimit 3. Not Null 4. HRL should be <= Real Power Rating (WARNING) | SME | MMS, NMMS
| Low Reasonability Limit | WIND | LR_LMT | 1. Low Reasonability Limit >0 2. Low ReasonabilityLimit <= High ReasonablityLimit 3. Not Null | SME | MMS, NMMS
| High Reasonability Ramp Rate Limit | WIND | HR_RAMPRATE_LMT | 1. High Reasonability Ramp Rate Limit >= Low Reasonability Ramp Rate Limit. 2. Not null | SME | EMS, MMS, NMMS
| Low Reasonability Ramp Rate Limit | WIND | LR_RAMP_RATE_LMT | 1. Low Reasonability Ramp Rate Limit >=0. 2. Not null | SME | EMS, MMS, NMMS
Seasonal Ratings
| Seasonal Net Max Sustainable Rating - Spring | WIND | SEASON_NET_MAX_SUST_RTG_SP | 1.Seasonal Net Max Sustainable Rating - Spring >= Seasonal Net Min Sustainable Rating - Spring 2.Seasonal Net Max Sustainable Rating - Spring <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Spring | WIND | SEASON_NET_MIN_SUST_RTG_SP | 1.Seasonal Net Min Sustainable Rating - Spring >= Seasonal Net Min Emergency Rating - Spring. 2.Seasonal Net Min Sustainable Rating - Spring >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Spring | WIND | SEASON_NET_MAX_EMGY_RTG_SP | 1.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Min Emergency Rating - Spring 2.Seasonal Net Max Emergency Rating - Spring >= Seasonal Net Max Sustainable Rating - Spring. 3.Seasonal Net Max Emergency Rating - Spring <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Spring | WIND | SEASON_NET_MIN_EMGY_RTG_SP | 1. Seasonal Net Min Emergency Rating - Spring >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Summer | WIND | SEASON_NET_MAX_SUST_RTG_SM | 1.Seasonal Net Max Sustainable Rating - Summer >= Seasonal Net Min Sustainable Rating - Summer 2.Seasonal Net Max Sustainable Rating - Summer <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Summer | WIND | SEASON_NET_MIN_SUST_RTG_SM | 1.Seasonal Net Min Sustainable Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Min Sustainable Rating - Summer >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Summer | WIND | SEASON_NET_MAX_EMGY_RTG_SM | 1.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Min Emergency Rating - Summer 2.Seasonal Net Max Emergency Rating - Summer >= Seasonal Net Max Sustainable Rating - Summer. 3. Seasonal Net Max Emergency Rating - Summer <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Summer | WIND | SEASON_NET_MIN_EMGY_RTG_SM | 1.Seasonal Net Min Emergency Rating - Summer >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Fall | WIND | SEASON_NET_MAX_SUST_RTG_FL | 1.Seasonal Net Max Sustainable Rating - Fall >= Seasonal Net Min Sustainable Rating - Fall 2.Seasonal Net Max Sustainable Rating - Fall <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Fall | WIND | SEASON_NET_MIN_SUST_RTG_FL | 1.Seasonal Net Min Sustainable Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2. Seasonal Net Min Sustainable Rating - Fall >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Fall | WIND | SEASON_NET_MAX_EMGY_RTG_FL | 1.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Min Emergency Rating - Fall 2.Seasonal Net Max Emergency Rating - Fall >= Seasonal Net Max Sustainable Rating - Fall. 3.Seasonal Net Max Emergency Rating - Fall <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Fall | WIND | SEASON_NET_MIN_EMGY_RTG_FL | 1.Seasonal Net Min Emergency Rating - Fall >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS
| Seasonal Net Max Sustainable Rating - Winter | WIND | SEASON_NET_MAX_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter 2.Seasonal Net Max Sustainable Rating - Winter <= High Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Min Sustainable Rating - Winter | WIND | SEASON_NET_MIN_SUST_RTG_WT | 1.Seasonal Net Max Sustainable Rating - Winter >= Seasonal Net Min Sustainable Rating - Winter. 2.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 3. Not Null | SME | MMS, NMMS
| Seasonal Net Max Emergency Rating - Winter | WIND | SEASON_NET_MAX_EMGY_RTG_WT | 1.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Min Emergency Rating - Winter 2.Seasonal Net Max Emergency Rating - Winter >= Seasonal Net Max Sustainable Rating - Winter. 3.Seasonal Net Max Emergency Rating - Winter <= High Reasonability Limit 4. Not Null | SME | MMS, NMMS
| Seasonal Net Min Emergency Rating - Winter | WIND | SEASON_NET_MIN_EMGY_RTG_WT | 1.Seasonal Net Min Emergency Rating - Winter >= Low Reasonability Limit 2. Not Null | SME | MMS, NMMS

## Operational Parameters - GEN
ERCOT Confidential
This worksheet tab provides resource parameters for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GENERATION RESOURCES (non-WIND, non-CC)
| Resource Parameters | Table: | DB Field: | Rules: | Source | APPLICATION
| Minimum On Line Time | GENERATION | MIN_ONLINE_TIME | 1. Minimum On Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Minimum Off Line Time | GENERATION | MIN_OFFLINE_TIME | 1. Minimum Off Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Hot Start Time | GENERATION | HOTSTART | 1. Hot Start Time <= Intermediate Start Time. 2. Should be >=0. 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate Start Time | GENERATION | INTERMSTART | 1. Intermediate Start Time<= Cold Start Time. 2. Cold Start Time >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Cold Start Time | GENERATION | COLDSTART | 1. Cold Start Time > = Intermediate Start Time. 2. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Weekly Starts | GENERATION | MAXWKLYSTARTS | 1.Max Weekly Starts >= Max Daily Starts. 2.Min value 1, Max value is 85. | SME | MMS, NMMS
| Max On Line Time | GENERATION | MAX_ONLINE_TIME | 1. Max On Line Time should be >0 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Daily Starts | GENERATION | MAXDLYSTARTS | 1. Max Daily Starts is an integer. 2. Not Null 3. Min value 1, Max value 13 | SME | MMS, NMMS
| Max Weekly Energy | GENERATION | MAXWKLYENRGY | 1. Max Weekly Energy > =0 | SME | MMS, NMMS
| Hot-to-Intermediate Time | GENERATION | HOT_TO_INTMDT_TIME | 1. Not null . 2. Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate-to-Cold Time | GENERATION | INTMDT_TO_COLD_TIME | 1. Not null . 2.Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
Normal Ramp Rate Curve
| MW1 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
Emergency Ramp Rate Curve
| MW1 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
71

## Operational Parameters - CFG
ERCOT Confidential
Operational Resource Parameters Resource Entity authorizes QSE representing this Generation Resource to submit Resource Parameters on this page for operational purposes in accordance with Section 3.7.1 on behalf of Resource Entity.
This worksheet tab provides resource parameters for Combined Cycle generation resources. This tab is Configuration specific.
Please complete this section and select RETURN TO MAP
CC GENERATION RESOURCES CC1 CONFIGURATIONS
| Resource Parameters | Table: | DB Field: | Rules: | Source | APPLICATION
| Minimum On Line Time | CONFIGURATION | MIN_ONLINE_TIME | 1. Minimum On Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Minimum Off Line Time | CONFIGURATION | MIN_OFFLINE_TIME | 1. Minimum Off Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Hot Start Time | CONFIGURATION | HOTSTART | 1. Hot Start Time <= Intermediate Start Time. 2. Should be >=0. 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate Start Time | CONFIGURATION | INTERMSTART | 1. Intermediate Start Time<= Cold Start Time. 2. Cold Start Time >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Cold Start Time | CONFIGURATION | COLDSTART | 1. Cold Start Time > = Intermediate Start Time. 2. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Weekly Starts | CONFIGURATION | MAXWKLYSTARTS | 1.Max Weekly Starts >= Max Daily Starts. 2.Min value 1, Max value is 85. | SME | MMS, NMMS
| Max On Line Time | CONFIGURATION | MAX_ONLINE_TIME | 1. Max On Line Time should be >0 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Daily Starts | CONFIGURATION | MAXDLYSTARTS | 1. Max Daily Starts is an integer. 2. Not Null 3. Min value 1, Max value 13 | SME | MMS, NMMS
| Max Weekly Energy | CONFIGURATION | MAXWKLYENRGY | 1. Max Weekly Energy > =0 | SME | MMS, NMMS
| Hot-to-Intermediate Time | CONFIGURATION | HOT_TO_INTMDT_TIME | 1. Not null . 2. Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate-to-Cold Time | CONFIGURATION | INTMDT_TO_COLD_TIME | 1. Not null . 2.Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
Normal Ramp Rate Curve
| MW1 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Emergency Ramp Rate Curve |  |  |  |  | MMS, NMMS
| MW1 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS

## Operational Parameters - WIND
ERCOT Confidential
Operational Resource Parameters Resource Entity authorizes QSE representing this Generation Resource to submit Resource Parameters on this page for operational purposes in accordance with Section 3.7.1 on behalf of Resource Entity.
This worksheet tab provides resource parameters for Wind generation resources. This tab is UNIT specific for all Wind.
Please complete this section and select RETURN TO MAP
WIND GENERATION RESOURCES
| Resource Parameters | Table: | DB Field: | Rules: | Source | APPLICATION
| Minimum On Line Time | WIND | MIN_ONLINE_TIME | 1. Minimum On Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Minimum Off Line Time | WIND | MIN_OFFLINE_TIME | 1. Minimum Off Line Time should be >0. 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it UP) | SME | MMS, NMMS
| Hot Start Time | WIND | HOTSTART | 1. Hot Start Time <= Intermediate Start Time. 2. Should be >=0. 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate Start Time | WIND | INTERMSTART | 1. Intermediate Start Time<= Cold Start Time. 2. Cold Start Time >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Cold Start Time | WIND | COLDSTART | 1. Cold Start Time > = Intermediate Start Time. 2. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Weekly Starts | WIND | MAXWKLYSTARTS | 1.Max Weekly Starts >= Max Daily Starts. 2.Min value 1, Max value is 85. | SME | MMS, NMMS
| Max On Line Time | WIND | MAX_ONLINE_TIME | 1. Max On Line Time should be >0 2. Decimal positive number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Max Daily Starts | WIND | MAXDLYSTARTS | 1. Max Daily Starts is an integer. 2. Not Null 3. Min value 1, Max value 13 | SME | MMS, NMMS
| Max Weekly Energy | WIND | MAXWKLYENRGY | 1. Max Weekly Energy > =0 | SME | MMS, NMMS
| Hot-to-Intermediate Time | WIND | HOT_TO_INTMDT_TIME | 1. Not null . 2. Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
| Intermediate-to-Cold Time | WIND | INTMDT_TO_COLD_TIME | 1. Not null . 2.Should be >=0 3. Decimal non-negative number of hours should be submitted. (Warning! If decimal value is submitted then Downstream System will round it DOWN) | SME | MMS, NMMS
Normal Ramp Rate Curve
| MW1 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_NRRC | MW_NUMBER_NRRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_NRRC | UPWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_NRRC | DOWNWARD_RAMPRATE_NRRC | 1. Low Reasonable Ramp Rate Limit <= Normal Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Downward Ramp Rate <= Emergency Downward Ramp Rate 3. Must not be negative or zero | SME | MMS, NMMS
Emergency Ramp Rate Curve
| MW1 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. 2. Not Null | SME | MMS, NMMS
| Upward RampRate1 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate1 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Not Null 4. Must not be negative or zero | SME | MMS, NMMS
| MW2 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate2 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate2 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW3 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate3 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate3 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW4 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate4 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate4 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW5 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate5 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate5 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW6 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate6 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate6 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW7 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate7 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate7 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS
| MW8 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate8 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate8 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW9 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate9 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate9 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| MW10 | RAMP_RATES_ERRC | MW_NUMBER_ERRC | 1. MW1,MW2,MW3,MW4,MW5 all are unique. | SME | MMS, NMMS
| Upward RampRate10 | RAMP_RATES_ERRC | UPWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Up ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate. 3. Must not be negative or zero | SME | MMS, NMMS
| Downward RampRate10 | RAMP_RATES_ERRC | DOWNWARD_RAMPRATE_ERRC | 1. Low Reasonable Ramp Rate Limit <= Emergency Dn ramp rate <= High Reasonable Ramp Rate Limit 2. Normal Upward Ramp Rate <= Emergency Upward RampRate 3. Must not be negative or zero | SME | MMS, NMMS

## Reactive Capability - Gen
ERCOT Confidential |  | RETURN TO MAP
Reactive Capability
This worksheet tab provides reactive capability for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GENERATION RESOURCES (non-WIND, non-CC)
| Reactive Capability Curve | Labels | Table: | DB Field: | Rules: | Source | APPLICATION
| MW1 | MW | GENERATION | MW1 | 1. MW1 >=0 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW1 output | MVAR | GENERATION | MVAR1LAG | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW1 output | MVAR | GENERATION | MVAR1LEAD | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW2 | MW | GENERATION | MW2 | 1. MW2>0 2. MW2<MW3 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW2 output | MVAR | GENERATION | MVAR2LAG | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW2 output | MVAR | GENERATION | MVAR2LEAD | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW3 | MW | GENERATION | MW3 | 1. MW3 >0 2. MW3<MW4 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW3 output | MVAR | GENERATION | MVAR3LAG | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW3 output | MVAR | GENERATION | MVAR3LEAD | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW4 | MW | GENERATION | MW4 | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW4 output | MVAR | GENERATION | MVAR4LAG | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW4 output | MVAR | GENERATION | MVAR4LEAD | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW5 - Unity Power Factor | MW | GENERATION | MW5UNITYPF | 1. MW5 >0 2. MW5 >MW4 | SME | EMS, MMS, NMMS, PLANNING
| If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | PSI | GENERATION | HYDROCOOLED | Data type is Numeric | Glossary
| Net Maximum Leading Operating Capability (MVAR) | MVAR | GENERATION | NETMAXLEAD | 1.Net Maximum Leading Operating Capability <=0 | SME | EMS, MMS, NMMS, PLANNING
| Net Maximum Lagging Operating Capability (MVAR) | MVAR | GENERATION | NETMAXLAG | 1.Net Maximum Lagging Operating Capability >=0 | SME | EMS, MMS, NMMS, PLANNING
| Manufacturer's Capability Curve submitted? | Y/N | GENERATION | MFR_CAPABILITY_CURVE_FLG | Select from the list: Y or N | Glossary

## Reactive Capability - CC
ERCOT Confidential |  | RETURN TO MAP
Reactive Capability
This worksheet tab provides reactive capability for Combined Cycle generation resources. This tab is UNIT specific for all CC.
Please complete this section and select RETURN TO MAP
CC GENERATION RESOURCES CC1
| Reactive Capability Curve | Labels | Table: | DB Field: | Rules: | Source | APPLICATION
| MW1 | MW | CCUNIT | MW1_GEN | 1. MW1 >=0 2. MW1<MW2. 3. X(1) <= WMN(Unit Minimal output) where X(1) represents MW1( Generate a Warning Only when Business Rule#2 fails) | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW1 output | MVAR | CCUNIT | MVAR1LAG_GEN | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW1 output | MVAR | CCUNIT | MVAR1LEAD_GEN | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW2 | MW | CCUNIT | MW2_GEN | 1. MW2>0 2. MW2<MW3 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW2 output | MVAR | CCUNIT | MVAR2LAG_GEN | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW2 output | MVAR | CCUNIT | MVAR2LEAD_GEN | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW3 | MW | CCUNIT | MW3_GEN | 1. MW3 >0 2. MW3<MW4 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW3 output | MVAR | CCUNIT | MVAR3LAG_GEN | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW3 output | MVAR | CCUNIT | MVAR3LEAD_GEN | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW4 | MW | CCUNIT | MW4_GEN | 1. MW4 >0 2. MW4<MW5 3. X(n) > = WMX (Unit Max output) where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate a Warning Only When Business Rule#2 Fails] | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW4 output | MVAR | CCUNIT | MVAR4LAG_GEN | 1. >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Lagging MVAR must be >= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW4 output | MVAR | CCUNIT | MVAR4LEAD_GEN | 1. <=0 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR | SME | EMS, MMS, NMMS, PLANNING
| MW5 - Unity Power Factor | MW | CCUNIT | MW5UNITYPF_GEN | 1. MW5 >0 2. MW5 >MW4 | SME | EMS, MMS, NMMS, PLANNING
| If hydrogen cooled, indicate hydrogen pressure (psi) associated with your Reactive Curve submitted for ERCOT studies | PSI | CCUNIT | HYDROCOOLED | Data type is Numeric | Glossary | EMS, MMS, NMMS, PLANNING
| Net Maximum Leading Operating Capability (MVAR) | MVAR | CCUNIT | NETMAXLEAD_GEN | 1.Net Maximum Leading Operating Capability <=0 | SME | EMS, MMS, NMMS, PLANNING
| Net Maximum Lagging Operating Capability (MVAR) | MVAR | CCUNIT | NETMAXLAG_GEN | 1.Net Maximum Lagging Operating Capability >=0 | SME | EMS, MMS, NMMS, PLANNING
| Manufacturer's Capability Curve submitted? | Y/N | CCUNIT | MFR_CAPABILITY_CURVE_FLG | Select from the list: Y or N | Glossary

## Reactive Capability - Wind
ERCOT Confidential |  | RETURN TO MAP
Reactive Capability
This worksheet tab provides reactive capability for Wind generation resources. This tab is UNIT specific for all WIND.
Please complete this section and select RETURN TO MAP
WIND GENERATION RESOURCES UNIT 1
| Reactive Capability Curve | Labels | Table: | DB Field: | Rules: | Source | APPLICATION
| Does this unit meet the ERCOT Reactive Standard? | Y/N
| MW1 | MW | REACT_CAP_WIND | MW1 | 1. MW1 >=0.1 2.MW1<MW2. 3. X(1) <= WMN(Unit Minimal output or LRL) where X(1) represents MW1( Generate a Warning Only when this rule fails). | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW1 output | MVAR | REACT_CAP_WIND | MVAR1LAG | 1. Lagging MVAR limit associated with MW1 output >=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LAG value is negative 4. Lagging MVAR must be>= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW1 output | MVAR | REACT_CAP_WIND | MVAR1LEAD | 1. Leading MVAR limit associated with MW1 output <=0 . 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3) Generate a Warning only if LEAD value is positive | SME | EMS, MMS, NMMS, PLANNING
| MW2 | MW | REACT_CAP_WIND | MW2 | 1. MW2 >0 2. MW2<MW3 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW2 output | MVAR | REACT_CAP_WIND | MVAR2LAG | 1. Lagging MVAR limit associated with MW2 output >=0 . 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4 .Lagging MVAR must be>= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW2 output | MVAR | REACT_CAP_WIND | MVAR2LEAD | 1.Leading MVAR limit associated with MW2 output <=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | SME | EMS, MMS, NMMS, PLANNING
| MW3 | MW | REACT_CAP_WIND | MW3 | 1. MW3 >0 2.MW3<MW4 | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW3 output | MVAR | REACT_CAP_WIND | MVAR3LAG | 1Lagging MVAR limit associated with MW3 output >=0 . 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4. Lagging MVAR must be>= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW3 output | MVAR | REACT_CAP_WIND | MVAR3LEAD | 1. Leading MVAR limit associated with MW3 output <=0. 2.The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LEAD value is positive | SME | EMS, MMS, NMMS, PLANNING
| MW4 | MW | REACT_CAP_WIND | MW4 | 1. MW4<MW5 2. X(n) > = WMX (Unit Max output or HRL), where n is the last MW value in the curve. If the curve has 4 points, X(n) is X(4) [ Generate an Error When this rule fails. 3)For wind units that have multiple groups of turbines, Produce a Warning Only when the rule#2 fails (MW4 should be >= HRL) . For Units that have single group of turbine, produce an Error when the rule fails (MW4 should be >= HRL) | SME | EMS, MMS, NMMS, PLANNING
| Lagging MVAR limit associated with MW4 output | MVAR | REACT_CAP_WIND | MVAR4LAG | 1. Lagging MVAR limit associated with MW4 output >=0. 2. The square root of (X(i)^2 + Ym(i)^2) <= S(unit MVA Rating), 1<=m<=2, 1<=i<=n. where X ->MW and Y1-> Lagging MVAR, Y2-> Leading MVAR 3. Generate a Warning only if LAG value is negative 4. Lagging MVAR must be>= MVAR Leading | SME | EMS, MMS, NMMS, PLANNING
| Leading MVAR limit associated with MW4 output | MVAR | REACT_CAP_WIND | MVAR4LEAD | 1. Leading MVAR limit associated with MW3 output <=0 . 2. Generate a Warning only if LEAD value is positive | SME | EMS, MMS, NMMS, PLANNING
| MW5 - Unity Power Factor | MW | REACT_CAP_WIND | MW5UNITYPF
| Net Maximum Leading Operating Capability | MVAR | REACT_CAP_WIND | NETMAXLEAD | 1. Net Maximum Leading Operating Capability <=0 2. Generate a Warning only if LEAD value is positive | SME | EMS, MMS, NMMS, PLANNING
| Net Maximum Lagging Operating Capability | MVAR | REACT_CAP_WIND | NETMAXLAG | 1. Net Maximum Lagging Operating Capability <=0 2. Generate a Warning only if LAG value is positive | SME | EMS, MMS, NMMS, PLANNING
| Has the Manufacturer's Capability Curve submitted? | Y/N | REACT_CAP_WIND | MFR_CAP_CURVE | Select from Y or N | Glossary
17
0
0
#DIV/0!
17
0
0
#DIV/0!
17
0
0
#DIV/0!
17
0
0
#DIV/0!
17
0
0
#DIV/0!

## Dropdowns (hidden)
Data Validations: | TDSP | TDSPDuns | RESCAT | REP | REPDuns
Yes No | AEP TEXAS CENTRAL COMPANY | 007924772 | Nuclear | 1-800-RECONEX INC | 802745240
| AEP TEXAS NORTH COMPANY | 007923311 | Hydro | ABSOLUTE ELECTRIC INC DBA ABSOLUTE POWER I (API) | 614150931
CMZone | AEP TEXAS NORTH COMPANY SPP | 053693388 | Coal and Lignite | ACACIA ENERGY INC (LSE) | 787476634
| BANDERA ELECTRIC CO OP INC (TDSP) | 0089451494000 | Combined Cycle ≤ 90 MW* | ACCENT ENERGY TEXAS LP (LSE) | 133305370
Unit Type | BARTLETT ELECTRIC CO OP INC | 002781813 | Combined Cycle > 90 MW* | ACN ENERGY INC (LSE) | 081791134
| BELFALLS ELECTRIC CO OP INC (TDSP) | 004998399 | Gas Steam - Supercritical Boiler | AEP TEXAS COMMERCIAL INDUSTRIAL RETAIL LP (LSE) | 038738451
FUELTYPE | BIG COUNTRY ELECTRIC CO OP INC (TDSP) | 0058630484000 | Gas Steam - Reheat Boiler | AFFORDABLE POWER PLAN LP | 171841633 | CODE
| BIG COUNTRY ELECTRIC CO OP INC TXU (TDSP) | 0058630484100 | Gas Steam - Non-reheat or Boiler without air-preheater | ALLIANCE POWER COMPANY LLC | 136249187 | #REF!
TRANSPTYPE | BLUEBONNET ELECTRIC CO OP INC (TDSP) | 0524834354000 | Simple Cycle ≤ 90 MW | AMBIT ENERGY LP (LSE) | 604792791 | #REF!
| BRAZOS ELECTRIC POWER CO OP INC (TDSP) | 0037722904000 | Simple Cycle > 90 MW | AMBRIDGE ENERGY | 788677354 | #REF!
OFFSET | BROWNSVILLE PUBLIC UTILITY BOARD (TDSP) | 6063470374000 | Diesel | AMERIPOWER LLC | 140780003 | #REF!
| BRYAN TEXAS UTILITIES (TDSP) | 0793907794000 | Renewable | ANDELER CORPORATION | 039471953 | #REF!
RESCAT | CAP ROCK ENERGY (HUNT COLLIN DIVISION) (TDSP) | 0079370974100 |  | ANDELER CORPORATION DBA ANDELER RETAIL | 0394719531000 | #REF!
| CAP ROCK ENERGY (MCCULLOCH DIVISION) (TDSP) | 0079370974000 |  | ANP POWER DIRECT COMPANY (LSE) | 125145693 | #REF!
WYE | CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP) | 957877905 |  | AP ELECTRIC LLC (LSE) | 807148635 | #REF!
| CENTRAL TEXAS ELECTRIC CO OP INC (TDSP) | 0079302744000 |  | APN STARFIRST LP | 141081328 | #REF!
TAPLOC | CHEROKEE COUNTY ELEC CO OP ASSOC | 008862625 |  | APNA HOLDINGS LLC | 784260866 | #REF!
| CHEROKEE COUNTY ELEC CO OP ASSOC (CORAL POWER AS QSE) | 0088626254000 |  | APS ENERGY SERVICES CO. | 084611867 | #REF!
SUBMITTAL | CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP) | 8008717664000 |  | ARC ENERGY LLC | 145408444 | #REF!
| CITY OF BARTLETT (TDSP) | 074618935 |  | ASSURANCE ENERGY (TXU LARGE NONRESIDENTIAL POLR) | 1733370281300 | #REF!
NWMODEL | CITY OF BASTROP (TDSP) | 0851553724000 |  | ASSURANCE ENERGY (TXU RESIDENTIAL POLR) | 1733370281100 | #REF!
| CITY OF BELLVILLE (TDSP) | 0935648704000 |  | ASSURANCE ENERGY (TXU SMALL NONRESIDENTIAL POLR) | 1733370281200 | #REF!
| CITY OF BOERNE (TDSP) | 0052470694000 |  | BANDERA ELECTRIC CO OP INC (LSE) | 0089451491000 | #REF!
| CITY OF BOWIE (TDSP) | 8094182964000 |  | BIG COUNTRY ELECTRIC CO OP INC (LSE) | 0058630481000 | #REF!
| CITY OF BRADY (TDSP) | 070804877 |  | BLU POWER OF TEXAS LLC | 604182134 | #REF!
| CITY OF BRENHAM (TDSP) | 0741649224000 |  | BLUEBONNET ELECTRIC CO OP INC (LSE) | 0524834351000 | #REF!
| CITY OF BRIDGEPORT MUN ELEC SYS (TDSP) | 0842801714000 |  | BP ENERGY COMPANY (LSE) | 6252757551000 | #REF!
| CITY OF BURNET (TDSP) | 0746121514000 |  | BP ENERGY COMPANY (SUB-LSE-CNE) | 8797234681100 | #REF!
| CITY OF CASTROVILLE (TDSP) | 797816378 |  | BRAZOS ELECTRIC POWER CO OP INC | 0037722901200 | #REF!
| CITY OF COLEMAN (TDSP) | 1024920064000 |  | BRAZOS ELECTRIC POWER CO OP INC (LSE) | 0037722901000 | #REF!
| CITY OF COLLEGE STATION (TDSP) | 0403303004000 |  | BRAZOS ELECTRIC POWER CO OP INC LCRA | 0037722901100 | #REF!
| CITY OF CUERO (TDSP) | 0526842144000 |  | BRILLIANT ENERGY LLC | 800312048 | #REF!
| CITY OF FARMERSVILLE (TDSP) | 1903494984000 |  | BROWNSVILLE PUBLIC UTILITY BOARD (LSE) | 6063470371000 | #REF!
| CITY OF FLATONIA (TDSP) | 0626890134000 |  | BRYAN TEXAS UTILITIES (LSE) | 0793907791000 | #REF!
| CITY OF FLORESVILLE DBA FLORESVILLE ELEC LIGHT AND PWR | 008948374 |  | CALPINE POWER AMERICA LP | 1127108761000 | #REF!
| CITY OF FREDERICKSBURG (TDSP) | 0769243074000 |  | CAP ROCK ENERGY (HUNT COLLIN DIVISION) (LSE) | 0079370971100 | #REF!
| CITY OF GARLAND (TDSP) | 6011012564000 |  | CAP ROCK ENERGY (MCCULLOCH DIVISION) (LSE) | 0079370971000 | #REF!
| CITY OF GARLAND GBCREEK (TDSP) | 6011012564100 |  | CATALYST ENERGY USA INC (LSE) | 807179234 | #REF!
| CITY OF GEORGETOWN (TDSP) | 0895923724000 |  | CENTRAL TEXAS ELECTRIC CO OP INC (LSE) | 0079302741000 | #REF!
| CITY OF GIDDINGS (TDSP) | 0096899514000 |  | CERTAIN ENERGY | 0086137911100 | #REF!
| CITY OF GOLDSMITH (TDSP) | 0888946704000 |  | CHAIN LAKES POWER LP DBA SIMPLE POWER (LSE) | 806949835 | #REF!
| CITY OF GOLDTHWAITE (TDSP) | 1558252764000 |  | CHAMPION ENERGY SERVICES LLC | 159988406 | #REF!
| CITY OF GONZALES (TDSP) | 0937385404000 |  | CINERGY RETAIL POWER LP (LSE) | 037214421 | #REF!
| CITY OF HALLETTSVILLE (TDSP) | 0090811834000 |  | CIRRO GROUP INC | 034441449 | #REF!
| CITY OF HEARNE MUNICIPAL ELECTRIC SYSTEM (TDSP) | 0897458894000 |  | CITY OF AUSTIN DBA AUSTIN ENERGY (LSE) | 8008717661000 | #REF!
| CITY OF HEMPSTEAD (TDSP) | 1272175604000 |  | CITY OF BASTROP (LSE) | 0851553721000 | #REF!
| CITY OF HONDO (TDSP) | 091703843 |  | CITY OF BELLVILLE (LSE) | 0935648701000 | #REF!
| CITY OF LA GRANGE (TDSP) | 0607085184000 |  | CITY OF BOERNE (LSE) | 0052470691000 | #REF!
| CITY OF LAMPASAS (TDSP) | 0203311204000 |  | CITY OF BOWIE (LSE) | 8094182961000 | #REF!
| CITY OF LEXINGTON (TDSP) | 0081817324000 |  | CITY OF BRADY (LSE) | 0708048771000 | #REF!
| CITY OF LLANO (TDSP) | 0916952054000 |  | CITY OF BRENHAM (LSE) | 0741649221000 | #REF!
| CITY OF LOCKHART (TDSP) | 0746168634000 |  | CITY OF BRIDGEPORT MUN ELEC SYS (LSE) | 0842801711000
| CITY OF LULING (TDSP) | 0105539984000 |  | CITY OF BURNET (LSE) | 0746121511000
| CITY OF MASON (TDSP) | 1561267084000 |  | CITY OF COLEMAN (LSE) | 1024920061000
| CITY OF MOULTON (TDSP) | 0091871544000 |  | CITY OF COLLEGE STATION (LSE) | 0403303001000
| CITY OF ROBSTOWN UTILITY SYSTEM (TDSP) | 9387911424000 |  | CITY OF CUERO (LSE) | 0526842141000
| CITY OF SAN ANTONIO CITY PUBLIC SERVICE (TDSP) | M 0079360734000 |  | CITY OF FARMERSVILLE (LSE) | 1903494981000
| CITY OF SAN MARCOS (TDSP) | 0694628694000 |  | CITY OF FLATONIA (LSE) | 0626890131000
| CITY OF SAN SABA (TDSP) | 0248592254000 |  | CITY OF FREDERICKSBURG (LSE) | 0769243071000
| CITY OF SANGER | 058956020 |  | CITY OF GARLAND (LSE) | 6011012561000
| CITY OF SCHULENBURG (TDSP) | 0532950364000 |  | CITY OF GEORGETOWN (LSE) | 0895923721000
| CITY OF SEGUIN (TDSP) | 0862819794000 |  | CITY OF GIDDINGS (LSE) | 0096899511000
| CITY OF SEYMOUR | 166319145 |  | CITY OF GOLDSMITH (LSE) | 0888946701000
| CITY OF SHINER (TDSP) | 1504533714000 |  | CITY OF GOLDTHWAITE (LSE) | 1558252761000
| CITY OF SMITHVILLE (TDSP) | 0916978134000 |  | CITY OF GONZALES (LSE) | 0937385401000
| CITY OF WAELDER (TDSP) | 0541779694000 |  | CITY OF HALLETTSVILLE (LSE) | 0090811831000
| CITY OF WEIMAR (TDSP) | 0214974584000 |  | CITY OF HEARNE MUNICIPAL ELECTRIC SYSTEM (LSE) | 0897458891000
| CITY OF WHITESBORO | 134546522 |  | CITY OF HEMPSTEAD (LSE) | 1272175601000
| CITY OF YOAKUM (TDSP) | 0694557724000 |  | CITY OF LA GRANGE (LSE) | 0607085181000
| COLEMAN COUNTY ELECTRIC CO OP INC (TDSP) | 0079246734000 |  | CITY OF LAMPASAS (LSE) | 0203311201000
| COMANCHE ELECTRIC CO OP ASSOCIATION | 002889210 |  | CITY OF LEXINGTON (LSE) | 0081817321000
| COMISION FEDERAL | 8100082434000 |  | CITY OF LLANO (LSE) | 0916952051000
| CONCHO VALLEY ELECTRIC CO OP INC (TDSP) | 0038666624000 |  | CITY OF LOCKHART (LSE) | 0746168631000
| CONCHO VALLEY ELECTRIC CO OP INC TXU (TDSP) | 0038666624100 |  | CITY OF LULING (LSE) | 0105539981000
| COOKE COUNTY ELECTRIC CO OP ASSOC INC | 008951808 |  | CITY OF MASON (LSE) | 1561267081000
| DEEP EAST TEXAS ELECTRIC CO OP INC | 047845623 |  | CITY OF MOULTON (LSE) | 0091871541000
| DEEP EAST TEXAS ELECTRIC CO OP INC (BLT TDSP) | 0478456234000 |  | CITY OF ROBSTOWN UTILITY SYSTEM (LSE) | 9387911421000
| DELETEME MARKET PARTICIPANT | 888888888 |  | CITY OF SAN ANTONIO CITY PUBLIC SERVICE (LSE) | 0079360731000
| DENTON COUNTY ELEC CO OP DBA COSERVE ELEC | 008947913 |  | CITY OF SAN MARCOS (LSE) | 0694628691000
| DENTON MUNICIPAL ELECTRIC (TDSP) | 0003540764000 |  | CITY OF SAN SABA (LSE) | 0248592251000
| DEWITT ELECTRIC CO OP INC (TDSP) | 0089461884000 |  | CITY OF SCHULENBURG (LSE) | 0532950361000
| EAST TEXAS ELECTRIC CO OP (TDSP) | 948535265 |  | CITY OF SEGUIN (LSE) | 0862819791000
| ELECTRIC TRANSMISSION TEXAS LLC (TDSP) | 808160514 |  | CITY OF SEYMOUR (LSE) | 1663191451000
| ENTERGY GULF STATES INC | 827438383 |  | CITY OF SHINER (LSE) | 1504533711000
| ENTERGY GULF STATES INC (BLT TDSP) | 8274383834000 |  | CITY OF SMITHVILLE (LSE) | 0916978131000
| FANNIN COUNTY ELECTRIC CO OP INC | 0018220894000 |  | CITY OF WAELDER (LSE) | 0541779691000
| FARMERS ELECTRIC CO OP INC DBA FEC ELECTRIC | 0098442344000 |  | CITY OF WEIMAR (LSE) | 0214974581000
| FAYETTE ELECTRIC CO OP INC (TDSP) | 0593309774000 |  | CITY OF YOAKUM (LSE) | 0694557721000
| FORT BELKNAP ELECTRIC CO OP INC (TDSP) | 007935299 |  | CLEARVIEW ELECTRIC INC | 785129219
| GEUS (TDSP) | 8062449354000 |  | COLEMAN COUNTY ELECTRIC CO OP INC (LSE) | 0079246731000
| GRANBURY MUNICIPAL UTILITIES (TDSP) | 0952141694000 |  | COMISION FEDERAL DE ELECTRICIDAD | 810008243
| GRAYSON COLLIN ELECTRIC CO OP INC | 008953812 |  | COMMERCE ENERGY INC (LSE) | 176343341
| GUADALUPE VALLEY ELECTRIC CO OP INC (TDSP) | 0079305894000 |  | CONCHO VALLEY ELECTRIC CO OP INC (LSE) | 0038666621000
| HAMILTON COUNTY ELECTRIC CO OP (BRAZOS) | 008949216 |  | CONOCOPHILLIPS COMPANY (LSE) | 001368265
| HAMILTON COUNTY ELECTRIC CO OP (LCRA) | 0089492164100 |  | CONSOLIDATED EDISON SOLUTIONS INC | 809887904
| HEART OF TEXAS ELECTRIC COOPERATIVE INC (DSP) | 012074558 |  | CONSTELLATION NEWENERGY INC (LSE) | 8797234681000
| HILCO ELECTRIC CO OP INC (TDSP) | 008950545 |  | CONSTELLATION NEWENERGY INC DBA NEWENERGY (LSE) | 8797234681200
| HOUSTON COUNTY ELEC COOP (TDSP) | 005777206 |  | CONSULTING GROUPS NETWORK LLC DBA POWERONE (LSE) | 119881790
| HOUSTON COUNTY ELEC COOP TXU (TDSP) | 0057772064100 |  | CORAL POWER LLC (LSE) | 9375172661000
| J A C ELECTRIC CO OP INC | 003890795 |  | CORAL POWER LLC DBA CORAL POWER SOLUTIONS (LSE) | 9375172661100
| JACKSON ELECTRICAL CO OP INC | 078423555 |  | CPL RETAIL ENERGY DBA 1300 | 0177405441300
| JASPER NEWTON ELECTRIC CO OP INC | 007933518 |  | CPL RETAIL ENERGY DBA 1400 | 0177405441400
| KARNES ELECTRIC CO OP INC | 006824106 |  | CPL RETAIL ENERGY LP (LSE) | 017740544
| KERRVILLE PUBLIC UTILITY BOARD (TDSP) | 1248248064000 |  | CPL RETAIL ENERGY LP 1100 | 0177405441100
| LAMAR COUNTY ELEC COOP DBA LEC (TDSP) | 0048060974000 |  | CPL RETAIL ENERGY LP DBA CPL | 0177405441200
| LCRA TRANSMISSION SERVICES CORPORATION | 0432268854000 |  | DENTON MUNICIPAL ELECTRIC (LSE) | 0003540761000
| LIGHTHOUSE ELECTRIC CO OP (TDSP) | 0028252894000 |  | DEWITT ELECTRIC CO OP INC (LSE) | 0089461881000
| LIGHTHOUSE ELECTRIC CO OP TXU (TDSP) | 0028252894100 |  | DIRECT ENERGY DBA 1300 | 0397133541300
| LYNTEGAR ELECTRIC CO OP INC (TDSP) | 0079371474000 |  | DIRECT ENERGY DBA 1400 | 0397133541400
| MAGIC VALLEY ELECTRIC CO OP INC (TDSP) | 008951501 |  | DIRECT ENERGY LP DBA DIRECT ENERGY | 039713354
| MCLENNAN COUNTY ELECTRIC CO OP INC | 007509698 |  | DIRECT ENERGY LP DBA DIRECT ENERGY BUSINESS SERVICES | 0397133541000
| MEDINA ELECTRIC CO OP INC (TDSP) AEP | 0081378124100 |  | DIRECT ENERGY LP DBA DIRECT ENERGY MULTI FAMILY | 0397133541200
| MEDINA ELECTRIC CO OP INC (TDSP) STEC | 0081378124000 |  | DPI ENERGY LLC (LSE) | 785092292
| MID SOUTH ELECTRIC CO OP ASSOC | 061278594 |  | DTE ENERGY TRADING INC (LSE) | 383323526
| NAVARRO COUNTY ELECTRIC CO OP INC | 006770101 |  | DYNEGY ENERGY MARKETING LP | 009924445
| NAVASOTA VALLEY ELECTRIC CO OP INC | 046299913 |  | ELECTRIC NOW LP (LSE) | 144817595
| NEW BRAUNFELS UTILITIES (TDSP) | 0383461694000 |  | EN TOUCH SYSTEMS INC (LSE) | 155807808
| NUECES ELECTRIC CO OP INC | 008828857 |  | ENERGY SERVICES PROVIDERS OF TEXAS INC (LSE) | 807680801
| NUECES ELECTRIC CO OP INC AEP (TDSP) | 0088288574100 |  | ENERGY WEST DBA FIRE FLY POWERED BY FRANKLIN POWER (LSE) | 1246639511000
| NUECES ELECTRIC COOP INC PILOT TDSP | 0088288574800 |  | ENERGY WEST LTD D/B/A FRANKLIN POWER COMPANY (LSE) | 124663951
| ONCOR ELECTRIC DELIVERY COMPANY | 1039940674000 |  | ENRON ENERGY SERVICES INC (LSE) | 0043285681000
| PEDERNALES ELEC CO OP INC AEP (TDSP) | 0079241114100 |  | ENRON POWER MARKETING INC (LSE) | 8489212761000
| PEDERNALES ELECTRIC CO OP INC (TDSP) | 0079241114000 |  | ENTERGY GULF STATES INC (BLT LSE) | 8274383831100
| PEDERNALES ELECTRIC COOPERATIVE INC | 0079241114300 |  | ENTERGY SOLUTIONS ESSENTIALS LTD POLR | 0077215121100
| PEDERNALES ELECTRIC COOPERATIVE, INC. | 0079241114200 |  | ENTERGY SOLUTIONS LTD | 007721512
| RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP) | 6243686014000 |  | ENTERGY SOLUTIONS SELECT LTD AFFILIATED REP | 0077215121200
| RIO GRANDE ELECTRIC CO OP (TDSP) | 002781953 |  | ERCOT TESTLSE2LSE | 140000000
| RIO GRANDE ELECTRIC CO OP TXU (TDSP) | 0027819534100 |  | ERCOTPRODVER LSE 31602 | 555555555
| RUSK COUNTY ELECTRIC CO OP (TDSP) | 009844440 |  | ERCOTTEST_LSE_1_K | 111111111
| SAM HOUSTON ELECTRIC CO OP INC (TDSP) | 056267867 |  | ERCOTTEST_LSE_2 | 111111112
| SAN BERNARD ELECTRIC CO OP (TDSP) | 0089453134000 |  | ERCOTTEST_LSE_3 | 111111113
| SAN MIGUEL ELECTRIC CO OP INC (TDSP) | 0884848524000 |  | ERCOTTEST_LSE_4 | 111111114
| SAN PATRICIO ELECTRIC CO OP (TDSP) | 003864907 |  | ESCO1 LLC (LSE) | 791327153
| SHARYLAND UTILITIES LP (TDSP) | 105262336 |  | EXTEX RETAIL SERVICES COMPANY LLC | 131494440
| SHARYLAND UTILITIES NOIE (TDSP) | 1052623364100 |  | EXXONMOBIL POWER AND GAS SERVICES INC (LSE) | 0012132141000
| SOUTH PLAINS ELECTRIC CO OP INC (TDSP) | 007934185 |  | FAYETTE ELECTRIC CO OP INC (LSE) | 0593309771000
| SOUTH TEXAS ELECTRIC CO OP INC | 0038663324000 |  | FIRE FLY ELECTRICITY LLC (LSE) | 127329071
| SOUTHWEST TEXAS ELECTRIC CO OP INC (TDSP) | 0084158954000 |  | FIRST CHOICE POWER SPECIAL PURPOSE LIMITED PARTNERSHIP | 008613791
| SOUTHWESTERN PUBLIC SERVICE COMPANY (TDSP) | 007369713 |  | FIRST CHOICE POWER SPECIAL PURPOSE LP DBA FIRST CHOICE POWER POL | 0086137911000
| SWEPCO ENERGY DELIVERY COMPANY (SWEPCO-EDC) (TDSP) | 026763672 |  | FPL ENERGY POWER MARKETING INC (LSE) | 0544813411000
| TAYLOR ELECTRIC CO OP INC (TDSP) | 0079344254000 |  | FREEDOM GROUP LLC (LSE) | 144991671
| TAYLOR ELECTRIC CO OP INC ABILENE (TDSP) | 0079344254100 |  | FRYAR ENERGY | 189041697
| TEXAS A&M | 0037722904TAM |  | FULCRUM POWER SERVICES LP (LSE) | 1319452431000
| TEXAS MUNICIPAL POWER AGENCY | 071374052 |  | GATEWAY ENERGY SERVICES CORP DBA GATEWAY POWER SERVICES (LSE) | 013876508
| TEXAS-NEW MEXICO POWER CO (TDSP) | 007929441 |  | GEUS (LSE) | 8062449351000
| TRI COUNTY ELECTRIC CO OP INC | 008945123 |  | GEXA CORP DBA GEXA ENERGY CORP (LSE) | 108114542
| TRINITY VALLEY ELEC CO OP | 009844564 |  | GEXA ENERGY (LSE) | 1081145421000
| UNITED ELECTRIC CO OP SERVICES INC | 008945826 |  | GLACIAL ENERGY OF TEXAS INC | 605515472
| VICTORIA ELECTRIC CO OP INC | 008953861 |  | GOLDEN SPREAD ELECTRIC COOPERATIVE INC (TOPS AS QSE) | 1864707791100
| VICTORIA ELECTRIC CO OP INC AEP (TDSP) | 0089538614100 |  | GOLDEN SPREAD ELECTRIC COOPERATIVE INC AEP AS QSE (LSE) | 1864707791000
| WEATHERFORD MUNICIPAL UTILITY SYSTEM (TDSP) | 0817196274000 |  | GOLDEN SPREAD ELECTRIC COOPERATIVE INC TXU AS QSE (LSE) | 186470779
| WESTERN FARMERS ELECTRIC COOPERATIVE (TDSP) | 0728624074000 |  | GOOD GUYS POWER LP (LSE) | 125113790
| WHARTON COUNTY ELECTRIC CO OP INC | 118487958 |  | GRANBURY MUNICIPAL UTILITIES (LSE) | 0952141691000
| WISE ELECTRIC CO OP | 041405408 |  | GREEN MOUNTAIN ENERGY COMPANY - COMMERCIAL | 1768714811200
| WOOD COUNTY ELECTRIC COOPERATIVE INC (TDSP) | 008952491 |  | GREEN MOUNTAIN ENERGY COMPANY (LSE) | 176871481
| Not Listed |  |  | GREEN MOUNTAIN ENERGY COMPANY-MULTIFAMILY (LSE) | 1768714811100
|  |  |  | GREEN MOUNTAIN ENERGY COMPANY-POLR (LSE) | 1768714811300
|  |  |  | GUADALUPE VALLEY ELECTRIC CO OP INC (LSE) | 0079305891000
|  |  |  | HIMALAYA POWER INC (LSE) | 156111168
|  |  |  | HINO ELECTRIC POWER COMPANY (LSE) | 026533844
|  |  |  | HUDSON ENERGY SERVICES LLC (LSE) | 121359595
|  |  |  | HWY 3 MHP LLC (LSE) | 786106208
|  |  |  | HWY 3 MHP LLC DBA ETRICITY (LSE) | 7861062081000
|  |  |  | IDEAL ENERGY INC | 186626128
|  |  |  | INTEGRYS ENERGY SERVICES INC (LSE) | 841739824
|  |  |  | INTEGRYS ENERGY SERVICES OF TEXAS LP | 784382017
|  |  |  | JUICE ENERGY INC (LSE) | 785159356
|  |  |  | JUST ENERGY TEXAS LP DBA JUST ENERGY TEXAS RGV | 1105699981000
|  |  |  | JUST ENERGY TEXAS LP DBA US ENERGY SAVINGS CORP | 110569998
|  |  |  | KERRVILLE PUBLIC UTILITY BOARD (LSE) | 1248248061000
|  |  |  | KINETIC ENERGY LLC | 792535846
|  |  |  | LIBERTY POWER CORP. | 112361204
|  |  |  | LIBERTY POWER DELAWARE LLC | 625111021
|  |  |  | LIBERTY POWER HOLDINGS LLC | 784087293
|  |  |  | LIBERTY POWER TEXAS LLC | 785076246
|  |  |  | LIGHTHOUSE ELECTRIC CO OP (LSE) | 0028252891000
|  |  |  | LINDE ENERGY SERVICES INC (LSE) | 123228178
|  |  |  | LOWER COLORADO RIVER AUTHORITY (LSE) | 0432268851000
|  |  |  | LPT LLC DBA LPT SP LLC | 6116339131000
|  |  |  | LUMINANT ET SERVICES COMPANY (LSE) | 1733370281500
|  |  |  | LYNTEGAR ELECTRIC CO OP INC (LSE) | 0079371471000
|  |  |  | M3 LP (LSE) | 125113799
|  |  |  | MAGIC VALLEY ELECTRIC CO OP INC (LSE) | 0089515011000
|  |  |  | MEGA ENERGY LP | 801176327
|  |  |  | MPOWER RETAIL ENERGY LP (LSE) | 121353085
|  |  |  | MS RETAIL DEVELOPMENT CORP | 138129197
|  |  |  | MUTUAL ENERGY SWEPCO LP (LSE) POLR | 0177415751100
|  |  |  | MXENERGY ELECTRIC LSE | 148062354
|  |  |  | NATIONAL POWER COMPANY INC | 189435345
|  |  |  | NEUMIN PRODUCTION CO | 074606807
|  |  |  | NEW BRAUNFELS UTILITIES (LSE) | 0383461691000
|  |  |  | NEW MEXICO NATURAL GAS LP DBA TEXAS POWER | 807025689
|  |  |  | NM ENERGY OF TEXAS LLC DBA FIVE POINT POWER | 131950672
|  |  |  | NORDIC MARKETING LLC (LSE) | 126473649
|  |  |  | NRG TEXAS RETAIL LLC (LSE) | 807679340
|  |  |  | NUECES ELECTRIC COOPERATIVE INC RETAIL DIVISION (NEC RD) | 0088288571000
|  |  |  | NV POWER LP | 167012553
|  |  |  | OCCIDENTAL POWER MARKETING LP (LSE) | 052298721
|  |  |  | PEDERNALES ELEC CO OP INC AEP (LSE) | 0079241111100
|  |  |  | PEDERNALES ELECTRIC CO OP INC (LSE) | 0079241111000
|  |  |  | PEGASUS ALLIANCE CORPORATION DBA ONPAC ENERGY (LSE) | 136387466
|  |  |  | PEPCO ENERGY SERVICES INC (LSE) | 106173672
|  |  |  | PILOT POWER GROUP INC. | 930453365
|  |  |  | POLR POWER LP | 076882203
|  |  |  | POTENTIA ENERGY LLC (LSE) | 809047512
|  |  |  | PRE BUY ELECTRIC LLC | 188610260
|  |  |  | PRE BUY ELECTRIC RETAIL | 1886102601000
|  |  |  | PRELECTRIC ENERGY SERVICES LLC (LSE) | 159059315
|  |  |  | PRIER ENERGY INC | 800805835
|  |  |  | PRODVERLSETEST5 | 131313131
|  |  |  | PROVIRON ENERGY LTD | 136385270
|  |  |  | RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (LSE) | 6243686011000
|  |  |  | REACH ENERGY LLC | 791894152
|  |  |  | RELIANT ENERGY HL AND P (LSE) | 014396092
|  |  |  | RELIANT ENERGY RETAIL SERVICES LLC | 799530915
|  |  |  | RELIANT ENERGY RETAIL SERVICES LLC POLR DIVISION | 029691099
|  |  |  | RELIANT ENERGY SERVICES CHANNELVIEW LLC | 114743953
|  |  |  | RELIANT ENERGY SOLUTIONS LLC | 616498114
|  |  |  | RELIANT ENERGY SOLUTIONS LLC POLR DIVISION (LSE) | 029692659
|  |  |  | REPOWER LLC (LSE) | 614822497
|  |  |  | REPUBLIC POWER DBA ENERGY AMERICA II (TEST) | 0397133541100
|  |  |  | RETAIL POWER SUPPLY LP | 362699949
|  |  |  | RIO GRANDE ELEC CO OP (LSE) AEP | 0027819531100
|  |  |  | RIO GRANDE ELECTRIC CO OP (LSE) TXU | 0027819531000
|  |  |  | RIVERWAY POWER COMPANY (LSE) | 788823149
|  |  |  | RWE TRADING AMERICAS INC | 0594282551000
|  |  |  | SAN BERNARD ELECTRIC CO OP (LSE) | 0089453131000
|  |  |  | SEMPRA ENERGY SOLUTIONS | 968254276
|  |  |  | SGE ENERGY MANAGEMENT LTD | 1590083951000
|  |  |  | SHARYLAND UTILITIES LP (LSE) | 1052623361000
|  |  |  | SHELL ENERGY SERVICES CO LLC | 016615689
|  |  |  | SITARA ENERGY INC (LSE) | 156110723
|  |  |  | SOLARO ENERGY MARKETING CORPORATION (LSE) | 128849358
|  |  |  | SOUTH TEXAS ELECTRIC CO OP INC (LSE) | 0038663321000
|  |  |  | SOUTH TEXAS ELECTRIC CO OP INC (LSE) AEP | 0038663321100
|  |  |  | SOUTH TEXAS ELECTRIC COOPERATIVE (CR) | 0038663321200
|  |  |  | SOUTH TEXAS ELECTRIC COOPERATIVE (POLR) | 0038663321300
|  |  |  | SOUTHWEST TEXAS ELECTRIC CO OP INC (LSE) | 0084158951000
|  |  |  | SOUTHWESTERN PUBLIC SERVICE COMPANY (LSE) | 0073697131000
|  |  |  | SPARK ENERGY LP | 037597437
|  |  |  | SPARK ENERGY LP - DBA FIRE FLY POWERED BY SPARK ENERGY | 0375974371000
|  |  |  | STAR ELECTRICITY LLC (LSE) | 201275877
|  |  |  | STAR ELECTRICITY LLC DBA STARTEX POWER (LSE) | 148055531
|  |  |  | STARLIGHT ENERGY LP | 181203170
|  |  |  | STATE POWER COMPANY INC (LSE) | 801220844
|  |  |  | STRATEGIC ENERGY LLC (LSE) | 800770810
|  |  |  | STRATEGIC ENERGY LLC DBA EXPERT ENERGY (LSE) | 8007708101000
|  |  |  | STREAM GAS AND ELECTRIC LTD (LSE) | 159008395
|  |  |  | SUEZ ENERGY MARKETING NA INC (LSE) | 9689097391000
|  |  |  | SUEZ ENERGY RESOURCES NA INC | 099668332
|  |  |  | SUEZ ENERGY RESOURCES NA INC DBA SERNA POLR | 0996683322222
|  |  |  | SWEPCO EDC (SPP ESI ID) (LSE) | 152402459
|  |  |  | SWEPCO ENERGY DELIVERY COMPANY (SWEPCO-EDC) (LSE) | 0267636721000
|  |  |  | TARA ENERGY INC. | 111950619
|  |  |  | TAYLOR ELECTRIC CO OP INC (LSE) | 0079344251000
|  |  |  | TAYLOR ELECTRIC CO OP INC-ABILENE (LSE) | 0079344251100
|  |  |  | TENASKA POWER SERVICES CO (LSE) | 015016913
|  |  |  | TENASKA POWER SERVICES CO DBA TPS I | 0150169131000
|  |  |  | TENASKA POWER SERVICES CO DBA TPS II | 0150169131100
|  |  |  | TENASKA POWER SERVICES CO DBA TPS III | 0150169131200
|  |  |  | TENASKA POWER SERVICES CO DBA TPS4 | 0150169131300
|  |  |  | TENASKA TOPS REP LP | 109518444
|  |  |  | TENASKA TOPS REP LP DBA TOPS I | 1095184441000
|  |  |  | TENASKA TOPS REP LP DBA TPS5 | 1095184445000
|  |  |  | TENASKA TOPS REP LP DBA TPS6 | 1095184446000
|  |  |  | TENASKA TOPS REP LP DBA TPS7 | 1095184447000
|  |  |  | TEXAS COMMERCIAL ENERGY (LSE) | 039711747
|  |  |  | TEXAS POWER LP (LSE) | 614848005
|  |  |  | TEXAS RETAIL ENERGY LLC (LSE) | 124238432
|  |  |  | TEXAS STAR ENERGY COMPANY | 799533091
|  |  |  | TEXAS STAR ENERGY COMPANY LNR (LSE) | 037667420
|  |  |  | TEXAS-NEW MEXICO POWER CO (LSE) | 0079294411000
|  |  |  | TEX-LA ELECTRIC CO OP OF TEXAS (BLT LSE) | 6091700301300
|  |  |  | TEX-LA ELECTRIC CO OP OF TEXAS (LSE) | 609170030
|  |  |  | TEX-LA ELECTRIC CO OP OF TEXAS INC./TPS (LSE) | 6091700301100
|  |  |  | TEX-LA ELECTRIC COOPERATIVE OF TEXAS INC./CORAL POWER (LSE) | 6091700301200
|  |  |  | TEXPO POWER LP DBA YEP | 780061300
|  |  |  | TEXREP1 LLC | 788707912
|  |  |  | TEXREP2 LLC (LSE) | 788707847
|  |  |  | TGT ENERGY LLC | 006961700
|  |  |  | THE NEW POWER CO | 364371679
|  |  |  | THE ROYAL BANK OF SCOTLAND PLC (LSE) | 229123146
|  |  |  | TRIEAGLE ENERGY LP (LSE) | 124769063
|  |  |  | TRIEAGLE ENERGY LP DBA EAGLE ENERGY | 1247690631100
|  |  |  | TRIEAGLE ENERGY LP DBA PILOT ENERGY | 1247690631200
|  |  |  | TRIEAGLE ENERGY LP DBA POWER HOUSE ENERGY | 1247690631300
|  |  |  | TRIEAGLE ENERGY LP DBA TRIEAGLE ENERGY SERVICES | 1247690631000
|  |  |  | TRIZEC HOLDINGS INC | 113632207
|  |  |  | TRUE ELECTRIC LLC | 793874822
|  |  |  | TXI POWER CO | 041083403
|  |  |  | TXU ELECTRIC CO (LSE) | 1039940671000
|  |  |  | TXU ENERGY | 1733370281000
|  |  |  | TXU SESCO CO (LSE) | 0079280961000
|  |  |  | TXU SESCO ENERGY SERVICES COMPANY (SUBLSE) | 1733370281400
|  |  |  | UBS AG LONDON BRANCH (LSE) | 4872019151000
|  |  |  | UG&E TEXAS INC (LSE) | 243434292
|  |  |  | URBAN ENERGY SOURCE LLC | 144737041
|  |  |  | USAVE ENERGY SERVICES INC (LSE) | 128490062
|  |  |  | UTILITY CHOICE LLC DBA UTILITY CHOICE ELECTRIC (LSE) | 834401601
|  |  |  | VARTEC TELECOM INC DBA VARTEC ENERGY (LSE) | 603613605
|  |  |  | VEGA RESOURCES LLC DBA AMIGO ENERGY | 141047543
|  |  |  | W POWER AND LIGHT LP (LSE) | 156766037
|  |  |  | WEATHERFORD MUNICIPAL UTILITY SYSTEM (LSE) | 0817196271000
|  |  |  | WEST TEXAS UTILITIES TX SPP (LSE) | 0536933881000
|  |  |  | WESTERN FARMERS ELECTRIC COOPERATIVE (LSE) | 072862407
|  |  |  | WTU ENERGY DELIVERY COMPANY (WTU-EDC) (LSE) | 0079233111000
|  |  |  | WTU RETAIL ENERGY DBA 1300 | 0177412941300
|  |  |  | WTU RETAIL ENERGY DBA 1400 | 0177412941400
|  |  |  | WTU RETAIL ENERGY LP (LSE) | 017741294
|  |  |  | WTU RETAIL ENERGY LP 1100 | 0177412941100
|  |  |  | WTU RETAIL ENERGY LP DBA WTU | 0177412941200
|  |  |  | XERS INC | 007346922
|  |  |  | YOUNG ENERGY (LSE) | 189069284
|  |  |  | Not Listed | 0

## Ownership - GEN
ERCOT Confidential
Representation of Facility Output
This worksheet tab applies to all Generation Resources. This tab identifies the Resource Entities that represent the output of the facility to ERCOT.
Please complete this section and select RETURN TO MAP
GENERATION RESOURCES (non-wind, non-CC)
Complete this section ONLY if a single Resource Entity (RE) represents 100% of all units.
| Resource Owner Data | Table: | DB Field: | Rules: | Source | APPLICATION
| Resource Entity Name | SITECODE | SITE_NAME | 1. Conditionally Required if single entity represents the Resource. 2. Data type: Character 3. No special characters except spaces. | Guide | EMS, SETTLEMENTS, NMMS
| Resource Duns Number | SITECODE | RE_DUNS | 1. Conditionally Required if single entity represents the Resource. 2. Either 9 or 13 digit number | Guide | EMS, SETTLEMENTS, NMMS
Complete the following sections if units at the same site are represented by different Resource Entites (RE) or represented as Split-Generation Resources.
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS

## Ownership - CC
ERCOT Confidential
Representation of Facility Output
This worksheet tab applies to all Combined Cycle Generation Resources. This tab identifies the Resource Entities that represent the output of the facility to ERCOT.
Please complete this section and select RETURN TO MAP
CC1
| Complete this section if a single Resource Entity (RE) represents 100% of all units. | Table: | DB Field: | Rules: | Source | APPLICATION
#REF!
| Resource Entity Name | SITECODE | SITE_NAME | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. No special characters except spaces | Guide | EMS, SETTLEMENTS, NMMS
| Resource Duns Number | SITECODE | RE_DUNS | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. Either 9 or 13 digit number | Guide | EMS, SETTLEMENTS, NMMS
CC2
Complete this section if a single Resource Entity (RE) represents 100% of all units.
#REF!
| Resource Entity Name | SITECODE | SITE_NAME | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. No special characters except spaces | Guide | EMS, SETTLEMENTS, NMMS
| Resource Duns Number | SITECODE | RE_DUNS | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. Either 9 or 13 digit number | Guide | EMS, SETTLEMENTS, NMMS
CC3
Complete this section if a single Resource Entity (RE) represents 100% of all units.
#REF!
| Resource Entity Name | SITECODE | SITE_NAME | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. No special characters except spaces | Guide | EMS, SETTLEMENTS, NMMS
| Resource Duns Number | SITECODE | RE_DUNS | 1. Conditionally Required if Resource Entity represents 100% of all units. 2. Either 9 or 13 digit number | Guide | EMS, SETTLEMENTS, NMMS

## Ownership - WIND
ERCOT Confidential
Representation of Facility Output
This worksheet tab applies to all WIND Generation Resources. This tab identifies the Resource Entities that represent the output of the facility to ERCOT.
Please complete this section and select RETURN TO MAP
WIND GENERATION RESOURCES
Complete this section ONLY if a single Resource Entity (RE) represents 100% of all units.
| Resource Owner Data | Table: | DB Field: | Rules: | Source | APPLICATION
| Resource Entity Name | SITECODE | SITE_NAME | 1. Conditionally Required if single entity represents the Resource. 2. Data type: Character 3. No special characters except spaces. | Guide | EMS, SETTLEMENTS, NMMS
| Resource Duns Number | SITECODE | RE_DUNS | 1. Conditionally Required if single entity represents the Resource. 2. Either 9 or 13 digit number | Guide | EMS, SETTLEMENTS, NMMS
Complete the following sections if units at the same site are represented by different Resource Entites (RE) or represented as Split-Generation Resources.
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS
#REF!
| Market Participant (Resource) Name | OWNERSHIP | MKT_PRTCPT | 1. Conditionally Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Data type: character. | Guide | EMS, SETTLEMENTS, NMMS
| Market Participant (Resource) Duns Number | OWNERSHIP | MKT_PRTCPT_DUNS | 1. Conditional Required if units at the same site are represented by different Resource Entities (RE) or represented as Split-Generation Resources. 2. Either 9 or 13 digit number 3. RE Duns# should be unique for different Owner RE's for a Jointly Owned Unit | Guide | EMS, SETTLEMENTS, NMMS
| Fixed Ownership % | OWNERSHIP | FIX_OWNRSHP_PCT | 1. Sum of the Ownership percentage should be 100. 2. Up to 4 decimal places only are valid (limit submission to 4 places after the point) | SME | EMS, SETTLEMENTS, NMMS
| Master Owner (Y or N) | OWNERSHIP | MASTR_OWNR_FLG | 1. Select from Y or N. 2. Required 3. Must select ‘Y’ for one resource entity for each unit on Split Generation Resources ( 'Y' identifies the Master Owner) | Guide | EMS, SETTLEMENTS, NMMS

## CC1 Config
ERCOT CONFIDENTIAL
Combined Cycle Configurations
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating configurations.
Please complete this section and select RETURN TO MAP
CC1 | Resource Name (Unit Code) | Unit Type | Table: | DB Field: | Rules: | Source | APPLICATION
|  |  | Configuration | UNIT_CODE | 1. Not null. 2. Data type: Character. 3. Must match unit Mnemonic for CC Unit | Guide | EMS, MMS, NMMS
|  |  | Configuration | CONFIG_TYPE | 1. Not null. 2. Data type: Character. 3. Must match physical unit type from unit info CC | Guide | EMS, MMS, NMMS
Number of units and MW increase from left to right.

## CC2 Config
ERCOT CONFIDENTIAL
Combined Cycle Configurations
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating configurations.
Please complete this section and select RETURN TO MAP
CC2 | Resource Name (Unit Code) | Unit Type | Table: | DB Field: | Rules: | Source | APPLICATION
|  |  | Configuration | UNIT_CODE | 1. Not null. 2. Data type: Character. 3. Must match unit Mnemonic for CC Unit | Guide | EMS, MMS, NMMS
|  |  | Configuration | CONFIG_TYPE | 1. Not null. 2. Data type: Character. 3. Must match physical unit type from unit info CC | Guide | EMS, MMS, NMMS
Number of units and MW increase from left to right.

## CC3 Config
ERCOT CONFIDENTIAL
Combined Cycle Configurations
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating configurations.
Please complete this section and select RETURN TO MAP
CC3 | Resource Name (Unit Code) | Unit Type | Table: | DB Field: | Rules: | Source | APPLICATION
|  |  | Configuration | UNIT_CODE | 1. Not null. 2. Data type: Character. 3. Must match unit Mnemonic for CC Unit | Guide | EMS, MMS, NMMS
|  |  | Configuration | CONFIG_TYPE | 1. Not null. 2. Data type: Character. 3. Must match physical unit type from unit info CC | Guide | EMS, MMS, NMMS
Number of units and MW increase from left to right.

## CC1 Transitions
ERCOT CONFIDENTIAL
Combined Cycle Transitions
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating transitions.
Please complete this section and select RETURN TO MAP
CC1 | To From .
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
| 1 | #REF! | TRANSITIONS | CONFIGCODE_FROM | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF! | TRANSITIONS | CONFIGCODE_TO | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!

## CC2 Transitions
ERCOT CONFIDENTIAL
Combined Cycle Transitions
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating transitions.
Please complete this section and select RETURN TO MAP
CC2 | To From .
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
| 1 | #REF! | TRANSITIONS | CONFIGCODE_FROM | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF! | TRANSITIONS | CONFIGCODE_TO | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!

## CC3 Transitions
ERCOT CONFIDENTIAL
Combined Cycle Transitions
This worksheet tab applies to all Combined Cycle Generation Resources. This tab defines the operating transitions.
Please complete this section and select RETURN TO MAP
CC3 | To From .
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
| 1 | #REF! | TRANSITIONS | CONFIGCODE_FROM | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF! | TRANSITIONS | CONFIGCODE_TO | 1.If CC1 Transitions to CC2 , CC2 should be registered as a Configuration. 2.Each configuration in CC1 Transitions including Offline can be reached. Each configuration in CC1 Transitions including Offline can reach at least one of the other configurations including Offline . 3.Values allowed are X for Main Transition , A for Alternate Transition ,Null for Non Transition 4. 1.If a RARF is submitted that does not have the first Transition from OFFLINE, Generate an ERROR. 5. Generate a Warning if the Transitions skip. For instance the transitions table has ‘Offline’ to ‘CC1_2’ and so it skips CC1_1. This is an acceptable possibility, but the resource needs to be notified of it because they would not be in RUC until the CC1_2 configuration, in this case would only be in RUC with both units available, not just the single unit associated to CC1_1. 6) Generate a Warning if the Transistion is missing for a Configuration | Jamil Daouk | EMS, MMS, NMMS
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!
| #REF! | #REF!

## Planning - GEN
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides planning information for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GEN (non-wind, non-CC)
| Generator Details | Labels | Table: | DB Field: | Rules: | Source | APPLICATION
| What is the MVA base that the following data is based on? | MVA | GENERATION | MVABASE | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | Raja Kakarla | MMS, NMMS, PLANNING
| What is the kV base that the following data is based on? | KV | GENERATION | KVBASE | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Subtransient reactance, X"di |  | GENERATION | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Transient reactance, X'di |  | GENERATION | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Positive Sequence Z | R in p.u. | GENERATION | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | GENERATION | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Negative Sequence Z | R in p.u. | GENERATION | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | GENERATION | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Zero Sequence Z | R in p.u. | GENERATION | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | GENERATION | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Generator Auxiliary Load | Labels
| Average Amount of Auxiliary Real Power | MW | GENERATION | AUX_MWTOTAL | 1) This field is optional 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | Raja Kakarla | MMS, NMMS, PLANNING
| Average Amount of Auxiliary Reactive Power | MVAR | GENERATION | AUX_MVARTOTAL | 1) This field is optional 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | Raja Kakarla | MMS, NMMS, PLANNING
Generation Auxiliary Load Characteristics for MW Load
| Large Motor, percent of total MW load | % | GENERATION | AUXMW_LARGEMTR_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | Raja Kakarla | MMS, NMMS, PLANNING
| Small Motor, percent of total MW load | % | GENERATION | AUXMW_SMALLMTR_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | Raja Kakarla | MMS, NMMS, PLANNING
| Resistive (Heating) Load, percent of total MW load | % | GENERATION | AUXMW_RESISTIVE_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Discharge Lighting, percent of total MW load | % | GENERATION | AUXMW_DISCHARGE_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Other, percent of total MW load | % | GENERATION | AUXMW_OTHER_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
Generation Auxiliary Load Characteristics for MVAR Load
| Large Motor, percent of total MVAR load | % | GENERATION | AUXMVAR_LARGEMTR_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | Raja Kakarla | MMS, NMMS, PLANNING
| Small Motor, percent of total MVAR load | % | GENERATION | AUXMVAR_SMALLMTR_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | Raja Kakarla | MMS, NMMS, PLANNING
| Discharge Lighting, percent of total MVAR load | % | GENERATION | AUXMVAR_DISCHARGE_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Other, percent of total MVAR load | % | GENERATION | AUXMVAR_OTHER_PCT | 1) This field is optional 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING

## Planning - CC
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides planning information for Combined Cycle generation resources. This tab is UNIT specific for all CC units.
Please complete this section and select RETURN TO MAP
CC1
| Generator Details |  | Table: | DB Field: | Rules: | Source | APPLICATION
| What is the MVA base that the following data is based on? | MVA | CCUNIT | MVABASE | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating. | Raja Kakarla | MMS, NMMS, PLANNING
| What is the kV base that the following data is based on? | KV | CCUNIT | KVBASE | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE > 40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Subtransient reactance, X"di |  | CCUNIT | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Transient reactance, X'di |  | CCUNIT | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Positive Sequence Z | R in p.u. | CCUNIT | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | CCUNIT | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Negative Sequence Z | R in p.u. | CCUNIT | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning when value is > 1.0 P.U | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | CCUNIT | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Zero Sequence Z | R in p.u. | CCUNIT | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1. Generate a Warning ONLY when value is > 1.0 P.U | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | CCUNIT | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) ] *Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab)] | Raja Kakarla | MMS, NMMS, PLANNING
| Generator Auxiliary Load |  | CCUNIT
| Average Amount of Auxiliary Real Power | MW | CCUNIT | AUX_MWTOTAL | 1) This field is required. 2) Data type is float 3) Value must be < Parameters - GEN - High Reasonability Limit 4) Warn if value > (High Reasonability Limit) * .75 5) Error if value > (High Reasonability Limit) * .66 | Raja Kakarla | MMS, NMMS, PLANNING
| Average Amount of Auxiliary Reactive Power | MVAR | CCUNIT | AUX_MVARTOTAL | 1) This field is required 2) Data type is Float 3) Value must be < Reactive Capability - GEN - Maximum Lagging Operating Capability (MVAR) 4) Warn if value > ( Maximum Lagging Operating Capability) * .75 5) Error if value > ( Maximum Lagging Operating Capability) * .66 | Raja Kakarla | MMS, NMMS, PLANNING
Generation Auxiliary Load Characteristics for MW Load
| Large Motor, percent of total MW load | % | CCUNIT | AUXMW_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | Raja Kakarla | MMS, NMMS, PLANNING
| Small Motor, percent of total MW load | % | CCUNIT | AUXMW_SMALLMTR_PCT | This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | Raja Kakarla | MMS, NMMS, PLANNING
| Resistive (Heating) Load, percent of total MW load | % | CCUNIT | AUXMW_RESISTIVE_PCT | This field is CONDITIONAL (Not required when Average Amount Of Real Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Discharge Lighting, percent of total MW load | % | CCUNIT | AUXMW_DISCHARGE_PCT | This field is CONDITIONAL (Not required when Average Amount Of Real Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Other, percent of total MW load | % | CCUNIT | AUXMW_OTHER_PCT | This field is CONDITIONAL (Not required when Average Amount Of Real Power value zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
Generation Auxiliary Load Characteristics for MVAR Load
| Large Motor, percent of total MVAR load | % | CCUNIT | AUXMVAR_LARGEMTR_PCT | 1) This field is CONDITIONAL (Not required when Average Amount Of Reactive Power VALUE is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% 4) Motors connected at >= 2400V / 4160V are large motors | Raja Kakarla | MMS, NMMS, PLANNING
| Small Motor, percent of total MVAR load | % | CCUNIT | AUXMVAR_LARGEMTR_PCT | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power Value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MW Load) = 100% 4) Motors connected at < 2400V / 4160V are small motors | Raja Kakarla | MMS, NMMS, PLANNING
| Discharge Lighting, percent of total MVAR load | % | CCUNIT | AUXMVAR_DISCHARGE_PCT | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
| Other, percent of total MVAR load | % | CCUNIT | AUXMVAR_OTHER_PCT | This field is CONDITIONAL (Not required when Average Amount Of Reactive Power value is zero) 2) Data Type must be percent 3) SUM(All Generation Auxiliary Load Characteristics for MVAR Load) = 100% | Raja Kakarla | MMS, NMMS, PLANNING
CC2
| 18 | 16
#REF!
#REF!
#REF!
18
#REF!
#REF!
#REF!
18
#REF!
#REF!
#REF!

## Planning - Wind
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides planning information for WIND generation resources. This tab is UNIT specific for all Wind units.
Please complete this section and select RETURN TO MAP
Wind
| Field Description | Labels | Table: | DB Field: | Rules: | Source | APPLICATION
| What is the MVA base that the following data is based on? | MVA | WIND | MVABASE | 1) This field is required 2) Value must be Float 3) Generate a Warning if MVABASE > 2500 4)[ If MVABASE value is within +/- 25% range of Unit Name Plate Rating] OR [MVABASE value = 100, then it is OK.If MVABASE value is outside the +/- 25% range of Unit Name Plate Rating, then Generate a Warning that the MVABSE is outside the typical +/- 25% variation of unit name plate rating | Raja Kakarla | MMS, NMMS, PLANNING
| What is the kV base that the following data is based on? | KV | WIND | KVBASE | 1) This field is required 2) Value must be >0 and <1000 3) Generate a Warning if KVBASE>40 4) If KVBASE value is within +/- 25% range of Unit KV value in the unit-information tab then it is OK.If If KVBASE value is outside the typical +/- 25% variation of Unit KV value in the unit-information tab then Generate a Warning that the KVBASE is outside the typical +/- 25% variation of Unit KV value | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Subtransient reactance, X"di |  | WIND | DIRECT_AXIS_SUBSTNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between -1 and 1 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value.(* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Direct Axis Transient reactance, X'di |  | WIND | DIRECT_AXIS_TRANSNT_REACTANCE | 1) This field is required and Data type is float 2) Value must be between 0 and 2 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.12 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.60 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Positive Sequence Z | R in p.u. | WIND | POSITIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | WIND | POSITIVE_SEQ_Z_X_PU | 1) This field is required and Data type is numeric 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.50 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Negative Sequence Z | R in p.u. | WIND | NEGATIVE_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | WIND | NEGATIVE_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.07 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.65 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING
| Zero Sequence Z | R in p.u. | WIND | ZERO_SEQ_Z_R_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 1 . Generate a Warning when value is > 1.0 P.U | Raja Kakarla | MMS, NMMS, PLANNING
|  | X in p.u. | WIND | ZERO_SEQ_Z_X_PU | 1) This field is required and Data type is float 2) Value must be between 0 and 100 3) Generate a Warning if the value entered is not within the calculated typical lower and upper limits. Warning should include the entered value and the typical limit value. (* Required Calculation of Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Lower Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.01 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) Required Calculation of Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base: Upper Limit Typical Reactance (X) on the Planning tab specified MVA and KV base = 0.24 * [(Unit Generating Voltage KV from the Unit Info tab / KV Base entered in row 8 of the Planning tab)^2] * (MVA base entered in row 7 of the Planning tab / Nameplate Rating MVA from the Unit Info tab) | Raja Kakarla | MMS, NMMS, PLANNING

## Protection - GEN
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides protection information for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GEN (non-wind, non-CC)
| Plant Voltage Protection | Label | Table: | DB Field: | Rules: | Source | APPLICATION
| Instantaneous Undervoltage Trip | p.u. | GENERATION | UVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 1 | p.u. | GENERATION | UVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | GENERATION | UVOLT_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 2 | p.u. | GENERATION | UVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | GENERATION | UVOLT_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 3 | p.u. | GENERATION | UVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | GENERATION | UVOLT_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 4 | p.u. | GENERATION | UVOLT_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | GENERATION | UVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overvoltage Trip | p.u. | GENERATION | OVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 1 | p.u. | GENERATION | OVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | GENERATION | OVOLT_TRIP_TIME1 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 2 | p.u. | GENERATION | OVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | GENERATION | OVOLT_TRIP_TIME2 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 3 | p.u. | GENERATION | OVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | GENERATION | OVOLT_TRIP_TIME3 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 4 | p.u. | GENERATION | OVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | GENERATION | OVOLT_TRIP_TIME4 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Plant Frequency Protection | Label
| Instantaneous Underfrequency Trip | Hz | GENERATION | UFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla
| Underfrequency 1 | Hz | GENERATION | UFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | GENERATION | UFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 2 | Hz | GENERATION | UFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | GENERATION | UFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 3 | Hz | GENERATION | UFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | GENERATION | UFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 4 | Hz | GENERATION | UFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | GENERATION | UFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overfrequency Trip | Hz | GENERATION | OFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla | NMMS, PLANNING
| Overfrequency 1 | Hz | GENERATION | OFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | GENERATION | OFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 2 | Hz | GENERATION | OFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | GENERATION | OFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 3 | Hz | GENERATION | OFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | GENERATION | OFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 4 | Hz | GENERATION | OFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | GENERATION | OFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Breaker Interruption Time | Label
| Breaker Interruption Time | cycles | GENERATION | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | Raja Kakarla | NMMS, PLANNING

## Protection - CC
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides protection information for Combined Cycle generation resources. This tab is UNIT specific for all CC.
Please complete this section and select RETURN TO MAP
CC1
| Plant Voltage Protection | Label | Table: | DB Field: | Rules: | Source | APPLICATION
| Instantaneous Undervoltage Trip | p.u. | CCUNIT | UVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 1 | p.u. | CCUNIT | UVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | CCUNIT | UVOLT_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 2 | p.u. | CCUNIT | UVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | CCUNIT | UVOLT_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 3 | p.u. | CCUNIT | UVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | CCUNIT | UVOLT_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 4 | p.u. | CCUNIT | UVOLT_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | CCUNIT | UVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overvoltage Trip | p.u. | CCUNIT | OVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 1 | p.u. | CCUNIT | OVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | CCUNIT | OVOLT_TRIP_TIME1 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 2 | p.u. | CCUNIT | OVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | CCUNIT | OVOLT_TRIP_TIME2 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 3 | p.u. | CCUNIT | OVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | CCUNIT | OVOLT_TRIP_TIME3 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 4 | p.u. | CCUNIT | OVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | CCUNIT | OVOLT_TRIP_TIME4 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Instantaneous Underfrequency Trip | Hz | CCUNIT | UFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla | NMMS, PLANNING
| Underfrequency 1 | Hz | CCUNIT | UFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | CCUNIT | UFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 2 | Hz | CCUNIT | UFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | CCUNIT | UFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 3 | Hz | CCUNIT | UFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | CCUNIT | UFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 4 | Hz | CCUNIT | UFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | CCUNIT | UFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overfrequency Trip | Hz | CCUNIT | OFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla | NMMS, PLANNING
| Overfrequency 1 | Hz | CCUNIT | OFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | CCUNIT | OFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 2 | Hz | CCUNIT | OFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | CCUNIT | OFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 3 | Hz | CCUNIT | OFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | CCUNIT | OFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 4 | Hz | CCUNIT | OFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | CCUNIT | OFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Breaker Interruption Time | cycles | CCUNIT | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | Raja Kakarla | NMMS, PLANNING
CC2
| 35 | 34
#REF!
#REF!
#REF!
35
#REF!
#REF!
#REF!
35
#REF!
#REF!
#REF!

## Protection - WIND
ERCOT Confidential |  | RETURN TO MAP
Planning Information
This worksheet tab provides protection information for WIND generation resources. This tab is UNIT specific for all Wind.
Please complete this section and select RETURN TO MAP
WIND
| Plant Voltage Protection | Label | Table: | DB Field: | Rules: | Source | APPLICATION
| Instantaneous Undervoltage Trip | p.u. | WIND | UVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 1 | p.u. | WIND | UVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | WIND | UVOLT_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 2 | p.u. | WIND | UVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | WIND | UVOLT_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 3 | p.u. | WIND | UVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | WIND | UVOLT_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Undervoltage 4 | p.u. | WIND | UVOLT_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3) Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” – Plant Voltage protection tab 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | WIND | UVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7) Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overvoltage Trip | p.u. | WIND | OVOLT_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float 3)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 1 | p.u. | WIND | OVOLT_TRIP_VOLT1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | WIND | OVOLT_TRIP_TIME1 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 2 | p.u. | WIND | OVOLT_TRIP_VOLT2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | WIND | OVOLT_TRIP_TIME2 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 3 | p.u. | WIND | OVOLT_TRIP_VOLT3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | WIND | OVOLT_TRIP_TIME3 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Overvoltage 4 | p.u. | WIND | OVOLT_TRIP_VOLT4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when this field is blank and instantaneous value is not entered. 2) Data type must be Float 3)Undervoltage 1 is required, Undervoltage 2,3,4 are optional 4)Voltage settings should exist if time settings are defined” 5)This should be expressed in p.u values. Generate an Error if it is <=0 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | WIND | OVOLT_TRIP_TIME4 | 1) This field is conditional, Not required if Instantaneous setting is defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time settings should exist if time delayed under/voltage settings are defined” – Plant Voltage protection tab “Time setting are dependent on voltage settings/can not have time settings without voltage settings”- Plant Voltage Protection Tab 7)This should be expressed in p.u values. Generate an Error if it is <1 . Generate a Warning if it is >396 p.u | Raja Kakarla | NMMS, PLANNING
| Instantaneous Underfrequency Trip | Hz | WIND | UFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla | NMMS, PLANNING
| Underfrequency 1 | Hz | WIND | UFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | WIND | UFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 2 | Hz | WIND | UFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | WIND | UFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 3 | Hz | WIND | UFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | WIND | UFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Underfrequency 4 | Hz | WIND | UFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined-Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= ERROR. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Underfrequency 1 is required, Underfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. 7)Frequency settings should exist if time settings are defined’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | WIND | UFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined- Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)Time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Instantaneous Overfrequency Trip | Hz | WIND | OFREQ_TRIP_INSTANT | 1) This field is optional 2) Data type must be Float | Raja Kakarla | NMMS, PLANNING
| Overfrequency 1 | Hz | WIND | OFREQ_TRIP_HZ1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 1 | sec | WIND | OFREQ_TRIP_TIME1 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 2 | Hz | WIND | OFREQ_TRIP_HZ2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 2 | sec | WIND | OFREQ_TRIP_TIME2 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 3 | Hz | WIND | OFREQ_TRIP_HZ3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 3 | sec | WIND | OFREQ_TRIP_TIME3 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Overfrequency 4 | Hz | WIND | OFREQ_TRIP_HZ4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)Frequency Settings Range is defined as below. 55 – 65 Hz= OK, <55 Hz = ERROR, >65 Hz= WARNING. Any number of stages can be defined as long as the time increments are in the following order. Time1>Time2>Time3>Time4.If there are any instantaneous settings defined, then the time should be zero 4) Overfrequency 1 is required, Overfrequency 2,3,4 are optional 5)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 6)Frequency settings should exist if time settings are defined’’ – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Time 4 | sec | WIND | OFREQ_TRIP_TIME4 | 1) This field is required if Instantaneous setting is not defined. Generate a warning ONLY when stage1 settings are blank and none of the protection settings (stages2,3,4) filled when instantaneous value is blank. 2) Data type must be Float 3)TIME 1 = required,TIME2, TIME3, TIME4 are optional 4)User can fill in a Stage provided the previous stage exists. For example TIME4 stage only exists if there is a TIME3 stage and a TIME2 stage 5) Time 1 > Time 2 > Time 3 >Time 4 (time points must decrement) 6)time setting is dependent on frequency setting, cannot have time setting with out frequency setting 7)If the instantaneous setting is defined then Time1 is not required. Time 1 is only required if they have time delayed under or over frequency settings. Each set should have at a minimum of 1 stage (TIME 1 = required) if instantaneous setting is blank OR time delayed under or over frequency settings defined 8)Time settings should exist if time delayed under/over frequencies defined’ – Plant Frequency Protection tab “Time setting are dependent on frequency settings/can not have time settings without freq settings” – Plant Frequency Protection tab | Raja Kakarla | NMMS, PLANNING
| Breaker Interruption Time | cycles | WIND | BREAKER_INTERRUP | 1) this field is required 2) Data type must be Integer | Raja Kakarla | NMMS, PLANNING

## SubSync - GEN
ERCOT Confidential
Planning Information
This worksheet tab provides subsynchronous resonance planning information for generation resources. This tab is UNIT specific for all non-Wind and non-CC.
Please complete this section and select RETURN TO MAP
GEN (non-wind, non-CC)
| Subsynchronous Resonance - Mass 1 | Table: | DB Field: | Rules: | Source | APPLICATION
| Name of Mass 1 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 2
| Name of Mass 2 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 1 and 2 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 3
| Name of Mass 3 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 2 and 3 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 4
| Name of Mass 4 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 3 and 4 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 5
| Name of Mass 5 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 4 and 5 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
For Additional Masses - please send separate file.

## SubSync - CC
ERCOT Confidential
Planning Information
This worksheet tab provides subsynchronous resonance planning information for Combined Cycle generation resources. This tab is UNIT specific for CC.
Please complete this section and select RETURN TO MAP
CC1
| Subsynchronous Resonance - Mass 1 | Table: | DB Field: | Rules: | Source | APPLICATION
| Name of Mass 1 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 2
| Name of Mass 2 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 1 and 2 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 3
| Name of Mass 3 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 2 and 3 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 4
| Name of Mass 4 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 3 and 4 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
Subsynchronous Resonance - Mass 5
| Name of Mass 5 | SUBSYNC | NAME | None | Raja Kakarla | PLANNING
| Mass Inertia | SUBSYNC | MASS_INERTIA | None | Raja Kakarla | PLANNING
| Inertia units | SUBSYNC | INERTIA_UNITS | None | Raja Kakarla | PLANNING
| Associated damping | SUBSYNC | ASST_DMPG | None | Raja Kakarla | PLANNING
| Damping units | SUBSYNC | DMPG_UNITS | None | Raja Kakarla | PLANNING
| Stiffness between Masses 4 and 5 | SUBSYNC | STFNS_BTWN_MASSES | None | Raja Kakarla | PLANNING
| Stiffness units | SUBSYNC | STFNS_UNITS | None | Raja Kakarla | PLANNING
For Additional Masses - please send separate file.
CC2

## Private Network
ERCOT Confidential |  | RETURN TO MAP
Private Network - Site and Unit Information
This worksheet tab applies to all Private Use Networks.
Please complete this section and select RETURN TO MAP
SITE
| PRIVATE NETWORK - SITE INFORMATION | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source |  | APPLICATION
| Private Network? | Y/N |  | SITECODES |  | PRIVATE_NTWK_SITE_FLG |  | 1. Select from Y or N. 2. Not null |  | Guide |  | EMS
| Average Amount of Self-Serve private load | MW |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | SITECODES |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' |  | Guide |  | EMS
Load Characteristics:
| Load Characteristics for MW Load | [10 empty] | MMS
| Large Motor, percent of total MW load | % |  | SITECODES |  | PUN_MW_LARGEMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Small Motor, percent of total MW load | % |  | SITECODES |  | PUN_MW_SMALLMTR_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Resistive (Heating) Load, percent of total MW load | % |  | SITECODES |  | PUN_MW_RESISTIVE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Discharge Lighting, percent of total MW load | % |  | SITECODES |  | PUN_MW_DISCHARGE_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Other, percent of total MW load | % |  | SITECODES |  | PUN_MW_OTHER_PCT |  | Large Motor, percent of total MW load+Small Motor, percent of total MW load+Resistive (Heating) Load, percent of total MW load+ Discharge Lighting, percent of total MW load+Other, percent of total MW load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
Load Characteristics for MVAR Load
| Large Motor, percent of total MVAR load | % |  | SITECODES |  | PUN_MVAR_LARGEMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR loadDischarge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Small Motor, percent of total MVAR load | % |  | SITECODES |  | PUN_MVAR_SMALLMTR_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR loadDischarge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Discharge Lighting, percent of total MVAR load | % |  | SITECODES |  | PUN_MVAR_DISCHARGE_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR loadDischarge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
| Other, percent of total MVAR load | % |  | SITECODES |  | PUN_MVAR_OTHER_PCT |  | Large Motor, percent of total MVAR load+ Small Motor, percent of total MVAR loadDischarge Lighting, percent of total MVAR load+Other, percent of total MVAR load = 100. This field is conditional. Required if Private Network flag is 'Y' |  | SME |  | MMS
GEN |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| PRIVATE NETWORK - Unit Information | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source
| Average Amount of Self-Serve private load | MW |  | GENERATION |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | GENERATION |  | AVG_LD_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | GENERATION |  | NET_INTERCHNG_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | GENERATION |  | NET_INTERCHNG_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | GENERATION |  | GROSS_CAPBLTY_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | GENERATION |  | GROSS_CAPBLTY_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
| If Unit trips, does Load trip? | Y/N |  | GENERATION |  | LOAD_TRIP_FLG |  | Select from Y or N. |  | Guide |  | EMS
| If yes, approximate percentage of Load that will trip? | % |  | GENERATION |  | LOAD_TRIP_PCT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' non-cc non-wind generation resource' |  | Guide |  | EMS
CC1 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| PRIVATE NETWORK - Unit Information | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source
| Average Amount of Self-Serve private load | MW |  | GENERATION |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | GENERATION |  | AVG_LD_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | GENERATION |  | NET_INTERCHNG_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | GENERATION |  | NET_INTERCHNG_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | GENERATION |  | GROSS_CAPBLTY_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | GENERATION |  | GROSS_CAPBLTY_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| If Unit trips, does Load trip? | Y/N |  | GENERATION |  | LOAD_TRIP_FLG |  | Select from Y or N. |  | Guide |  | EMS
| If yes, approximate percentage of Load that will trip? | % |  | GENERATION |  | LOAD_TRIP_PCT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
CC2 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| PRIVATE NETWORK - Unit Information | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source
| Average Amount of Self-Serve private load | MW |  | GENERATION |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | GENERATION |  | AVG_LD_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | GENERATION |  | NET_INTERCHNG_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | GENERATION |  | NET_INTERCHNG_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | GENERATION |  | GROSS_CAPBLTY_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | GENERATION |  | GROSS_CAPBLTY_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| If Unit trips, does Load trip? | Y/N |  | GENERATION |  | LOAD_TRIP_FLG |  | Select from Y or N. |  | Guide |  | EMS
| If yes, approximate percentage of Load that will trip? | % |  | GENERATION |  | LOAD_TRIP_PCT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
CC3 |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| PRIVATE NETWORK - Unit Information | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source
| Average Amount of Self-Serve private load | MW |  | GENERATION |  | AVG_LD_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | GENERATION |  | AVG_LD_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | GENERATION |  | NET_INTERCHNG_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | GENERATION |  | NET_INTERCHNG_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | GENERATION |  | GROSS_CAPBLTY_MW_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | GENERATION |  | GROSS_CAPBLTY_MVAR_UNIT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
| If Unit trips, does Load trip? | Y/N |  | GENERATION |  | LOAD_TRIP_FLG |  | Select from Y or N. |  | Guide |  | EMS
| If yes, approximate percentage of Load that will trip? | % |  | GENERATION |  | LOAD_TRIP_PCT |  | Conditionally Required if Private Network flag is 'Y' and Generation Resource Type is ' Combined Cycle Units' |  | Guide |  | EMS
WIND |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| PRIVATE NETWORK - Unit Information | Labels |  | Table: |  | DB Field: |  | Rules: |  | Source
| Average Amount of Self-Serve private load | MW |  | WIND |  | AVG_LD_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| Average Amount of Self-Serve private reactive load | MVAR |  | WIND |  | AVG_LD_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| Expected Typical Private Network Net Interchange | MW |  | WIND |  | NET_INTERCHNG_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| Expected Typical Private Network Net Reactive Interchange | MVAR |  | WIND |  | NET_INTERCHNG_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| Private Network Gross Unit Capability | MW |  | WIND |  | GROSS_CAPBLTY_MW_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| Private Network Gross Unit Reactive Capability | MVAR |  | WIND |  | GROSS_CAPBLTY_MVAR_UNIT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS
| If Unit trips, does Load trip? | Y/N |  | WIND |  | LOAD_TRIP_FLG |  | Select from Y or N. |  | Guide |  | EMS
| If yes, approximate percentage of Load that will trip? | % |  | WIND |  | LOAD_TRIP_PCT |  | This field is conditional. Required if Private Network flag is 'Y' and Generation Resource Type is ' Wind unit' |  | Guide |  | EMS

## Line Data
ERCOT Confidential
Line Data
SITE |  |  |  | Table: | DB Field: | Rules: | Source | APPLICATION
GENERAL
| Description of change |  |  | LINE | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| LINE (any length) |  | Labels
| ERCOT Line Name |  |  | LINE | ERCOT_LINE_NAME | 1) This field is required 2) This field may not have any special characters, except an underscore "_" and a dash "-" 3) Warn if > 14 characters. Warning! ERCOT Line Name () should not be > 14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Line Voltage Level kV |  | kV | LINE | LINE_VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value must be < 345 4) The value must be > 1 | Joel Koepke | NMMS
| TO Station | ERCOT Station Code Mnemonic |  | LINE | ERCOT_CODE_TO | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | Joel Koepke | NMMS
|  | Internal Line | Y/N | LINE | INTERNAL_LINE_TO_FLG | 1) This field is required 2) Value must be of the following: 'Y', 'N' | Joel Koepke | NMMS
|  | TSP Name |  | LINE | TSPNAME_TO | 1) This field is conditionally required if TO STATION - Internal Line - 'N' 2) This field must match ERCOT records (drop down in RARF) | Joel Koepke | NMMS
|  | Connected Device Name(s) |  | LINE_DEVICES | DEVICE_NAME | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  | Bus Number (PTI Bus Number) | (integer) | LINE | BUS_NUM_TO | 1) This field is optional 2) This field must be between 1 - 99,999 3) Warn if left blank | Joel Koepke | NMMS
|  | Weather Zone / Weather Station (used for Dynamic Ratings) |  | LINE | WEATHERZONE_TO | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the list | Joel Koepke | NMMS
| FROM Station | ERCOT Station Code Mnemonic |  | LINE | ERCOT_CODE_FROM | 1) This field is Optional 2) Warn if left blank 3) This field must match ERCOT records (unless new) 4.If the Internal Line Flag is 'Y', then the TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic can be same. If the internal Line Flag is 'N', TO STATION - ERCOT Station Code Mnemonic and FROM STATION - ERCOT Station Code Mnemonic should be distinct . Error message should be "'Error! TO and FROM Station Code ( ) should not be duplicated if Internal Line Flag = "N". 5) If the internal Line Flag is 'N', ,FROM Station Code Mnemonic cannot be listed as a TO Station Code Mnemonic on any other lines. The Warning would occur on the secondary side (eg: they had DIESEL on the FROM station on the first line, and DIESEL on the TO Station on the second line then the TO station would produce the Warning) or (eg: DIESEL is on the TO station on the 3rd line and DIESEL on the FROM station on the 4th line then the FROM station would produce the Warning). | Joel Koepke | NMMS
|  | Connected Device Name(s) |  | LINE_DEVICES | DEVICE_NAME | 1) This field is required 2) May not be >= than 17 characters. Warning! Device Name () should not be > 17 characters long or the name will be truncated in the model which requires uniqueness. 3) May not have duplicates within the TO or FROM Station 4) May not contain special characters except for an underscore "_" and a dash "-" | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | LINE_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  | Bus Number (PTI Bus Number) | (integer) | LINE | BUSNUMBR_FROM | 1) This field is optional 2) This field must be between 1 - 99,999 3) Warn if left blank | Joel Koepke | NMMS
|  | Weather Zone / Weather Station (used for Dynamic Ratings) |  | LINE | WEATHERZONE_FROM | 1) This field is conditionally required if "Line Rating (Static or Dynamic)" = 'DYNAMIC' 2) Value must be from the list | Joel Koepke | NMMS
| Resistance in p.u. (100 MVA Base) |  | p.u. | LINE | RESISTANCE | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Resistance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Resistance should be less than 0.0001 3) If Line Data - Line Voltage Level = 69kV, value must be <= 1.5 If Line Data - Line Voltage Level = 138kV or 345kV, value must be <= 0.5 WARN if value is outside of these conditions 4) If the Zero Impedance Lines are contained within a single substation,then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | Joel Koepke | NMMS
| Reactance in p.u. (100 MVA Base) |  | p.u. | LINE | REACTANCE | 1) Field is required If value is < 0.0001 and Internal Line = 'Y' then Warning! Reactance should be less than 0.0001 If value is < 0.0001 and Internal Line = 'N' then Warning! Reactance should be less than 0.0001 If Line Data - Line Voltage Level = 69kV, value must be <=1.0 If Line Data - Line Voltage Level = 138kV, value must be <=0.1 If Line Data - Line Voltage Level = 345kV, value must be <=.05 WARN if value is outside of these conditions 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). 4) If the Zero Impedance Lines are contained within a single substation,then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab" | Joel Koepke | NMMS
| Charging Susceptance in p.u. (100 MVA Base) |  | p.u. | LINE | CHARGING_SUSC | 1) Field is required 2) Value must be >= 0 If Line Data - Line Voltage Level = 69kV, value must be <=0.3 If Line Data - Line Voltage Level = 138kV, value must be <=0.5 If Line Data - Line Voltage Level = 345kV, value must be <=2.2. Generate a Warning if Rule fails 3) If the Zero Impedance Lines are contained within a single substation,then they should be removed from the Line tab and the updated connections should be shown in the Breaker/Switch tab. "ERROR! Internal zero impedance lines should be modeled on the breaker/switch tab. If Zero Impedance Linesoes between two substations,produce a warning if line ratings are entered as 9999. "ERROR! Invalid MVA Rating between substations. | Joel Koepke | NMMS
| Type (overhead / underground / both) |  |  | LINE | TYPE | 1) Field is required 2) Value must be at from the following list: OVERHEAD, UNDERGROUND, BOTH | Joel Koepke | NMMS
| Segment Length |  | miles | LINE | SEGMENT_LENGTH | 1) Field is required 2) Value must > 0 3) Formula on Line Data - Segment Length: The formula to determine the length of a line based on the Reactance (X) and the Charging Susceptance (Chg) is 486 * SQRT(X_pu * Chg_pu). Generate a Warning when Segment length is not within the 25% variation of the calculated value. 4) Update the Warning message to include the text " This is applicable for Overhead lines only" | Joel Koepke | NMMS
| Line Rating (Static or Dynamic) |  |  | LINE | LINE_RATING | 1) Field is required 2) Field must be from the following list: STATIC, DYNAMIC | Joel Koepke | NMMS
| Nominal (Static) | Continuous Rating | MVA | LINE | CONTINUOUS_RTG | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be <= Nominal (Static) - 2-hr Emergency Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - Continuous Rating AND value must be >= 115 °F Continuous Rating | Joel Koepke | NMMS
|  | 2-hr Emergency Rating | MVA | LINE | EMGCY_RTG_2HR | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be <= Nominal (Static) - 15-min Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 2-hr Emergency Rating AND value must be >= 115 °F 2-hr Emergency Rating | Joel Koepke | NMMS
|  | 15-min Rating | MVA | LINE | RTG_15MIN | 1) This field is required regardless of STATIC or DYNAMIC 2) Value must be >= Nominal (Static) - Continuous Rating 3) Value must be >= Nominal (Static) - 2-hr Emergency Rating 4) Conditional Rule (if Line Rating (Static or Dynamic) = Dynamic): Value must be <= 20 °F - 15-min Rating AND value must be >= 115 °F 15-min Rating | Joel Koepke | NMMS
| 20 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be <= the subsequent dynamic rating. For example: 20 °F - Continuous Rating >= 25 °F - Continuous Rating 25 °F - Continuous Rating >= 30 °F - Continuous Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating 5) Produe an error when invalid MVA rating (ex: 9999) is entered 'Error! Invalid Continous MVA rating' | Joel Koepke | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr Emergency Rating >= 25 °F - 2-hr Emergency Rating 25 °F - 2-hr Emergency Rating >= 30 °F - 2-hr Emergency Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating 5) Produe an error when invalid MVA rating (ex: 9999) is entered 'Error! Invalid 2-Hr Emergency MVA rating' | Joel Koepke | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN | 1) These field are conditionally required. If Line Rating (Static or Dynamic) = Dynamic this field is required 2) Line Rating (Static or Dynamic) = Static, this field must be blank 3) If required, these values must be >= the subsequent dynamic rating. For example: 20 °F - 2-hr 15-min Rating >= 25 °F - 15-min Rating 25 °F - 2-hr 15-min Rating >= 30 °F - 15-min Rating 4) If required, within each temp rating, the following must apply Continuous Rating <= 2-hr Emergency Rating <= 15-min rating 5) Produe an error when invalid MVA rating (ex: 9999) is entered 'Error! Invalid 15-min MVA rating' | Joel Koepke | NMMS
| 25 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 30 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 35 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 40 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 45 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 50 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 55 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 60 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 65 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 70 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 75 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 80 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 85 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 90 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 95 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 100 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 105 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 110 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| 115 °F | Continuous Rating | MVA | LINE_TEMP | CONTINUOUS_RTG |  |  | NMMS
|  | 2-hr Emergency Rating | MVA | LINE_TEMP | EMGCY_RTG_2HR |  |  | NMMS
|  | 15-min Rating | MVA | LINE_TEMP | RTG_15MIN |  |  | NMMS
| Comments |  |  | LINE | COMMENTS_LINE | None |  | NMMS
| EFFECTIVE DATE: |  |  | LINE | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B8: Line names must meet the character limitation of the ERCOT system. They must be UNIQUE within ERCOT. Line data is provided monthly and posted.
Note on C10: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on C13: Enter up to 10 switching device names that this line is connected to at the "To Station".
Note on C23: Bus Number for Line termination point being modeled in the "To" station (Bus number as determined by Planning groups)
Note on C25: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on C26: Enter up to 10 switching device names that this line is connected to at the "From Station".
Note on C36: Bus Number for Line termination point being modeled in the "From" station (Bus number as determined by Planning groups)

## Breaker_Switch Data
ERCOT Confidential
Breaker_Switch Data
|  |  |  | Table: | DB Field: | Rules: | Source | APPLICATION
SITE
GENERAL
| Description of change |  |  | BREAKER_SWITCH | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| BREAKER / SWITCH |  | Labels
| ERCOT Station Code Mnemonic |  |  | BREAKER_SWITCH | SITE_CODE | 1) This field is required 2) Must match ERCOT records (unless new) 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | Joel Koepke | NMMS
| Is this a Fault Isolating Device (e.g. Circuit Breaker) |  | Y/N | BREAKER_SWITCH | FAULT_ISO_DEV_FLG | 1) This is a required field 2) Values must from the following list: 'Y', 'N' | Joel Koepke | NMMS
| Switch Name |  |  | BREAKER_SWITCH | SWITCH_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Switch Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Normal Operating Status (when in-service) (Open or Closed) |  |  | BREAKER_SWITCH | NORM_OP_STATUS | 1) This field is required 2) Value must be from the following list: 'OPEN', 'CLOSED' | Joel Koepke | NMMS
| Voltage Level |  | kV | BREAKER_SWITCH | VOLT_LVL | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | Joel Koepke | NMMS
| SIDE 1 | Directly connected device name(s) |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
| SIDE 2 | Directly connected device name(s) |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=17 characters. Must be <=17 characters. Warning! Device Names () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4) At least one connected device is required on each side of the Breaker/Switch. Generate an error if at least one connected device is missing on both sides Generate a Warning when at least one connected device is missing on any one side. | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | BREAKER_SWITCH_SIDE | DEVICE_NAME | Optional | Joel Koepke | NMMS
| Comments |  |  | BREAKER_SWITCH | COMMENTS_BRKRSWITCH | None |  | NMMS
| EFFECTIVE DATE: |  |  | BREAKER_SWITCH | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B8: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on B10: Name of switch to be used in ERCOT model (will be seen in Outage Scheduler and on one-lines)
Note on C13: Enter up to 10 Connected device Names
Note on C23: Enter up to 10 Connected device Names

## Capacitor and Reactor Data
ERCOT Confidential
Capacitor and Reactor Data
Please submit one-line diagram together with this Capacitor or Reactor request form.
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
SITE
GENERAL
| Description of change |  | CAPREACT | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| CAPACITOR or REACTOR | Labels
| ERCOT Station Code Mnemonic |  | CAPREACT | SITE_CODE | 1) This field is required 2) Must match ERCOT records (unless new) 3)This field may not have any special characters, except an underscore "_" and a dash "-" 4) Value must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | Joel Koepke | NMMS
| Capacitor or Reactor | C/R | CAPREACT | CAPACITOR_REACTOR_FLG | 1) This field is required 2) Value must be from the following list: 'C', 'R' | Joel Koepke | NMMS
| Device Name |  | CAPREACT | DEVICE_NAME | 1) This field is required 2) Value may contain no special characters except an underscore "_" and a dash "-" 3) Must be <=14 characters. Warning! Device Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Nominal MVAR | MVAR | CAPREACT | NOMINAL_MVAR | 1) This field is required 2) If the Capacitor or Reactor field is 'C' , the value should be > 0 , if it is 'R', value should be < 0 | Joel Koepke | NMMS
| Voltage Level kV | kV | CAPREACT | VOLT_LVL_KV | 1) This field is required. 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | Joel Koepke | NMMS
| Bus Number (PTI Bus Number) | (integer) | CAPREACT | PTI_BUSNUM | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| Device Name(s) - that this reactive device is directly connected to |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) ) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 4)This field should be unique. Every Device entry needs to have a unique “Device Name(s) – that this reactive device is directly connected to". No two capacitors should have the same controlling breaker or switch. 5) 'Connected Device' Field in Capcitor Reactor Tab should be defined either in the Breaker/Switch Tab(if the connected device is a sSwitch Name) or in the Transformer Tab(if the connected device is a Transformer Name). Audit report should produce an error if the rule fails. | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | CAPREACT_DEVICE | CONNECTED_DEVICE_NAME | Optional | Joel Koepke | NMMS
| Automatic Voltage Regulation | Y/N | CAPREACT | AUTO_VOLT_FLG | 1) This field is required 2) Value must be from the following list: 'Y', 'N' | Joel Koepke | NMMS
| Voltage Level of Busbar being regulated | kV | CAPREACT | BUSBAR_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | Joel Koepke | NMMS
| Desired Regulating voltage | kV | CAPREACT | DES_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value must be > 0 3) The value must >= Minimum Regulating Voltage 4) The value must <=Maximum Regulating Voltage 5) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | Joel Koepke | NMMS
| Minimum Regulating Voltage | kV | CAPREACT | MIN_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) The value must be > 0 3) The value must be <= Maximum Regulating Voltage 4) Warning if value exceeds 50% from Maximum Regulating Voltage 5) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | Joel Koepke | NMMS
| Maximum Regulating Voltage | kV | CAPREACT | MAX_REG_VOLT | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 3) The value must be > 0 4) The value must be >= Minimum Regulating Voltage 5) Warning if value exceeds 50% from Minimum Regulating Voltage 6) Value should be within the range of 10% of the base kV..anything beyond should be a Warning. | Joel Koepke | NMMS
| Comments |  | CAPREACT | COMMENTS_CAPREACT |  |  | NMMS
| EFFECTIVE DATE: |  | CAPREACT | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B9: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on B10: Capacitors or Reactors on tertiary voltages will not have a PTI Bus number.
Note on B11: This is the name provided by the owner and meets the ERCOT Character limitation.
Note on B15: Enter up to 10 Switching Device Names
Note on B25: If Yes, then fill out the rest of the table pertaining to voltage regulation.

## Transformer Data
ERCOT Confidential
Transformer Data
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
Transformer Data (100MVA Base)
GENERAL
| Description of change |  | TRANSFORMER | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| TRANSFORMER DETAILS | Labels
| ERCOT Station Name (Station Code or Station Mnemonic) |  | TRANSFORMER | SITE_CODE | 1) This field is required 2) Must match ERCOT records 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. 5) substation code should be in Upper case letters. Generate an error if the rule fails | Joel Koepke | NMMS
| Transformer Name |  | TRANSFORMER | TRANSFORMER_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Transformer Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Is this transformer in a Master/Follower current balancing configuration? | Y/N | TRANSFORMER | MASTER_FOLLOW_FLG | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | Joel Koepke | NMMS
| Master Name (can be same as this transformer) |  | TRANSFORMER | MASTER_NAME | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) Warn if >= 14 characters. First 14 characters must be unique. Warning! Master Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" 4) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name | Joel Koepke | NMMS
| Follower Name (can be same as this transformer) |  | TRANSFORMER | FOLLOWER_NAME | 1) This field is conditionally required if Transformer Data - Is this transformer in Master / Follower of Current Balancing configuration? = 'Y' 2) May not contain special characters except for an underscore "_" and a dash "-" 3) Either the Master Name or the Follower Name MUST = Transformer Data - Transformer Name 4) Warn if >= 14 characters. First 14 characters must be unique. Warning! Follower Name () should not be >=14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Generator Step Up Transformer? | Y/N | TRANSFORMER | GSU_TRANSFORMER_FLG | 1) This field is required 2) Value must be in the following list: 'Y', 'N' | Joel Koepke | NMMS
| Unit(s) associated with this transformer |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | 1) This field is conditionally required - if Generation Step-up = 'Y', this is required 2) Value(s) must be <=17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. 3) Warn if the unit name is not in the Unit Info - GEN or Unit Info - CC or Unit Info - Wind | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_UNITS | TRANSFORMER_UNIT_CODE | Optional | Joel Koepke | NMMS
| High Side Voltage Level (no-load) | kV | TRANSFORMER | HIGH_NOLOAD | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | Joel Koepke | NMMS
| High Side Voltage Level (PTI) | (Integer) | TRANSFORMER | HIGH_PTI | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| High Side Voltage Connection - Wye or Delta |  | TRANSFORMER | HIGH_CONNECTION | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | Joel Koepke | NMMS
| High Side Voltage Connected Devices (list on separate lines) |  | TRANSFORMER_DEVICES | DEVICE_NAME | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
| High Side Manufactured Nominal Voltage | kV | TRANSFORMER | HIGH_MANU_VOLT | 1) This field is required 2) If value > 60kV Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage 6) High Side Manufactured Nominal Voltage should be > Voltage at Lowest Tap Position and < Voltage at Highest Tap Position 7) Transformer High Side Manufactured Nominam Voltage should equal to Voltage at Highest Tap - Step Size voltage to reach Nominal Tap. | Joel Koepke | NMMS
| Low side Voltage Level (no-load) | kV | TRANSFORMER | LOW_NOLOAD | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be <= High Voltage Level (no-load) 6) If Generator Step-up Transformer = 'Y' AND Low Side Voltage Level (no-load) > 1kV AND Then the Low Side Voltage Level (no-load) must be equal to Unit Info - GEN / CC / WIND - Unit Generating Voltage | Joel Koepke | NMMS
| Low Side Voltage Level (PTI) | (Integer) | TRANSFORMER | LOW_PTI | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| Low Side Voltage Connection - Wye or Delta |  | TRANSFORMER | LOW_CONNECTION | 1) This field is required 2) Value must be of the following: 'Wye', 'Delta' | Joel Koepke | NMMS
| Low Side Voltage Connected Devices (list on separate lines) |  | TRANSFORMER_DEVICES | DEVICE_NAME | 1) This field is required a) Error: if High Side Voltage >= 60kV and Low Side Voltage >1kV b) Warn: if High Side Voltage < 60kV and Low Side Voltage = 1kV 2) Warn if >= 17 characters. 3) No special characters except an underscore "_" or a dash "-" | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | TRANSFORMER_DEVICES | DEVICE_NAME | Optional | Joel Koepke | NMMS
| Low Side Manufactured Nominal Voltage | kV | TRANSFORMER | LOW_MANU_VOLT | 1) This field is required 2) If the value >= 69kv: Accepted if value (using 5%) Deviates < ¦3.45¦ kV from 69 Deviates < ¦6.9¦ kV from 138 Deviates < ¦17.25¦ kV from 345 Warn if value (using >= 5% and <10%) Deviates > = ¦3.45¦ but deviates < ¦6.9¦ from 69 Deviates >= ¦6.9¦ but deviates < 13.8 from 138 Deviates >= ¦17.25¦ but deviates < 34.5 from 345 Error if value (using > =10%) Deviates >= ¦6.9¦ kV from 69 Deviates >= ¦13.8¦kV from 138 Deviates >= ¦34.5¦kV from 345 3) Warn if value > 345 4) The value must be > 0 5) High Side Manufactured Nominal Voltage >= Low Side Manufactured Nominal Voltage | Joel Koepke | NMMS
| Series Resistance (100 MVA Base) | p.u. | TRANSFORMER | SERIES_RESIST | 1) This field is required 2) Value must be >=0. Allow negative Resistance only when low side kV is 1kV. 3) Produce an Error if the Transformer Resistance value is less than 3 decimals.(('Error! Resitance (x) may be rounding, it should be accurate to 5th decimal') Produce a Warning if the Transformer Resistance value is greater than 2 decimals and less than 5 decimals('Warning! Resitance(x) may be rounding, it should be accurate to 5th decimal') 4) If “Low kV” <> 1 Then ERROR if R/X > 1 Else “no warning/error” Else if “Low kV” = 1 Then Warning if R/X > 3 Else “no warning/error” | Joel Koepke/Joe Weatherley | NMMS
| Series Reactance (100 MVA Base) | p.u. | TRANSFORMER | SERIES_REACT | 1) This field is required 2) Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). Allow negative Reactance only when low side kV is 1kV. 3) Produce an Error if the Transformer Reactance value is less than 3 decimals.(('Error! Reactance (x) may be rounding, it should be accurate to 5th decimal') Produce a Warning if the Transformer Reactance value is greater than 2 decimals and less than 5 decimals('Warning! Reactance(x) may be rounding, it should be accurate to 5th decimal') 4) If “Low kV” <> 1 Then ERROR if R/X > 1 Else “no warning/error” Else if “Low kV” = 1 Then Warning if R/X > 3 Else “no warning/error” | Joel Koepke/Joe Weatherley | NMMS
| Continuous Rating | MVA | TRANSFORMER | CONTINUOUS_RTG | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | Joel Koepke | NMMS
| 2-hr Emergency Rating | MVA | TRANSFORMER | EMGCY_RTG_2HR | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <= 15-min Rating | Joel Koepke | NMMS
| 15-min Rating | MVA | TRANSFORMER | RTG_15MIN | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | Joel Koepke | NMMS
Voltage Regulation
| Automatic Voltage Regulation | Y/N | TRANSFORMER | AUTO_VOLT_REG | 1) This field is required 2) Value must be from the following list: 'Y', 'N' 3) AVR is expected to be 'Y' when total number of tap positions >=16. Warn if "Automatic Voltage Regulation" = 'N' and Total Number of Tap Positions>=16 | Joel Koepke | NMMS
| Does Transformer have a Load Tap Changer? | Y/N | TRANSFORMER | LOADTAP_CHNGR_FLG | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be from the following list: 'Y', 'N' 3) Load Tap Changer is expected to be 'Y' when total number of tap positions >=16. Warn if "Load Tap Changer" = 'N' and Total Number of Tap Positions>=16 | Joel Koepke | NMMS
| Location of Load Tap Changer - High or Low |  | TRANSFORMER | LOCN_TAP_CHNGR | 1) This field is conditionally required if 'Does Transformer have a Load Tap Changer ?' = 'Y' 2) Value must be of the following: 'HIGH', 'LOW' 3) Load Tap Changer should be 'Y' when AVR is 'Y'. Generate an error if Load Tap Changer is 'N' and AVR = 'Y'. | Joel Koepke | NMMS
| Base kV of Regulated Side | kV | TRANSFORMER | REG_KV_BASE | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 5) The value must be >= Low Voltage Level (no-load) | Joel Koepke | NMMS
| Target kV of Regulated Side | kV | TRANSFORMER | REG_KV_TARGET | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must be > 0 | Joel Koepke | NMMS
| Acceptable Deviation of Target Voltage | % | TRANSFORMER | ACCEPT_DEV_VOLT_TARGET | 1) This field is conditionally required if Automatic Voltage Regulation = 'Y' 2) Value must not exceed 50% | Joel Koepke | NMMS
Low Tap Settings | Only if Tap Exists
| Tap position at Manufactured Nominal Voltage | (Integer) | TRANSFORMER_TAP_SETTINGS | MANU_VOLT_TAP_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Note: this value may be negative 3. Value must be between Lowest and Highest Tap position 4)All tap information is required if it exists on either the LTC or Fixed side. | Joel Koepke | NMMS
| Total Number of Tap Positions | (Integer) | TRANSFORMER_TAP_SETTINGS | TOTAL_NUM | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= 2 3) Warn if value >= 16 and "Automatic Voltage Regulation" = 'N' Warn if value >=16 and "Load Tap Changer" = 'N' | Joel Koepke | NMMS
| Normal Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | NORMAL_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Lowest Tap Position 3) Value must be <= Low Tap Settings - Highest Tap Position 4) Note: this value may be negative | Joel Koepke | NMMS
| Lowest Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | LOWEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Highest Tap Position 3) Note: this value may be negative | Joel Koepke | NMMS
| Voltage at Lowest Tap Position | kV | TRANSFORMER_TAP_SETTINGS | LOWEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be <= Low Tap Settings - Voltage at Highest Tap Position 3) Value must be < High Tap Settings - Voltage at Lowest Tap Position 4) Value must be >= 0 | Joel Koepke | NMMS
| Highest Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | HIGHEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field must be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Low Tap Position 3) Note: this value may be negative | Joel Koepke | NMMS
| Voltage at Highest Tap Position | kV | TRANSFORMER_TAP_SETTINGS | HIGHEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out. Note that it is valid for both, Low and High Tap settings to be filled out. Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must be >= Low Tap Settings - Voltage at Lowest Tap Position 3) Value must be <= High Tap Settings - Voltage at Highest Tap Position 4) Value must be >= 0 | Joel Koepke | NMMS
| Size of each Voltage Level Step | kV | TRANSFORMER_TAP_SETTINGS | STEP_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap Second Condition: This field may be left blank if Low Voltage Level = 1 2) Value must > 0 3) Warn if < 0.002 * Low Side Voltage Level (no-load) 4) Warn if > 0.05 * Low Side Voltage Level (no-load) | Joel Koepke | NMMS
High Tap Settings | Only if Tap Exists
| Tap position at Manufactured Nominal Voltage | (Integer) | TRANSFORMER_TAP_SETTINGS | MANU_VOLT_TAP_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Note: this value may be negative 3.Value must be between Lowest and Highest Tap position 4)All tap information is required if it exists on either the LTC or Fixed side. | Joel Koepke | NMMS
| Total Number of Tap Positions | (Integer) | TRANSFORMER_TAP_SETTINGS | TOTAL_NUM | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be >= 2 3) Warn if value >= 16 and "Automatic Voltage Regulation" = 'N' Warn if value >=16 and "Load Tap Changer" = 'N' | Joel Koepke | NMMS
| Normal Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | NORMAL_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be >= High Tap Settings - Lowest Tap Position 3) Value must be <= High Tap Settings - Highest Tap Position 4) Note: this value may be negative | Joel Koepke | NMMS
| Lowest Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | LOWEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be <= High Tap Settings - Highest Tap Position 3) Note: this value may be negative | Joel Koepke | NMMS
| Voltage at Lowest Tap Position | kV | TRANSFORMER_TAP_SETTINGS | LOWEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be <= High Tap Settings - Voltage at Highest Tap Position 3) Value must be > Low Tap Settings - Voltage at Lowest Tap Position 4) Value must be >= 0 | Joel Koepke | NMMS
| Highest Tap Position | (Integer) | TRANSFORMER_TAP_SETTINGS | HIGHEST_POS | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be >= Low Tap Position 3) Note: this value may be negative | Joel Koepke | NMMS
| Voltage at Highest Tap Position | kV | TRANSFORMER_TAP_SETTINGS | HIGHEST_VOLT | 1) This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must be >= High Tap Settings - Voltage at Lowest Tap Position 3) Value must be > Low Tap Settings - Voltage at Highest Tap Position 4) Value must be > 0 | Joel Koepke | NMMS
| Size of each Voltage Level Step | kV | TRANSFORMER_TAP_SETTINGS | STEP_VOLT | 1)This field is conditionally required If "Does transformer have a load tap changer?" = 'Y' then either Low Tap Settings or High Tap Settings must be filled out based on the Location of the Load Tap Changer (e.g. Load Tap is on the high side, high tap settings is now required). Note that it is valid for both, Low and High Tap settings to be filled out if there is a non-load tap on the opposite side of the Load Tap 2) Value must > 0 3) Warn if < 0.002 * High Side Voltage Level (no-load) 4) Warn if > 0.05 * High Side Voltage Level (no-load) | Joel Koepke | NMMS
| Comments | [5 empty] | NMMS
| EFFECTIVE DATE: |  | TRANSFORMER | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B9: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on B10: Existing transformer names can be found in the ERCOT Branch Data spreadsheet available in the Operations and System Planning secure area of the ERCOT website. New names are either obtained by the transmission operator, the RE, or the TDSP and RE work together to determine a name.
Note on B15: Select all unit(s) associated with this transformer from the drop down list provided
Note on B50: If Yes, then fill out the rest of the table pertaining to voltage regulation.

## Static_Var_Compensator Data
ERCOT Confidential
Static_Var_Compensator Data
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
SITE
GENERAL
| Description of change |  | STATIC_VAR_COMP | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| STATIC VAR COMPENSATOR | Labels
| ERCOT Station Name (Station Code or Station Mnemonic) |  | STATIC_VAR_COMP | SITE_CODE | 1) This field is required 2) Must match ERCOT records (unless new) 3) Must be <= 8 characters. Warning! Station Name () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| SVC Name |  | STATIC_VAR_COMP | SVC_NAME | 1) This field is required 2) May not be > than 14 characters..Warning! SVC Name () should not be >14 characters long or the name will be truncated in the model which requires uniqueness. 3) May not contain special characters except for an underscore "_" and a dash "-" | Joel Koepke | NMMS
| Switching Device Name(s) - that this reactive device is directly connected to |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 3) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | STATIC_VAR_COMP_DEVICES | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
| SVC Base Voltage Level | kV | STATIC_VAR_COMP | SVC_BASE_VOLT | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | Joel Koepke | NMMS
| Fixed MVAR (VAR injection at nominal voltage) | MVAR | STATIC_VAR_COMP | FIXED_MVAR | 1) This field is required 2) Value must be > 0 | Joel Koepke | NMMS
| Minimum Admittance Limits (100 MVA Base) | p.u. | STATIC_VAR_COMP | MIN_ADM_LIMIT | 1) This field is required 2) Value must be <= Maximum Admittance | Joel Koepke | NMMS
| Maximum Admittance Limits (100 MVA Base) | p.u. | STATIC_VAR_COMP | MAX_ADM_LIMIT | 1) This field is required 2) Value must be >= Minimum Admittance | Joel Koepke | NMMS
| Minimum Steady State Reactive Power Limits | MVAR | STATIC_VAR_COMP | MIN_STD_STATE_REACT | 1) This field is required 2) Value must be >= Maximum Steady State Reactive Power Limits | Joel Koepke | NMMS
| Maximum Steady State Reactive Power Limits | MVAR | STATIC_VAR_COMP | MAX_STD_STATE_REACT | 1) This field is required 2) Value must be >= Minimum Steady State Reactive Power Limits | Joel Koepke | NMMS
| Minimum Threshold (post contingency) Reactive Power Limits | MVAR | STATIC_VAR_COMP | MIN_THRESH_REACT | 1) This field is required 2) Value must be <= Maximum Threshold (post contingency) Reactive Power Limits | Joel Koepke | NMMS
| Maximum Threshold (post contingency) Reactive Power Limits | MVAR | STATIC_VAR_COMP | MAX_THRESH_REACT | 1) This field is required 2) Value must be >= Minimum Threshold (post contingency) Reactive Power Limits | Joel Koepke | NMMS
| Minimum Voltage Threshold | kV | STATIC_VAR_COMP | MIN_VOLT_THRESH | 1) This field is required 2) Value must be <= Maximum Voltage Threshold (100 MVA Base) 3) The value may not exceed 345 3) The value must be > 0 4) Warn if Max / Min exceed 50% of one another | Joel Koepke | NMMS
| Maximum Voltage Threshold | kV | STATIC_VAR_COMP | MAX_VOLT_THRESH | 1) This field is required 2) Value must be >= Minimum Voltage Threshold (100 MVA Base) 3) The value may not exceed 345 4) The value must be > 0 5) Warn if Max / Min exceed 50% of one another | Joel Koepke | NMMS
| Comments |  | STATIC_VAR_COMP | COMMENTS_STATIC_VAR_COMP |  |  | NMMS
| EFFECTIVE DATE: |  | STATIC_VAR_COMP | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B8: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on B9: This is the name provided by the owner and meets the ERCOT Character limitation.
Note on B10: List up to 10 Switching Device Names
Note on B20: Transmission Level Voltage that this device is being operated to control.

## Series Device Data
ERCOT Confidential
Series Device Data
|  |  |  | Table: | DB Field: | Rules: | Source | APPLICATION
SITE
GENERAL
| Description of change |  |  | SERIES_DEVICE_DATA | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| SERIES DEVICE DATA |  | Labels
| Series Device Name |  |  | SERIES_DEVICE_DATA | SD_NAME | 1) This field is required 2) No special characters except and underscore 3) Warn if >= 14 characters. First 14 characters must be unique. Warning! Series Device Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| ERCOT Station Name (Station Code or Station Mnemonic) |  |  | SERIES_DEVICE_DATA | SITE_CODE | 1) This field is required 2) Must match ERCOT records (unless new) 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters. Warning! Station Code () should not be >8 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Voltage Level (kV |  | kV | SERIES_DEVICE_DATA | VOLATGE | 1) This field is required 2) If the value >= 69kv it must be 69,138, or 345 3) The value may not exceed 345 4) The value must be > 0 | Joel Koepke | NMMS
| SIDE 1 | Connected Device Name(s) |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  | Bus Number (PTI Bus Number) | (integer) | SERIES_DEVICE_DATA | SIDE1_PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| SIDE 2 | Connected Device Name(s) |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | 1) This field is required 2) May not have duplicates within the TO or FROM Station 3) May not contain special characters except for an underscore "_" and a dash "-" 4) May not be > than 17 characters. Warning! Device Name () should not be >17 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  |  | SERIES_DEVICE_DATA_SIDE | SWITCH_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  | Bus Number (PTI Bus Number) | (integer) | SERIES_DEVICE_DATA | SIDE2_PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| Resistance |  | p.u. | SERIES_DEVICE_DATA | RESISTANCE | 1) This value is required 2) Value must be > 0 | Joel Koepke | NMMS
| Reactance |  | p.u. | SERIES_DEVICE_DATA | REACTANCE | 1) This value is required 2) Value may be negative. Allow negative Reactance (to represent Series Capacitors) 3)Error if Reactance value is > 1. Error! Reactance (value) > 1.0. Reactance should be expressed in terms of per unit (e.g. not percentage). | Joel Koepke | NMMS
| Continuous Rating |  | MVA | SERIES_DEVICE_DATA | CONTINUOUS_RTG | 1) This field is required 2) Value must be <= 2-hr Emergency Rating 3) Value must be <= 15-min Rating | Joel Koepke | NMMS
| 2-hr Emergency Rating |  | MVA | SERIES_DEVICE_DATA | EMGCY_RTG_2HR | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be <=15-min Rating | Joel Koepke | NMMS
| 15-min Rating |  | MVA | SERIES_DEVICE_DATA | RTG_15MIN | 1) This field is required 2) Value must be >= Continuous Rating 3) Value must be >= 2-hr Emergency Rating | Joel Koepke | NMMS
| Comments |  |  | SERIES_DEVICE_DATA | SD_COMMENTS |  |  | NMMS
| EFFECTIVE DATE: |  |  | SERIES_DEVICE_DATA | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B8: Serial Device Name- Must be unique within ERCOT (including uniqueness with Lines in the ERCOT system…in other words can not be named the same as a line)
Note on B9: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on C11: List up to 10 connected switching devices
Note on C22: List up to 10 connected switching devices

## Load data
ERCOT Confidential
Load Data
For the transmission grid (>60kV) and for the kV grids modeled for output paths of generators (<60kV), all Auxillary, Station Service and/or Power transformers are modeled in ERCOT as a load point at the high side of these types of transformers. Modeled Loads are expected to have MW/MVAR telemetry. Two modeling options exist for modeled loads on the generator’s kV grid. 1) Model all loads as an equivalent load without a controlling breaker/switch. The model must ensure the path of the load served by the transmission grid (>60kV) is accurate. Typically placement of the modeled load is per GSU (on the low side) if low side breaker/switches exist that can break the load’s path between GSUs. 2) Model loads individually and topologically accurate with controlling breaker/switches modeled (status telemetry required).
|  |  | Table: | DB Field: | Rules: | Source | APPLICATION
SITE
GENERAL
| Description of change |  | LOADS | CHANGE_DESCRIPTION | 1) This field is conditionally Required - If there is a change to a tab, the change must be described. | Joel Koepke | NMMS
| Load Data | Labels
| ERCOT Station Name (Station Code or Station Mnemonic) |  | LOADS | SITE_CODE | 1) This field is required 2) Must match ERCOT records 3) This field may not have any special characters, except an underscore "_" and a dash "-" 4) Must be <= 8 characters 5) substation code should be in Upper case letters. Generate an error if the rule fails | Joel Koepke | NMMS
| Load Name (as it appears in the ERCOT model) |  | LOADS | LOAD_NAME | 1) This field is required 2) May not contain special characters except for an underscore "_" and a dash "-" 2) Warn if >= 14 characters. First 14 characters must be unique. 3)Warning! ERCOT Load Name() should not be >= 14 characters long or the name will be truncated in the model which requires uniqueness. | Joel Koepke | NMMS
| Load Voltage Level | kV | LOADS | VOLATGE | 1) This field is required 2) Value must be >= 0 3) If the value >= 69kv it must be 69,138, or 345 | Joel Koepke | NMMS
| PTI Bus Number | Integer | LOADS | PTI_BUS_NUM | 1) This field is optional 2) This field must be between 1 - 99,999 | Joel Koepke | NMMS
| Device Name(s) - that this load is physically connected to |  | LOAD_DEVICES | LOAD_DEVICE_NAME | 1) This field is required 2) No special characters except an underscore or a dash 3) Warn if >= 17 characters. First 17 characters must be unique. Warning! ERCOT Device Name() should not be >=17 characters long or the name will be truncated in the model which requires uniqueness. 4) 'Connected Device that this load is directly connected to' Field in Load Data Tab should be defined either in the Breaker/Switch Tab(if the connected device is a sSwitch Name) or in the Transformer Tab(if the connected device is a Transformer Name) | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
|  |  | LOAD_DEVICES | LOAD_DEVICE_NAME | Optional | Joel Koepke | NMMS
| Average Load Under Normal Operations | MW | LOADS | AVG_LOAD | 1) This field is required 2) It should be >0 and generate a warning if = 0 | Joel Koepke | NMMS
| Average MVAR Under Normal Operations | MVAR | LOADS | AVG_MVAR | 1) This field is required 2) It should be >0 and generate a warning if = 0 | Joel Koepke | NMMS
| Comments |  | LOADS | LOAD_COMMENTS |  |  | NMMS
| EFFECTIVE DATE: |  | LOADS | EFF_DATE | This is a Required field and Data Type is mm/dd/yyyy. Date Effective should be >= Site-In-Service Date (SITECODES Table, SITE_IN_SRVC_DT Field). Generate an error if the rules fail. | Woody Rickerson | NMMS
Note on B9: This is the substation Mnemonic as determined by character limitations between Planning and Operations Models. Currently listed in "Data Dictionary"
Note on B10: This is the name provided by the owner and meets the ERCOT Character limitation.
Note on B13: List up to 10 Switching Device Names
Note on B23: Transmission Level Voltage that this device is being operated to control.
Note on B24: Transmission Level Voltage that this device is being operated to control.