# Nodal Market Non-Spinning Reserve Service Deployment and Recall Procedures

# (Proposed ROS response to TAC)

There are three situations that will cause Non-Spinning Reserve Service (NSRS) to be deployed.

- Detection of insufficient capacity for energy dispatch during periodic checking of available capacity for future operations.

- Disturbance conditions such as a unit trip, sustained frequency decay or sustained low frequency operations.

- SCED not having enough energy available to execute successfully.

  - Each situation is described below.  In each case, the ERCOT operator will make the final decision and initiate the deployment.  The ERCOT operator shall deploy NSRS in amounts sufficient to respond to the operational circumstances.  This means that NSRS may be deployed partially over time or may be deployed in its entirety.  If NSRS is deployed partially, it shall be deployed in increments of 100% of each Resources capacity.  To support partial deployment, ERCOT shall, following the Day-Ahead Market (DAM), rank, for each hour of the Operating Day, the Resources supplying NSRS in an economic order based on DAM Settlement Point Prices, the energy cost for online Resources and startup and operation at LSL for off-line Resources.  ERCOT shall develop a procedure, which will be approved by TAC, to create the economic order of NSRS Resources. Partial NSRS deployment and recall decisions shall be based on each Resource’s economic cost order.

# Deployment based on periodic checking of available capacity for future operations

ERCOT executes HRUC one hour prior to each Operating Hour.  The first hour of HRUC simulation is for the next Operating Hour.  During that process, functionality similar to the real-time Ancillary Services Capacity Monitor (6.5.7.5) will evaluate available capacity for the next Operating Hour.  If the A/S capacity monitor indicates a capacity margin of less than 5% of the forecast demand, the ERCOT Operator will receive notification of a Capacity Insufficiency.  NSRS will be deployed as described below.

# Off-Line Generation Resource reserved for Non-Spin

- The QSE will be sent a Resource specific Dispatch Instruction that NSRS has been deployed.

- The Dispatch Instruction must include the expected amount of capacity that will be available for SCED and the anticipated duration of the deployment.

- The QSE must have the Resource on-line and ready for SCED dispatch Base Points as soon as practical.

- SCED will respond to the changes in Resource Status that are received by telemetry from the QSE.  A typical sequence would be from OFFNS to ONOS (with output schedule equal to minimum load) and then to ON.

- SCED will execute each time it is has detected a Resource Status change for an off-line NSRS deployed Resource.

- The Resource must, at a minimum be capable of providing all the energy to SCED  within 30 minutes of the Dispatch Instruction.

- The QSE will ensure that the NSRS A/S Schedule for that unit has been reduced to zero in COP and real-time telemetry.

# Load Resource reserved for Non-Spin

- The QSE will be sent a Resource specific Dispatch Instruction that NSRS has been deployed.

- The Dispatch Instruction must include the MW level of load energy to be interrupted by the Load Resource and the estimated duration of the deployment.

- NSRS procured from a Load Resource block offer must be deployed as a block.

- The Resource must, at a minimum, interrupt the requested deployment energy within 30 minutes of the Dispatch Instruction.

# On-Line Generation Resource with an Energy Offer Curve

- The QSE will be sent a Resource specific Dispatch Instruction that NSRS has been deployed.

- The deployment will be for the total amount of capacity on that Resource that had been reserved for NSRS,

- ERCOT will automatically calculate new HASL constraints for SCED by reducing the Resource’s Non-Spin Ancillary Service Schedule to zero.

- The QSE will update the Resource parameters in COP and the real-time telemetry according.

- The Resource must, at a minimum, provide the additional SCED requested deployment energy within 30 minutes of the Dispatch Instruction.

# On-Line Generation Resource with output schedules

- The QSE will be sent a Resource specific Dispatch Instruction that NSRS has been deployed.

- The Dispatch Instruction must include the additional amount of energy (MW) that needs to be produced by the Resource and the estimated duration of the deployment.

- For DSR’s providing NSRS, as soon as the QSE receives the deployment, ERCOT shall adjust the HASL for the Resource with the Output Schedule in the real-time telemetry and the QSE shall adjust the COP accordingly.

- For non-DSR’s (with Output Schedules) providing NSRS, ERCOT shall adjust the HASL for the Resource with the Output Schedule for the remainder of the Operating Period to reflect the amount of deployment.

# Deployment triggered by disturbance conditions

The deployment procedure will be the same as described above except it will be based on the real-time Ancillary Services Capacity Monitor that executes every 10 seconds.  EECP processes may govern the deployment of NSRS during such conditions.

# Deployment to cover shortage of energy available to SCED

The deployment procedure will be the same as described above except it will be based on the real-time Ancillary Services Capacity Monitor that executes every 10 seconds.  Since SCED failing to converge initiates an Emergency state, Emergency processes will govern the deployment of NSRS during such conditions.

# Recall of Non-Spin Deployment

NRSR will be dispatched or deployed in this manner for each clock hour until the HRUC capacity monitor expects a near-term sustained capacity margin of greater than 8% of the forecast load demand.  When the 8% threshold is exceeded, ERCOT will recall the Non-Spin energy and/or capacity.

- A QSE with a Generation Resource that was previously off-line will be allowed to control the unit down to its LSL at the Normal Ramp Rate and then trip it off-line.

- A QSE with a Generation Resource (with an Energy Offer Curve) that will stay on-line will restore the NSRS A/S Schedule for that unit and let the ERCOT Resource Limit Calculator update the HASL prior to the next SCED execution.  The unit will ramp to the new Base Point at the Normal Ramp Rate.

- A QSE with a Generation Resource (with an Output Schedule) that will stay on-line will back out the NSRS addition that was made to the Output Schedule.  This can be incrementally deleted depending on the size of the deployment and Normal Ramp Rate.

- A QSE with a Load Resource that has provided NSRS will ensure that the load energy and NSRS capability is restored within three hours from the expiration of the NSRS deployment.  If it is not, the NSRS capability will be replaced by the QSE on other Generation or Load Resources not previously committed.

# Comments

With in 30 minutes

The change should be from OFFNS to ON since

- The deadline for submitting Output Schedule for non-DSR Resources is end of Adjustment Period

- Off-Line Resources providing Non-Spin are required by protocol to have Energy Offer Curve 6.5.7.6.2.3(3).

- When the Resource is starting up since its HDL will be below its LDL, the base point will be set to current telemetry.

This could result in a lot of successive run of SCED. I think it would be reasonable to assume that those Resources will be considered in the next scheduled SCE run. Operator can always manually run SCED if needed

The Resource should be able to free the capacity with in 30 minute. The energy deployments are done by SCED. Hence the energy deployed (Base Point) should be provided in 5 minutes.

Based on the latest approved whitepaper QSE will telemeter Non-Spin Schedule as well as Non-Spin Remaining Schedule. Non-Spin Remaining Schedule will be reduced to zero when Non-Spin is deployed from that Resource. But COP will have only Non-Spin Schedule.

I don’t think the QSE should reduce the AS Schedule in COP since next HRUC will consider that capacity to meet Load Forecast. Also the deadline for submitting COP is end of Adjustment Period.

Based on the current approved whitepaper, QSE’s will update the telemetered Non-Spin Remaining Schedule. ERCOT will not be making any changes to the Schedule. ERCOT will just use Non-Spin Remaining Schedule to calculate the HASL

I don’t think COP should be changed. See comment for Offline Resources

Since the energy deployments are done by SCED, the Non-Spin energy deployment will be part of Base Point and hence should be provided in 5 minutes.

I don’t think COP should be changed. See comment for Offline Resources

Based on the current approved whitepaper, QSE’s will update the telemetered Non-Spin Remaining Schedule for both DSR and non-DSR. Also for DSR Resources QSEs will increase the Output Schedule by Non-Spin deployment amount. For non-DSR Resources ERCOT will increase the Output Schedule considered in SCED by Non-Spin deployment amount ERCOT will just use Non-Spin Remaining Schedule to calculate the HASL hence for non-DSR Resources if the QSE doesn’t reduce the Non-Spin Remaining Schedule  then the HASL will not change and so the HDL will be limited and SCED will not deploy any energy from that Resource from Non-Spin Capacity

QSE’s will update the telemetered Non-Spin Remaining Schedule. ERCOT will just use Non-Spin Remaining Schedule to calculate the HASL

This will be different for DSR and Non-DSR Resources. For DSRs, QSE will reduce the Output Schedule by the Non-Spin deployment amount. For Non-DSR, ERCOT will consider the QSE submitted Output Schedule when Non-Spin is recalled.