ERCOT Operations Report

January 2010 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 1/2/2010 5:19 | 59.849 | 96 | Unit trip with 585 MW |
| 1/5/2010 17:32 | 59.852 | 62 | Unit trip with 700 MW |
| 1/6/2010 17:35 | 60.104 | 21 | Out of Down Regulation. 300 MW fleet down. |
| 1/9/2010 10:28 | 59.767 | 132 | Unit trip with 1231 MW |
| 1/9/2010 10:34 | 60.135 | 134 | SCE +2590 MW in 5 min. Out of Down Regulation due to the deployment of LaaRs. |
| 1/9/2010 13:11 | 59.89 | 6 | Unit trip with 754 MW |
| 1/9/2010 13:50 | 60.129 | 793 | Out of Down Regulation |
| 1/11/2010 5:54 | 59.877 | 4 | Unit trip with 598 MW |
| 1/20/2010 13:25 | 59.898 | 5 | Unit trip with 471 MW |
| 1/20/2010 16:00 | 59.789 | 104 | Unit trip with 765 MW |
| 1/26/2010 1:58 | 59.743 | 110 | Unit trip with 789 MW |
| 1/26/2010 4:17 | 60.138 | 239 | SCE +1280 MW in 21 min. Out of Down Regulation. |
| 1/28/2010 10:04 | 60.123 | 104 | Wind trending down but stopped after offset was entered. Slow responsive recall. |
| 1/28/2010 13:15 | 60.167 | 587 | Out of Down Regulation. Wind generation increased 1000 MW after offset was calculated for Real-Time Balancing Market. |
| 1/28/2010 13:55 | 59.895 | 6 | Out of Up Regulation Service. Wind generation dropped 1120 MW after offset was calculated for RTBM. |
| 1/28/2010 17:32 | 59.774 | 115 | Unit trip with 810 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 1/1 00:02:49 | 1/1 00:24:49 | 0:22:00 | 402.61 | No offset entered due to MOI failure during midnight database load. |
| 1/2 05:19:49 | 1/2 05:35:37 | 0:15:48 | 638.89 |  |
| 1/5 17:32:12 | 1/5 17:44:12 | 0:12:00 | 629.65 |  |
| 1/5 21:05:48 | 1/5 21:22:32 | 0:16:44 | 336.17 | Out of Up Regulation. |
| 1/7 09:51:30 | 1/7 09:58:38 | 0:07:08 | 357.52 | Unit Trip |
| 1/8 06:53:38 | 1/8 07:03:06 | 0:09:28 | 368.19 | Unit Trip |
| 1/9 03:29:24 | 1/9 03:43:12 | 0:13:48 | 325.50 | Unit Trip |
| 1/9 10:28:54 | 1/9 10:49:18 | 0:20:24 | 1083.2 |  |
| 1/9 13:01:11 | 1/9 13:32:02 | 0:30:51 | 634.98 |  |
| 1/11 05:54:22 | 1/11 06:02:02 | 0:07:40 | 496.26 |  |
| 1/13 19:24:40 | 1/13 19:31:12 | 0:06:32 | 336.17 | Unit Trip |
| 1/19 13:14:14 | 1/19 13:27:48 | 0:13:34 | 346.85 | Out of Up Regulation. |
| 1/20 13:25:58 | 1/20 13:35:06 | 0:09:08 | 384.20 |  |
| 1/20 16:00:30 | 1/20 16:28:54 | 0:28:24 | 965.81 |  |
| 1/26 01:58:14 | 1/26 03:06:34 | 1:08:20 | 1162 |  |
| 1/28 09:39:38 | 1/28 10:07:36 | 0:27:58 | 389.54 | Out of Up Regulation.(Wind generation decreased 800 MW after offset calculated) |
| 1/28 13:55:00 | 1/28 14:32:24 | 0:37:24 | 400.2 |  |
| 1/28 17:32:20 | 1/28 17:54:40 | 0:22:20 | 1045.9 |  |
| 1/30 22:47:09 | 1/30 23:16:12 | 0:29:03 | 373.52 | Out of Up Regulation. |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| W RIO | 90 | 0 | 0 | 0 | 0 | 90 |
| DFW | 42 | 6 | 18 | 24 | 0 | 66 |
| Houston | 16 | 0 | 28 | 28 | 0 | 44 |
| Austin | 20 | 5 | 6 | 11 | 0 | 31 |
| Western | 1 | 2 | 8 | 10 | 2 | 13 |
| North | 2 | 3 | 5 | 8 | 0 | 10 |
| San Antonio | 0 | 5 | 1 | 6 | 0 | 6 |
| South | 0 | 4 | 0 | 4 | 0 | 4 |
| Northeast | 1 | 0 | 0 | 0 | 0 | 1 |
| Corpus | 0 | 0 | 1 | 1 | 0 | 1 |
| Bryan Area | 0 | 0 | 1 | 1 | 0 | 1 |
| E RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 172 | 25 | 68 | 93 | 2 | 267 |

| Historical Totals | Jan-10 | Jan-09 | Dec-09 |
| --- | --- | --- | --- |
| Austin | 25 | 19 | 9 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 0 | 2 | 2 |
| DFW | 48 | 28 | 16 |
| E RIO | 0 | 22 | 1 |
| Houston | 16 | 1 | 0 |
| Laredo | 0 | 16 | 0 |
| North | 5 | 8 | 5 |
| Northeast | 1 | 0 | 3 |
| San Antonio | 5 | 0 | 4 |
| South | 4 | 0 | 4 |
| W RIO | 90 | 137 | 79 |
| Western | 5 | 3 | 15 |
| Total | 199 | 243 | 102 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Dilley Switch - San Miguel Switch 138 kV | Derby - Pearsall 69 kV | 14 |
| Garfield - Onion Creek & Hicross AEN 138 kV | Lytton Springs 345/138 kV #1 | 11 |
| Abilene Mulberry Creek - Bitter Creek and Long Creek Switching Station - Sweetwater Generating Plant 345 kV | Anson - Radium 69 kV | 11 |
| Graham - Parker Switch 345 kV | Barton Switch - Oran 138 kV | 10 |
| Graham SES - Parker Switch 345 kV | Flat Creek - Leon Switch 138 kV | 10 |
| Garfield - Onion Creek & Hicross AEN 138 kV | Lytton Springs 345/138 kV #2 | 9 |
| Hamilton Road - Sonora 138 kV | Sonora - Friess Ranch 69 kV | 8 |
| Twin Buttes - San Angelo 345 kV | Twin Buttes transformer 345/138 kV T1 | 8 |
| Whitney - Bosque Switch 138 kV | Lake Whitney - Whitney 138 kV | 6 |
| Base Case | Stanton East Switching Station - Midland East 138 kV | 6 |
| Graham - Parker Switch 345 kV | Graham 345/138 kV AT | 5 |
| Base Case | Matador - Spur 69 kV | 5 |
| Sandow Switch - Temple Switch 345 kV | Hearne 138/69 kV transformer | 5 |
| Abilene South - Eskota 138 kV | Trent - Merkel 69 kV | 4 |
| McDonald - Big Spring Switch 138 kV | Sprayberry Switch - Midland Downtown 138 kV | 3 |
| Abilene Mulberry Creek - Bitter Creek and Long Creek Switching Station - Sweetwater Generating Plant 345 kV | Merkel - Trent 69 kV | 3 |
| Base Case | Matador - Paducah REA Tap 69 kV | 3 |
| Batesville - Pearsall 138 kV | Pearsall Switch 138/69 kV AT | 3 |
| Temple Pecan Creek - Tradinghouse SES and Temple Switch - Lake Creek SES 345 kV | San Angelo Power Station - Yellow Jacket 138 kV | 3 |
| Aspermont - Spur 138KV | Matador - Paducah 69 kV | 2 |
| McDonald - Big Spring 138 kV | Forsan Tap - Sprayberry 138 kV | 2 |
| Pearsall - San Miguel 138 kV | Pearsall 138/69 kV AT | 2 |
| PH Robinson 345/138 kV T2 AT | Garrott - Midtown 138 kV | 2 |
| San Angelo - Ballinger 138 kV | Humble Ballinger - Novice 69 kV | 2 |
| Watermill Switch - Limestone 345 kV | Trinidad - Richland Chambers 345 kV | 2 |
| Menard - Fort Mason - Yellow Jacket - Gilles 138 kV | Gillespie - Phillips Mason 69 kV | 2 |
| Odessa EHV - Morgan SES and Quail Switch 345 kV | Big Spring Switch - Big Spring West 138 kV | 2 |
| Abilene Mulberry Creek - Bitter Creek and Long Creek Switching Station - Sweetwater Generating Plant 345 kV | Matador - Paducah Rea 69 kV | 2 |
| Aspermont - Paint Creek 138 kV | Matador - Spur 69 kV | 2 |
| Base Case | Palmhurst - Magic Valley EC 138 kV | 2 |
| Graham SES - Long Creek Switching Station and Cook Field Road Switching Station 345 kV | San Angelo Power Station - Yellow Jacket 138 kV | 2 |
| Danevang transformer 138/69 kV | Blessing - Palacios 69 kV | 1 |
| Graham - Parker Switch 345 kV | Graham - Graham East 138 kV | 1 |
| Kendall 345/138 kV T2 | Kendall 345/138 kV T1 | 1 |
| Whitney - Bosque SW 138 kV | Bosque - Lake Whitney 138 kV | 1 |
| Austrop - Lost Pines 345 kV | Lytton Springs 345/138 kV #1 AT | 1 |
| Live Oak - Sonora 138 kV | Live Oak - Eldorado 69 kV | 1 |
| Morgan Creek - Quail Switch & Longshore Switch 345 kV | Morgan Creek SES 345/138 kV AT #1 | 1 |
| Odessa EHV - Morgan SES and Quail Switch 345 kV | Morgan Creek SES 345/138 kV AT#1 | 1 |
| Abilene Mulberry Creek - Bitter Creek and Long Creek Switching Station - Sweetwater Generating Plant 345 kV | Sterling County - Sterling City 69KV | 1 |
| Abilene South - Eskota Switch 138 kV | Eskota Switch 138/69 kV AT | 1 |
| Aspermont - Spur 138 kV | Spur 138/69 kV AT | 1 |
| Base Case | Enas Snyder - MEC Plainview Tap 69 kV | 1 |
| Base Case | San Angelo - Yellow Jacket 138 kV | 1 |
| Euless - Liggett Switch 138 kV | DFW B East - Hackberry 138 kV | 1 |
| Graham - Parker Switch 345 kV | Leon Switch - Putnam 138 kV | 1 |
| Graham - Parker Switch 345 kV | San Angelo - Yellow Jacket 138 kV | 1 |
| McDonald - Big Spring Switch 138 kV | Forsan Tap - Colorado Municipal District 138 kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West – North | 13 |
| North – Houston | 1 |
| North – South | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 01/06/2010 | Transmission and Security Desk V4 Rev 10 | 457 |
| 01/06/2010 | Shift Supervisor Desk V4 Rev 10 | 456 |
| 01/06/2010 | Frequency Control Desk V4 Rev 9 | 455 |
| 01/06/2010 | Day-Ahead Desk V4 Rev 8 | 454 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

1/08 08:00 55,856 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2007 | 2008 | 2009 | 2010 |
| January | 4.55 | 3.30 | 4.11 | 3.78 |
| February | 3.75 | 3.59 | 3.49 | NA |
| March | 2.70 | 3.29 | 3.24 | NA |
| April | 3.00 | 2.45 | 2.66 | NA |
| May | 3.22 | 3.01 | 2.90 | NA |
| June | 4.46 | 2.81 | 2.89 | NA |
| July | 4.29 | 2.55 | 2.83 | NA |
| August | 3.11 | 3.66 | 3.07 | NA |
| September | 3.78 | 4.99 | 3.68 | NA |
| October | 3.08 | 2.79 | 2.92 | NA |
| November | 2.95 | 2.60 | 1.93 | NA |
| December | 3.74 | 4.54 | 3.70 | NA |
| Annual Average | 3.55 | 3.29 | 3.11 | 3.78 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 1/02/10 | 5:05 | 11:00 | OCN issued due to a projected reserve capacity shortage for HE 0800 - HE 1100. |
| 1/02/10 | 5:25 | 12:00 | Advisory issued due to ARRS below 3000 MW. |
| 1/03/10 | 10:15 | 13:50 | Advisory issued due to ARRS below 3000 MW. |
| 1/05/10 | 7:32 | 0:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/9/10. |
| 1/06/10 | 0:15 | 0:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/9/10. |
| 1/07/10 | 0:15 | 0:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/9/10. |
| 1/08/10 | 0:15 | 24:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/9/10. |
| 1/09/10 | 0:15 | 24:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/9/10. |
| 1/10/10 | 0:15 | 13:00 | Advisory issued for extreme winter weather with temperatures expected to be in the teens to low 20’s for most of the state starting Thursday 01/7/10 – 01/10/10. |
| 1/14/10 | 10:47 | 21:00 | Operating Condition Notice (OCN) issued for a potential capacity shortage for HE 19:00 - 23:00. |
| 1/15/10 | 5:41 | 12:18 | Advisory issued due to ARRS below 3000 MW. |
| 1/15/10 | 22:07 | 0:00 | Advisory issued due to ARRS below 3000 MW. |
| 1/15/10 | 22:40 | 23:59 | Watch issued due to ARRS below 2500 MW. |
| 1/16/10 | 0:15 | 13:10 | Advisory issued due to ARRS below 3000 MW. |
| 1/16/10 | 10:39 | 23:14 | OCN issued for projected reserve capacity shortage for hours 19:00 to 24:00. |
| 1/16/10 | 18:22 | 23:14 | Advisory issued due to ARRS below 3000 MW. |
| 1/26/10 | 3:20 | 7:35 | Advisory issued for ARRS below 3000 MW. |
| 1/26/10 | 4:00 | 7:30 | OCN issued for projected capacity shortage for HE 07:00 through HE 09:00. |
| 1/28/10 | 9:52 | 11:10 | Advisory issued for ARRS below 3000 MW. |
| 1/28/10 | 12:05 | 21:00 | Advisory issued for ARRS below 3000 MW. |

Transmission Watch

1/08 07:35	Transmission Watch issued for the post contingency loss of Dilley Switch - San Miguel Switch 138KV overloads Derby - Pearsall 69KV.  ERCOT received emergency energy from CFE across the Laredo VFT and Eagle Pass DC tie.

1/09 00:15	Transmission Watch issued for the post contingency loss of Dilley Switch - San Miguel Switch 138KV overloads Derby - Pearsall 69KV.  ERCOT received emergency energy from CFE across the Laredo VFT.

Emergency Notice

1/08 18:00	Market Emergency Notice issued due to Replacement Reserve Service Market did not meet the required time-line.

1/09 10:28	Emergency Notice issued for NERC Reportable Disturbance Control Standard (DCS) Event.  Load acting as a Resource (LaaR) were deployed to recover frequency.

Texas RE Event Analysis

1/08 18:00	Market Emergency Notice issued due to RPRS Market failed to meet timeline.

1/09 10:28	Emergency Notice issued for NERC Reportable Disturbance Control Standard (DCS) Event due to loss of one unit.

Others

1/26  02:00	Held Real-Time Balancing Market IE 2:15 and resumed with IE 2:45 due to scheduled generation changed after offset input.