## Slide 1: Generation Adequacy Task Force Update to WMS
January 20, 2010

## Slide 2: Topics
Review of draft final report:
  Summary of recommendations.
Determine Next Steps

## Slide 3: Report Contents
Introduction
GATF Charter and Goals
LOLP Study Review
Load Forecasting
EILS and other Demand Response Resources
Review and Discussion of CDR Inputs, Calculations and Format
  Installed Capacity Assumptions
  New Unit Additions
  Renewables
  Mothballed Capacity
  DC Tie Capacity
  Switchable” Capacity
  Netting of Generation and Load
  Retired Capacity
  CDR Format
Recommendations

## Slide 4: Recommendations: LOLP
LOLP Study
  Utilize NERC GADS forced outage rate data averaged over the 2004 to 2008 timeframe and compare to ERCOT’s operational data to ensure it is reasonable. ERCOT has already implemented a process in which market participants either: 1) grant ERCOT permission to obtain each company’s GADS data directly from NERC, or 2) provide each company’s information directly to ERCOT.
  The LOLP study year will be 2012.
  Transmission topology will be modeled in a “single node” arrangement - separate studies will be performed once LOLP cases are developed to look at transmission needs probabilistically.
  Scheduled maintenance will be handled the same as forced outage rate data above.
  Natural gas-fired CC combustion turbines and natural gas-fired simple-cycle peaking units will be used for new unit additions when determining reserve margins and the ELCC of wind resources.
  To determine the ELCC of wind generators, ERCOT Staff will determine the ELCC for each region (north/west and south) to determine if there are significant differences between the two. If so, ERCOT will add a line item in the CDR showing the ELCC for each. If not, then the ELCC of wind generators in both regions will be combined on a capacity weighted basis in the CDR. Once the ELCC of wind generation is determined, ERCOT Staff will compare the ELCC values with actual wind operational data to ensure reasonableness.
  Solar plants will be treated the same as conventional generation in the LOLP until a threshold level of 200 MW has a SGIA.

## Slide 5: Recommendations: EILS and Other DR Programs
Load Forecasting - No recommended changes to the existing ERCOT load forecasting processes.
Emergency Interruptible Load Service
  The GATF recommends the following methodology be utilized for EILS quantities in the reserve margin calculation:
  For the winter period, “current year”
    Use only the Oct.-Jan. Contract Period
    Use simple average of 2 Time Period procurements (Business Hours 3 and Non-Business Hours)
  For the summer period, “current year”
    Use the actual May procurement amount for Business Hours 3 (this procurement is for the June through September contract period).
  For the later years of the CDR (years 2 through 5), a 10% growth rate in EILS will be used, with ERCOT Staff reviewing this growth rate, and possibly amending as additional EILS procurement data is collected.
Other Demand Response Programs
  Advanced metering programs will not be included in the reserve margin calculations at this time. ERCOT Staff will continue to monitor the programs and may include them in the future once additional information is collected.
  ERCOT Staff will continue to monitor energy efficiency initiatives ongoing by the State of Texas to determine their impact, if any, on firm load calculations.

## Slide 6: Recommendations : CDR
Installed Capacity Assumptions – Utilize the following RARF data points in the reserve calculation:
  “Seasonal net max sustainable rating – summer”, and
  “Seasonal net max sustainable rating – winter”
New Unit Additions – The GATF will develop a protocol revision that will require Generating Entities that already have a SGIA and air permit to submit an “affirmative” declaration that the SGIA and air permit, and the in-service dates referenced in those documents, are still applicable.
Renewables – Already covered on previous slide.
Mothballed Capacity – Continue to utilize the current “mothballed” capacity methodology based on the lead time and probability information furnished as per Protocol Section 6.5.9.3, Generation Resource Return to Service Updates.
DC Tie Capacity – No changes recommended: 50% of DC Tie Capacity in the reserve margin calculation.

## Slide 7: Recommendations : CDR
“Switchable” Capacity – Utilize the resource capacity reported in the RARF and the data provided pursuant to ERCOT Protocol Section 16.5.3, Requirements for Reporting and for Changing the Terms of a Resource Registration.
Netting of Generation and Load – No suggested changes.
Retired Capacity – Modify the CDR line item for retired capacity to read “Pending Unit Retirements” for instances in which a generation resource owner has notified ERCOT they intend to cease operations for a particular resource within a certain period of time, yet ERCOT Staff may still be evaluating the resource for potential RMR service when the CDR is published.
CDR Format
  Move the “SummerCapacities” and “WinterCapacities” tabs further closer to the front of the report, right behind the “SummerSummary” and “WinterSummary” tabs.
  Post the GATF reports on the planning portion of the website.
  Add a column showing the on line commercial date for each unit in the “SummerCapacities” and “WinterCapacities” tabs.
  In the “SummerFuelTypes” and “WinterFuelTypes” tabs, provide a definition of the generation category of “Other” and add a row for Solar technologies.

## Slide 8: GATF Next Steps
Draft Report completed by GATF
Implement any suggested changes from today.
Submit draft to WMS, take comments and vote next month?