| NPRR Number | 203 | NPRR Title | Amend Telemetry Bus Accuracy Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | February 18, 2010 |  |  |
| Proposed Effective Date |  | Upon the Nodal Protocol Transition Plan’s Texas Nodal Market Implementation Date, as prescribed by zonal Protocol Section 21.12, Process for Transition to Nodal Market Protocol Sections. |  |  |
| Priority and Rank Assigned |  | Not applicable |  |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 3.10.7.5.2, Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) proposes a new term, State Estimator Bus, and proposes language changes to Section 3.10.7.5.2. |  |  |
| Reason for Revision |  | “Electrical Bus” is not the correct term to describe the way this item is being or could be monitored. This data is generated from the State Estimator (SE) and the term “State Estimator Bus” should be given a unique definition for this case. Being more specific will mitigate ambiguity about the way this item should and will be reported. |  |  |
| Overall Market Benefit |  | Market will be provided clear indication where data for SE and Telemetry Standards is being derived. |  |  |
| Overall Market Impact |  | No impact to market. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR203 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 12/22/09, NPRR203 and the CEO Revision Request Review were posted. - On 1/20/10, ERCOT comments were posted. - On 1/21/10, PRS considered NPRR203. - On 1/26/10, an Impact Analysis was posted. - On 2/18/10, PRS considered the 1/21/10 PRS Report and Impact Analysis for NPRR203. |  |  |
| PRS Decision |  | On 1/21/10, PRS unanimously voted to recommend approval of NPRR203 as submitted. All Market Segments were present for the vote. On 2/18/10, PRS unanimously voted to endorse and forward the 1/21/10 PRS Report and Impact Analysis for NPRR203 to TAC. All Market Segments were present for the vote |  |  |
| Summary of PRS Discussion |  | On 1/21/10, there was no discussion. On 2/18/10, there was no discussion. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Reporting mechanism for the SE Bus Accuracy Reports would remain unchanged. |  |
|  | 2 | Significant changes in the ERCOT Energy Management System (EMS) would be required if the language remained unchanged. |  |
|  | 3 | The intent of the revision language is to capture possible SE telemetry inaccuracies. The State Estimator Topology Processor collapses network topology into a collection of electrical nodes including Electrical Buses. |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | No market cost to implement this change. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | SE Bus Accuracy Report Interpretation. | No monetary impact but a true reflection of the Nodal Protocol intent will be attained with the revision. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | This change correctly identifies the intent of the Nodal Protocol language and is already within the scope of the ERCOT EMS capabilities. If left unchanged there would be significant rework on the ERCOT EMS and subsequent reporting software to accommodate the possibilities. |  |
|  | 2 | The definition of an Electrical Bus does not necessarily conform to the stated requirement. |  |
|  | 3 | Electrical Bus, as defined and utilized, is more relative to the Market Management System (MMS) environment not the EMS SE environment. |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Ebby John on behalf of the Network Data Support Working Group (NDSWG) |
| E-mail Address | ebby.john@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | (713) 207-2136 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 012010 | Provided a PowerPoint to describe State Estimator Bus vs. Electrical Bus. |

Proposed Protocol Language Revision

## 2.1 	DEFINITIONS

State Estimator Bus

An electrical node of common voltage at a substation that consists of one or more Electrical Buses tied together with closed breakers or switches.

3.10.7.5.2	Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows

(1)	Each TSP or QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the SE and as needed to achieve the TAC-approved SE performance standard with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy.

(2)	Each QSE that represents a Split Generation Resource, with metering according to Section 3.8, Special Considerations for Split Generation Meters, shall provide ERCOT with telemetry of the actual equivalent generator injection of its individual Split Generation Resource and with telemetry of the total generation injection of the total generation facility.  ERCOT shall calculate the sum of each QSE’s telemetry on an individual Split Generation Resource and compare the sum to the telemetry for the total generation facility.  ERCOT shall notify each QSE representing the Split Generation Resource of any errors in telemetry detected by the SE.

(3)	Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure SE observability, per TAC-approved telemetry criteria, of any monitored voltage and power flow between their associated transmission breakers to the extent such can be shown to be needed in achieving the TAC-approved SE performance standard.  On monitored non-Load substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”  An N-1 Redundancy exists if the substation remains observable on the loss of any single measurement pair (kW, kVAr) excluding station RTU communication path failures.  In making the determination to request additional telemetry, ERCOT shall consider the economic implications of inaccurate representation of Load models in LMP results versus the cost to remedy.

(4)	The accuracy of the SE is critical to successful market operations.  For this reason it is a critical objective for ERCOT to maintain reasonable and accurate results of the SE.  ERCOT shall use all reasonable efforts to achieve that objective, including the provision of legitimate constraints used in calculating LMPs.

(5)	Each TSP, QSE and ERCOT shall develop a continuously operated program to maintain telemetry of all Transmission Element measurements to provide accurate results using TAC-approved accuracy standards from the SE.  For any location where there is a connection of multiple, measured, Transmission Elements, ERCOT shall have an automated process to detect and notify ERCOT System operators if the residual sum of all telemetered measurements is more than (a) five percent of the largest line Normal Rating at the SE Bus or (b) five MW, whichever is greater.  If a location chronically fails this test, ERCOT shall notify the applicable TSP or QSE and suggest actions that the TSP or QSE could take to correct the failure.  Within 30 days, the TSP or QSE shall take the actions necessary to correct the failure or provide ERCOT with a detailed plan with a projected time frame to correct the failure.  ERCOT shall post a notice on the MIS Secure Area of any SE Buses not meeting TAC-approved accuracy requirements, including a list of all measurements and the residual errors on a monthly basis.

(6)	ERCOT shall implement a study mode version of the SE with special tools designed for troubleshooting and tuning purposes that can be used independently of any other ERCOT process that is dependant on the Real-Time SE.  ERCOT shall implement a process to recognize inaccurate SE results and shall create and implement alternative Real-Time LMP calculation processes for use when inaccurate results are detected.  ERCOT must be guided in this by TAC-approved accuracy standards.

(7)	ERCOT shall establish a system to provide overload and over/under limit alarming on all Transmission Elements monitored as constraints in the LMP models.