ERCOT Operating Guides

Section 1:  Introduction

Market Overview, Change Control, 
Relationships and Definitions

October 1, 2009

Contents

1.	Introduction	1-3

1.1	Document Purpose	1-3

1.2	Document Relationship	1-5

1.3	Process for Operating Guide Revision	1-6

1.4	Market Overview	1-18

1.5	Conformance to NERC Policies, Procedures, and Reliability Standards	1-20

1.6	Operating Definitions	1-23

1.7	Entity Definitions and Roles	1-25

1.7.1	ERCOT Control Area Authority	1-25

1.7.2	Qualified Scheduling Entities	1-25

1.7.3	Transmission Operator (TO)	1-25

1.7.4	Resource Entity	1-26

1.7.5	Load Serving Entities (LSE)	1-27

1.8	Operational Training	1-28

1.8.1	Operator Training Objectives	1-28

1.8.2	System Operator Training Requirements	1-28

1.8.3	ERCOT Operations Training Seminar	1-29

1.8.4	ERCOT Black Start Training	1-29

1.8.5	ERCOT Severe Weather Drill	1-29

1.8.6	Criteria For The Selection Of Operators	1-29

1.8.7	Training Practices	1-30

1.9	Document Revisions	1-31

Protocol References

Reference:  Protocol Section 5.2.2, Operating Standards	1-3

Reference:  Protocol Section 6.10.5.4, Responsive Reserve Services Deployment Performance Monitoring Criteria (In Part)	1-22

Reference:  Protocol Section 22, Attachment A, Standard Form Black Start Agreement (In Part)	1-27

# Introduction

## 1.1	Document Purpose

These Electric Reliability Council of Texas (ERCOT) Operating Guides supplement the Protocols and describe the working relationship between the ERCOT Control Area Authority and entities within the ERCOT System that interact with the ERCOT Control Area Authority on a minute-to-minute basis to ensure the reliability and security of the ERCOT System, as shown in the following diagram:

Specific practices described in these Guides for the ERCOT System are consistent with the North American Electric Reliability Corporation (NERC) Operating Policies and Reliability Standards, the ERCOT Protocols and consist of the following Guides:

Section 1 -  Introduction

Section 2 - System Operations

Section 3 - Operational Interfaces

Section 4 - Emergency Operation

Section 5 - Planning

Section 6 - Reports and Forms

Section 7 -  Disturbance Monitoring and System Protection

Section 8 – Operational Metering and Communication

Reference:  Protocol Section 5.2.2, Operating Standards

ERCOT and TDSPs shall operate the ERCOT System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures.  These Protocols shall control to the extent of any inconsistency between the Protocols and any of the following documents:

(1)		Any reliability guides applicable to ERCOT, including the Operating Guides;

(2)		The NERC Operating Manual and ERCOT procedures manual, supplied by NERC and ERCOT, respectively, as references for dispatchers to use during normal and emergency operations of the ERCOT Transmission Grid;

(3)		Specific operating procedures, submitted to ERCOT by individual transmission Facility owners or operators to address operating problems on their respective grids that could affect operation of the interconnected ERCOT Transmission Grid; and

(4)		Guidelines established by the ERCOT Board, which may be more stringent than those established by NERC for the secure operation of the ERCOT System.

## 1.2	Document Relationship

The relationship of these Operating Guides to other documents is defined in the following diagram:

It is the responsibility of the ERCOT Control Area Authority to develop internal Operating Procedures.  QSEs and TDSPs are required to develop their own internal Operating Procedures with respect to the ERCOT System entities, using their services and the Control Area Authority.  However, in doing so, QSE and TDSP Operating Procedures shall incorporate the relevant requirements of these Operating Guides.

These Operating Guides are derived from the ERCOT Protocols and the NERC Policies, Procedures, and Reliability Standards.  As the ERCOT system is within the State of Texas, the Public Utilities Commission of Texas (PUCT) defines additional requirements for the ERCOT Control Area Authority and connected entities.

PUCT requirements and directives and the ERCOT Protocols supercede these Guides.  NERC Policies and Procedures, with the exception of the specific modifications defined in these Guides will also be followed.

## 1.3	Process for Operating Guide Revision

1.3.1	Introduction

(1)	A request to make additions, edits, deletions, revisions, or clarifications to these Operating Guides, including any attachments and exhibits to these Operating Guides, is called an Operating Guide Revision Request (OGRR).  Except as specifically provided in other sections of these Operating Guides, this Section shall be followed for all OGRRs.  ERCOT Members, Market Participants, Public Utility Commission of Texas (PUCT) Staff, ERCOT , and any other Entities are required to utilize the process described herein prior to requesting, through the PUCT or other Governmental Authority, that ERCOT make a change to these Operating Guides, except for good cause shown to the PUCT or other Governmental Authority.

(2)	All decisions of the Operations Working Group (OWG), as defined below, the Reliability and Operations Subcommittee (ROS), the Technical Advisory Committee (TAC) and the ERCOT Board with respect to any OGRRs shall be posted to the Market Information System (MIS) within three Business Days of the date of the decision.  All such postings shall be maintained on the MIS for at least 180 days from the date of posting.

(3)	The “next regularly scheduled meeting” of the OWG, ROS, TAC, or the ERCOT Board shall mean the next scheduled meeting for which required Notice can be timely given regarding the item(s) to be addressed, as specified in the appropriate ERCOT Board or committee procedures.

(4)	Throughout the Operating Guides, references are made to the ERCOT Protocols.  ERCOT Protocols supersede the Operating Guides and any OGRRs must be compliant with the ERCOT Protocols.  The ERCOT Protocols are subject to the revision process outlined in Protocol Section 21, Process for Protocol Revision.

(5)	ERCOT may make non-substantive corrections at any time during the processing of a particular OGRR.  Under certain circumstances, however, the Operating Guides can also be revised by ERCOT rather than using the OGRR process outlined in this Section.

(a)	This type of revision is referred to as an “Administrative OGRR” or “Administrative Change” and shall consist of non-substantive corrections, such as typos (excluding grammatical changes), internal references (including table of contents), improper use of acronyms, and references to ERCOT Protocols, PUCT Substantive Rules, the Public Utility Regulatory Act (PURA), North American Electric Reliability Corporation (NERC) regulations, Federal Energy Regulatory Commission (FERC) rules, etc.  Updates to the ERCOT Load Shed Table in Section 4.5.3.3, EEA Levels, shall be processed as an Administrative OGRR.

(b)	ERCOT shall post such Administrative OGRRs to the MIS and distribute the OGRR to the OWG at least ten Business Days before implementation.  If no interested party submits comments to the Administrative OGRR, ERCOT shall implement it according to Section 1.3.6, Operating Guide Revision Implementation.  If any interested party submits comments to the Administrative OGRR, then it shall be processed in accordance with the OGRR process outlined in this Section.

1.3.1.1	Nodal Operating Guide Revision

A request to make additions, edits, deletions, revisions, or clarifications to the Nodal Operating Guides, including any attachments and exhibits to the Nodal Operating Guides, is called a Nodal Operating Guide Revision Request (NOGRR).  Except as specifically provided for in Section 1.3.4.1, Review and Posting of Operating Guide Revision Requests and Nodal Operating Guide Revision Requests, Section 1.3, Process for Operating Guide Revision, shall be followed for all NOGRRs.  ERCOT Members, Market Participants, PUCT Staff, ERCOT, and any other Entities are required to utilize the process described herein prior to requesting, through the PUCT or other Governmental Authority, that ERCOT make a change to the Nodal Operating Guides, except for good cause shown to the PUCT or other Governmental Authority.

1.3.2	Submission of an Operating Guide Revision Request

The following Entities may submit an OGRR:

(a)	Any Market Participant;

(b)	Any Entity that is an ERCOT Member;

(c)	PUCT Staff;

(d)	ERCOT; and

(e)	Any other Entity who resides (or represent residents) in Texas or operates in the ERCOT Region.

1.3.3	Operations Working Group

(1)	ROS shall assign a working group (“Operations Working Group” or “OWG”) to review and recommend action on formally submitted OGRRs.  ROS may create such a working group or assign the responsibility to an existing working group provided that:

(a)	Such working group’s meetings are open to ERCOT, ERCOT Members, Market Participants, and the PUCT Staff; and

(b)	Each Market Segment is allowed to participate.

(2)	Where additional expertise is needed, the OWG may request that ROS refer an OGRR to existing subcommittees, working groups or task forces for review and comment on the OGRR.  Suggested modifications—or alternative modifications if a consensus recommendation is not achieved by a non-voting working group or task force—to the OGRR shall be submitted by the chair or the chair’s designee on behalf of the commenting subcommittee, working group or task force as comments on the OGRR for consideration by OWG.  However, the OWG shall retain ultimate responsibility for the processing of all OGRRs.

(3)	The OWG shall ensure that the Operating Guides are compliant with the ERCOT Protocols.  As such, the OWG will monitor all changes to the ERCOT Protocols and initiate any OGRRs necessary to bring the Operating Guides in conformance with the ERCOT Protocols.  The OWG will also initiate a Protocol Revision Request (PRR) if such a change is necessary to accommodate a proposed OGRR prior to proceeding with that OGRR.

(4)	ERCOT shall consult with the chair of the OWG to coordinate and establish the meeting schedule for the OWG or other assigned subcommittees.  The OWG shall meet at least once per month, unless no OGRRs were submitted during the prior 24 days, and shall ensure that reasonable advance notice of each meeting, including the meeting agenda, is posted to the MIS.

1.3.4	Operating Guide Revision Procedure

1.3.4.1	Review and Posting of Operating Guide Revision Requests and Nodal Operating Guide Revision Requests

(1)	OGRRs shall be submitted electronically to ERCOT by completing the designated form provided on the MIS.

(2)	The OGRR shall include the following information:

(a)	Description of requested revision;

(b)	Reason for the suggested change;

(c)	Impacts and benefits of the suggested change on ERCOT market structure, ERCOT operations, and Market Participants, to the extent that the submitter may know this information;

(d)	OGRR Impact Analysis (applicable only for an OGRR submitted by ERCOT);

(e)	List of affected Operating Guide sections and subsections;

(f)	General administrative information (organization, contact name, etc.); and

(g)	Suggested language for requested revision.

(3)	ERCOT shall evaluate the OGRR for completeness and shall notify the submitter, within five Business Days of receipt, if the OGRR is incomplete, including the reasons for such status.  ERCOT may provide information to the submitter that will correct the OGRR and render it complete.  An incomplete OGRR shall not receive further consideration until it is completed.  In order to pursue the revision requested, a submitter must submit a completed version of the OGRR with the deficiencies corrected.

(4)	If a submitted OGRR is complete or once an OGRR is corrected, ERCOT shall post the complete OGRR to the MIS and distribute the OGRR to the OWG within three Business Days.

(5)	Once a NOGRR has been determined to be complete, the NOGRR must be evaluated by the ERCOT Chief Executive Officer (ERCOT CEO) or his designee before posting to the MIS.  The ERCOT CEO or his designee shall make his determination within five Business Days or issue a Notice to the submitter advising them that additional time is necessary.  Within three Business Days after a determination by the ERCOT CEO or his designee, ERCOT shall notify the submitter of the NOGRR of the ERCOT CEO’s or his designee’s decision.  If the ERCOT CEO or his designee determines the NOGRR is not necessary prior to the Texas Nodal Market Implementation Date, any ERCOT Member, Market Participant, PUCT Staff, or ERCOT may appeal the decision directly to the ERCOT Board.  Such appeal to the ERCOT Board must be submitted to ERCOT within ten Business Days after the date of the ERCOT CEO’s or his designee’s decision.

(6)	Once a submitted NOGRR has been evaluated by the ERCOT CEO or his designee, ERCOT shall post the completed NOGRR and the ERCOT CEO’s or his designee’s decision to the MIS and distribute the NOGRR to the ROS within three Business Days after the ERCOT CEO’s or his designee’s decision has been made.

(7)	Any posted NOGRR that changes scope during the stakeholder process must be reevaluated by the ERCOT CEO or his designee before proceeding to the next TAC Subcommittee, TAC, or the ERCOT Board for review.

1.3.4.2	Withdrawal of an Operating Guide Revision Request

(1)	By providing Notice to OWG, the submitter of an OGRR may withdraw the OGRR at any time prior to its recommendation for approval of the OGRR by the OWG.  ERCOT shall post a notice of the submitter’s withdrawal of an OGRR on the MIS within one Business Day of the submitter’s Notice to OWG.

(2)	The submitter of an OGRR may request withdrawal of an OGRR after a recommendation for approval by OWG.  Such withdrawal must be approved by ROS (if it has not yet been considered by ROS) or by TAC (if it has been recommended for TAC approval by ROS, but not yet considered by TAC).

(3)	Once approved by TAC, an OGRR cannot be withdrawn.

1.3.4.3	Operations Working Group Review and Action

(1)	Any interested party may comment on the OGRR.

(2)	To receive consideration, comments must be delivered electronically to ERCOT in the designated format provided on the MIS within 21 days from the posting date of the OGRR.  Comments submitted after the 21 day comment period may be considered at the discretion of OWG after these comments have been posted.  Comments submitted in accordance with the instructions on the MIS, regardless of date of submission, shall be posted to the MIS and distributed electronically to the OWG within three Business Days of submittal.

(3)	The OWG shall review the OGRR at its next regularly scheduled meeting after the end of the 21 day comment period, unless the 21 day comment period ends less than three Business Days prior to the next regularly scheduled OWG meeting.  In that case, the OGRR will be reviewed at the next regularly scheduled OWG meeting.  At such meeting, the OWG may take action on the OGRR to:

(a)	Recommend approval as submitted or modified;

(b)	Recommend rejection;

(c)	If no consensus can be reached, present options for ROS consideration;

(d)	Defer action on the OGRR; or

(e)	Request that ROS refer the OGRR to another subcommittee, workgroup, or task force.

(4)	Within three Business Days after OWG takes action (other than deferral), ERCOT shall issue a report (“OWG Recommendation Report”) to ROS reflecting the OWG’s action and post the same to the MIS.  The OWG Recommendation Report shall contain the following items:

(a)	Identification of submitter;

(b)	Modified Operating Guide language proposed by the OWG, when appropriate;

(c)	Identification of authorship of comments;

(d)	Proposed effective date(s) of the OGRR;

(e)	Recommended action; and

(f)	Recommended priority and rank for any OGRRs requiring a system change project.

1.3.4.4	Comments to the Operations Working Group Recommendation Report

(1)	Any interested party may comment on the OWG Recommendation Report.  To receive consideration, comments on the OWG Recommendation Report must be delivered electronically to ROS and ERCOT in the designated format provided on the MIS.  Comments received regarding the OWG Recommendation Report after three Business Days prior to the next regularly scheduled OWG meeting may be considered at the discretion of the ROS chair.

(2)	Within three Business Days of receipt of comments related to the OWG Recommendation Report, ERCOT shall post such comments to the MIS.  The comments shall include identification of the commenting Entity.

(3)	Comments submitted in accordance with the instructions on the MIS, regardless of date of submission, shall be posted to the MIS and distributed electronically to the ROS and OWG within three Business Days of submittal.

(4)	ROS shall review the OWG Recommendation Report and any posted comments to the Recommendation Report at its next regularly scheduled meeting.  Comments must be posted seven days prior to the next regularly scheduled ROS meeting.  Comments posted after the due date may be considered at the discretion of the ROS chair.

1.3.4.5	Operating Guide Revision Request Impact Analysis

(1)	ERCOT shall complete an Impact Analysis based on the submitted OWG Recommendation Report and will report the Impact Analysis’ results to OWG at the next regularly scheduled OWG meeting.

(2)	The Impact Analysis shall include:

(a)	An estimate of any cost and budgetary impacts to ERCOT;

(b)	The estimated amount of time required to implement the proposed OGRR;

(c)	The identification of alternatives to the original proposed language that may result in more efficient implementation; and

(d)	The identification of any manual workarounds that may be used as an interim solution.

1.3.4.6	Operations Working Group Review of Impact Analysis

(1)	After ERCOT posts the results of the Impact Analysis, OWG shall review the Impact Analysis at its next regularly scheduled meeting.  OWG may revise its OWG Recommendation Report after considering the information included in the Impact Analysis.

(2)	If OWG revises its Recommendation Report, a revised OWG Recommendation Report shall be issued by OWG to ROS and posted on the MIS.  Additional comments received regarding the revised OWG Recommendation Report shall be accepted up to three Business Days prior to the ROS meeting at which the OGRR is scheduled for consideration.  If OWG revises its recommendation, ERCOT shall update the Impact Analysis and issue the updated Impact Analysis at least three Business Days prior to the regularly scheduled ROS meeting.  If a longer review period is required for ERCOT to update the Impact Analysis, ERCOT shall submit a schedule for completion of the Impact Analysis to the ROS chair.

1.3.4.7	Reliability and Operations Subcommittee Vote

(1)	ROS shall consider any OGRR that OWG has submitted to ROS for consideration for which both a OWG Recommendation Report has been posted and an Impact Analysis based on such OWG recommendation (as updated if modified by OWG under Section 1.3.4.6, Operations Working Group Review of Impact Analysis) has been posted on the MIS for at least three days.  The following information must be included for each OGRR considered by ROS:

(a)	The OWG Recommendation Report and Impact Analysis; and

(b)	Any comments timely received in response to the OWG Recommendation Report.

(2)	The quorum and voting requirements for ROS action are set forth in the Technical Advisory Committee Procedures.  In considering action on an OWG Recommendation Report, ROS may:

(a)	Recommend approval of the OGRR as recommended in the OWG Recommendation Report or as modified;

(b)	Reject the OGRR;

(c)	Defer decision on the OGRR;

(d)	Remand the OGRR to the OWG with instructions; or

(e)	Refer the OGRR to another ROS working group or task force with instructions.

(3)	If a motion is made to recommend approval of an OGRR and that motion fails, the OGRR shall be deemed rejected by ROS unless at the same meeting ROS later votes to recommend approval of, remand, or refer the OGRR.  The rejected OGRR shall be subject to appeal pursuant to Section 1.3.4.12, Appeal of Action.

(4)	If ROS recommends approval of an OGRR, ERCOT shall prepare a ROS Recommendation Report, issue the report to TAC and post the report on the MIS within three Business Days of the ROS recommendation concerning the OGRR.  The ROS Recommendation Report shall contain the following items:

(a)	Identification of the submitter of the OGRR;

(b)	Modified Operating Guide language proposed by ROS;

(c)	Identification of the authorship of comments;

(d)	Proposed effective date(s) of the OGRR;

(e)	Recommended priority and rank for any OGRR requiring a change to ERCOT’s computer systems;

(f)	OWG recommendation; and

(g)	ROS recommendation.

1.3.4.8	ERCOT Impact Analysis Based on Reliability and Operations Subcommittee Recommendation Report

For OGRRs not designated Urgent, ERCOT shall review the ROS Recommendation Report and update the Impact Analysis as soon as practicable, but no later than seven days prior to the next regularly scheduled TAC meeting, unless a longer period is warranted due to the complexity of the changes proposed by ROS.  ERCOT shall issue the updated Impact Analysis, if any, to TAC and post it on the MIS within three Business Days of issuance.  If a longer review period is required for ERCOT to update the Impact Analysis, ERCOT shall submit a schedule for completion of the Impact Analysis to the ROS and TAC chairs.

1.3.4.9	PRS Review of Project Prioritization

At its next regularly scheduled meeting, the PRS shall recommend to TAC an assignment of project priority for each OGRR recommended for approval by ROS that requires a change to ERCOT’s computer systems.

1.3.4.10	Technical Advisory Committee Review and Action

(1)	Upon recommendation for approval of an OGRR by ROS and issuance of an Impact Analysis by ERCOT to TAC, TAC shall review the ROS Recommendation Report and the Impact Analysis at its next regularly scheduled meeting; provided that the Impact Analysis is available for distribution to the TAC at least seven days in advance of the TAC meeting.

(2)	The quorum and voting requirements for TAC action are set forth in the Technical Advisory Committee Procedures.  In considering action on a ROS Recommendation Report, TAC shall:

(a)	Approve the ROS Recommendation Report as originally submitted or as modified by TAC;

(b)	Reject the ROS Recommendation Report;

(c)	Defer decision on the merits of the ROS Recommendation Report;

(d)	Remand the ROS Recommendation Report to ROS with instructions; or

(e)	Refer the ROS Recommendation Report to another TAC subcommittee or a TAC working group or task force with instructions.

(3)	If a motion is made to recommend approval of an OGRR and that motion fails, the OGRR shall be deemed rejected by TAC unless at the same meeting TAC later votes to approve, remand, or refer the OGRR.  The rejected OGRR shall be subject to appeal pursuant to Section 1.3.4.12, Appeal of Action.

(4)	If the ROS Recommendation Report is approved by TAC, as recommended by ROS or as modified by TAC, TAC shall review and approve or modify the proposed effective date.

(5)	If TAC approves an OGRR and it does not require an ERCOT project for implementation, or rejects an OGRR, ERCOT shall prepare a TAC Action Report and post it on the MIS within three Business Days.  The TAC Action Report shall contain the following items:

(a)	Identification of the submitter of the OGRR;

(b)	Identification of the authorship of comments;

(c)	Proposed effective date(s) of the OGRR;

(d)	Procedural history;

(e)	ROS recommendation; and

(f)	TAC action.

(6)	The chair of TAC shall report the results of all votes by TAC related to OGRRs to the ERCOT Board at its next regularly scheduled meeting.

(7)	TAC shall consider the Project Priority of each OGRR requiring a change to ERCOT's computer systems and make recommendations to the ERCOT Board.  If TAC recommends approval of an OGRR that requires an ERCOT project which can be funded in the current ERCOT budget cycle based upon its priority and ranking, ERCOT shall prepare a TAC Recommendation Report, issue the report to the ERCOT Board and post the report on the MIS within three Business Days of the TAC recommendation concerning the OGRR.  The TAC Recommendation Report shall contain the following items:

(a)	Identification of the submitter of the OGRR;

(b)	Modified Operating Guide language proposed by TAC, if applicable;

(c)	Identification of the authorship of comments;

(d)	Proposed effective date(s) of the OGRR;

(e)	Priority and rank of the OGRR;

(f)	ROS recommendation; and

(g)	TAC Recommendation.

(8)	If TAC recommends approval of an OGRR that requires a project for implementation that cannot be funded within the current ERCOT budget cycle, ERCOT shall prepare a TAC Recommendation Report and post the report on the MIS within three Business Days of the TAC recommendation concerning the OGRR.  ERCOT shall assign the approved OGRR to the “Unfunded Project List” until the ERCOT Board approves an annual ERCOT budget in a manner that indicates funding would be available in the new budget cycle to implement the project if approved by the ERCOT Board; in such case, the TAC Recommendation Report would be provided at the next ERCOT Board meeting following such budget approval for the ERCOT Board’s consideration under Section 1.3.4.11, ERCOT Board Review and Action.

(9)	Notwithstanding the above, an OGRR on the Unfunded Project List may be removed from the list and provided to the ERCOT Board for approval, as set forth in Protocol Section 21.9, Review of Project Prioritization, Review of Unfunded Project List, and Annual Budget Process.  ERCOT shall maintain the Unfunded Project List to track projects that cannot be funded in the current ERCOT budget cycle.  Any OGRR approved by TAC but assigned to the Unfunded Project List may be challenged by appeal as set forth in Section 1.3.4.12, Appeal of Action.

1.3.4.11	ERCOT Board Review and Action

(1)	The ERCOT Board shall review all OGRRs which impact ERCOT Systems or staffing and can be funded in the current ERCOT budget cycle based upon its priority and ranking.  The quorum and voting requirements for ERCOT Board action are set forth in the ERCOT Bylaws.  In considering action on a TAC Recommendation Report, the ERCOT Board shall:

(a)	Approve the TAC Recommendation Report as originally submitted or as modified by the ERCOT Board;

(b)	Reject the TAC Recommendation Report;

(c)	Remand the TAC Recommendation Report to TAC with instructions.

(2)	If a motion is made to approve a TAC Recommendation Report and that motion fails, the OGRR shall be deemed rejected by the ERCOT Board unless at the same meeting the ERCOT Board later votes to approve or remand the TAC Recommendation Report.  The rejected OGRR shall be subject to appeal pursuant to Section 1.3.4.12, Appeal of Action.

1.3.4.12	Appeal of Action

(1)	Any interested party may appeal directly to the ROS, any OWG action regarding an OGRR.  Such appeal to the ROS must be submitted to ERCOT within ten Business Days after the date of the relevant OWG appealable event.  Appeals made after this time shall be rejected.  Appeals to the ROS shall be posted on the MIS within three Business Days and placed on the agenda of the next available regularly scheduled ROS meeting, provided that the appeal is provided to ERCOT at least 11 days in advance of the ROS meeting; otherwise the appeal will be heard by the ROS at the next regularly scheduled ROS meeting.  An appeal of an OGRR to ROS suspends consideration of the OGRR until the appeal has been decided by ROS.

(2)	Any interested party may appeal directly to the TAC, any ROS action regarding an OGRR.  Such appeal to the TAC must be submitted to ERCOT within ten Business Days after the date of the relevant ROS appealable event.  Appeals made after this time shall be rejected.  Appeals to the TAC shall be posted on the MIS within three Business Days and placed on the agenda of the next available regularly scheduled TAC meeting, provided that the appeal is provided to ERCOT at least 11 days in advance of the TAC meeting; otherwise the appeal will be heard by the TAC at the next regularly scheduled TAC meeting.  An appeal of an OGRR to TAC suspends consideration of the OGRR until the appeal has been decided by TAC.

(3)	Any interested party may appeal directly to the ERCOT Board, any TAC action regarding an OGRR.  Such appeal to the ERCOT Board must be submitted to ERCOT within ten Business Days after the date of the relevant TAC appealable event.  Appeals made after this time shall be rejected.  Appeals to the ERCOT Board shall be posted on the MIS within three Business Days and placed on the agenda of the next available regularly scheduled ERCOT Board meeting, provided that the appeal is provided to the ERCOT General Counsel at least 11 days in advance of the ERCOT Board meeting; otherwise the appeal will be heard by the ERCOT Board at the next regularly scheduled ERCOT Board meeting.  An appeal of an OGRR to the ERCOT Board suspends consideration of the OGRR until the appeal has been decided by the ERCOT Board.

(4)	Any interested party may appeal any decision of the ERCOT Board regarding the OGRR to the PUCT or other Governmental Authority.  Such appeal to the PUCT or other Governmental Authority must be made within 35 days of the date of the relevant appealable event.  If the PUCT or other Governmental Authority rules on the OGRR, ERCOT shall post the ruling on the MIS.

1.3.5	Urgent Requests

(1)	The party submitting an OGRR may request that the OGRR be considered on an urgent basis (“Urgent”) only when the submitter can reasonably show that an existing Operating Guide provision is impairing or could imminently impair ERCOT System reliability or wholesale or retail market operations, or is causing or could imminently cause a discrepancy between a settlement formula and a provision of the ERCOT Protocols.

(2)	If a submitter requests Urgent status for an OGRR, ROS may designate the OGRR for Urgent consideration if the ROS determines that such OGRR requires immediate attention due to:

(a)	Serious concerns about ERCOT System reliability or market operations under the unmodified language; or

(b)	The crucial nature of settlement activity conducted pursuant to any settlement formula; and

(c)	Is of a nature that allows for rapid implementation without negative consequence to the reliability and integrity of the ERCOT System or market operations.

(3)	The Urgent OGRR and Impact Analysis (if available) shall be considered at the earliest regularly scheduled OWG or ROS meeting, or at a special meeting called by the OWG or ROS chair to consider the Urgent OGRR.

(4)	If the submitter desires to further expedite processing of the OGRR, a request for ROS to vote via electronic mail may be submitted to the ROS chair.  The ROS chair may grant the request for voting via electronic mail.  Such voting shall be conducted pursuant to TAC procedures.  If ROS recommends approval of the Urgent OGRR, ERCOT shall submit a ROS Recommendation Report to the TAC within three Business Days after ROS takes action.  The TAC chair may request action from TAC to accelerate or alter the procedures described herein, as needed, to address the urgency of the situation.

(5)	Notice of an Urgent OGRR pursuant to this subsection shall be posted on the MIS.

1.3.6	Operating Guide Revision Implementation

(1)	For OGRRs with no impact to ERCOT systems or staffing, ERCOT shall implement OGRRs on the first day of the month following TAC approval, unless otherwise provided in the TAC Action Report for the approved OGRR.

(2)	For OGRRs with impacts to ERCOT systems or staffing, ERCOT shall implement OGRRs on the first day of the month following ERCOT Board approval, unless otherwise provided in the Board Action Report for the approved OGRR.

(3)	ERCOT shall implement an Administrative OGRR on the first day of the month following the end of the ten Business Day posting requirement outlined in Section 1.3.1, Introduction.

## 1.4	Market Overview

The Electric Reliability Council of Texas (ERCOT) is a not-for-profit, regulated Control Area Authority (CAA) and member of the North American Electric Reliability Corporation (NERC).  The Public Utility Commission of Texas (PUCT) is the principal regulatory authority of ERCOT.  The Federal Energy Regulatory Commission (FERC) has regulatory authority over the DC Tie Line and future interconnections between ERCOT and out of state entities.

The primary responsibility of the ERCOT Control Area Authority is to ensure secure and reliable power grid operation within the ERCOT System in accordance with NERC standards, where applicable and to facilitate the efficient use of the electric transmission system by the market participants.

The ERCOT System market is based on bilateral transactions between buyers and sellers. ERCOT will ensure that the power grid can accommodate market participant schedules.  In addition, ERCOT Control Area Authority will monitor the power grid in real time and provide ancillary services to resolve capacity shortfalls, transmission congestion and maintain reliability.

The ERCOT Control Area Authority only interacts directly with Qualified Scheduling Entities and Transmission and/or Distribution Service Providers to operate the ERCOT System in a reliable and secure manner.

The relationship between the entities is defined in Section 1.7, Entity Definitions and Roles.

## 1.5	Conformance to NERC Policies, Procedures, and Reliability Standards

The Electric Reliability Council of Texas (ERCOT) Operating Guides are for the purpose of outlining specific practices for the ERCOT System.  These practices are consistent with the North American Electric Reliability Corporation (NERC) Operating Policies and standards.  For application in ERCOT, some NERC Policies must be adapted to fit the unique characteristics of the ERCOT System.  Specific necessary adaptations are listed below:

| NERC Policy | ERCOT Adaptation |
| --- | --- |
| Time and Frequency Control | Sustained frequency deviations from 60 Hz result in time error. |
| - Time Error Monitoring | ERCOT will monitor accumulated time error and initiate time corrections. The instantaneous time error is available to all ERCOT Qualified Scheduling Entities (QSEs) on the ERCOT website. When time error is equal to or greater than ±3 seconds, ERCOT may initiate a time correction. The correction will be ended when the error is less than ±0.5 seconds. The time correction may be postponed if it is determined that Load patterns in the immediate future will result in the desired time correction. |
| - Time Error Correction | When a time correction is necessary, ERCOT will adjust scheduled frequency in the following manner. ERCOT will arrange for more or less Resources. Information to be passed along will include the correction frequency (59.98 Hz for fast and 60.02 Hz for slow) and the start time. A time correction may be terminated after five (5) hours, after any hour without a one-half (0.5) second error reduction. The Control Area Authority will provide adequate notice of ending the time correction. |
| Inadvertent Interchange Management | The only Inadvertent Energy will be between ERCOT and Southwest Power Pool (SPP) and/or Comision Federal de Electricidad (CFE). Accounting / payback will be handled according to NERC policy. The hourly difference between a Control Area’s actual net interchange and a Control Area’s scheduled net interchange is classified as inadvertent energy. All inadvertent energy is placed in an Inadvertent Payback Account to be paid back in kind. |
| Control Surveys | Not all of the surveys defined by NERC apply to a system the size of ERCOT and /or a single Control Area interconnection such as ERCOT. |
| Load Shedding and System Restoration | Automatic firm Load shedding will be initiated as follows: Frequency % Load Relief 59.3 Hz 5% 58.9 Hz 10% 58.5 Hz 10% Load shedding will be widely dispersed in each Transmission and/or Distribution Service Provider (TDSP), with no preference to Load Serving Entities (LSEs), and will be accomplished by using high-speed under-frequency relays. The frequency measuring relays shall have a time delay of no more than thirty (30) cycles (or one-half (0.5) seconds for relays that do not count cycles). If the frequency and time values are reached, an irretrievable trip is initiated. Total time from the time when frequency first reaches one of the values specified above to the time Load is interrupted should be no more than forty (40) cycles, including all relay and breaker operating times. Under-frequency relays may be installed on Transmission Facilities under the direction of ERCOT, provided the relays are set at 58.0 cycles or below, are not directional, and have at least 2.0 seconds time delay. Load restoration will be under the direction of the ERCOT Control Area Authority. A TDSP may by mutual agreement, with the approval of the Technical Advisory Committee (TAC), arrange to have all or part of its automatic Load shedding obligation carried by another TDSP. ERCOT will be notified and provided with the details of any such arrangement prior to implementation. |
| Information Exchange – Disturbance Reporting | ERCOT will record the following data from the ERCOT System for frequency deviations of 0.175 Hz or greater and will use this information to generate the ERCOT initial Disturbance Report: - ERCOT and individual QSE control biases. - Net MW Capability (including any capability lost) at the time of the disturbance. - Net System Load (MW) for the hour ending closest to the time of the disturbance. - Scheduled Net Interchange (MW) at the time of the disturbance. - Amount of interruptible Load (MW) tripped. Reference: Protocol Section 6.10.5.4, Responsive Reserve Services Deployment Performance Monitoring Criteria (In Part) …For all frequency deviations exceeding 0.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve Service. ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event or Manual / Dispatch Instruction until ten (10) minutes after the start of the frequency excursion event or Manual / Dispatch Instruction… |
| Reliability Criteria | ERCOT operating reserve requirements are more restrictive than the concepts in the NERC Operating Manual. The ERCOT Responsive Reserve Obligation is a minimum of 2300 MW. |

## 1.6	Operating Definitions

A complete list of definitions is contained within Protocol Section 2, Definitions and Acronyms.  The following definitions apply specifically to reliability and security operation.

It is essential to the reliability of the ERCOT System that all appropriate personnel use and understand the same terms in their daily operations.  The definitions in this section are intended to enable the ERCOT Control Area Authority (CAA), Qualified Scheduling Entities (QSEs) and Transmission and/or Distribution Service Provider (TDSP) operators to effectively communicate on an ongoing basis.

| Capacitor | Produces reactive power (VAR source) for voltage control and causes the system power factor to move towards a leading condition. |
| --- | --- |

| Designated Agent | Any Entity that is authorized to perform actions or functions on behalf of another Entity. |
| --- | --- |

| Generator Reactive Power Sign/Direction Terminology | (1) Lagging power factor operating condition is when VAR flow is out of the generating unit (overexcited generator) and into the transmission system and is considered to be positive (+) flow, i.e., in the same direction as MW power flow. The generator is producing MVARs (2) Leading power factor operating condition is when VAR flow is into the generating unit (underexcited generator) and out of the transmission system and is considered to be negative (-) flow, i.e., in the opposite direction as MW power flow. The generator is absorbing MVARs. |
| --- | --- |
| Inadvertent Energy | The difference between a Control Area’s actual net interchange and a Control Area’s scheduled net interchange. |

| Interchange | a. Net Interchange The algebraic sum of the power flows of the ERCOT Control Area’s interconnections with other Control Areas. Sign convention is that net interchange out of an area is positive while net interchange into an area is negative. b. Scheduled Net Interchange The mutually prearranged intended net power flow on the ERCOT Control Area’s interconnections with other Control Areas. |
| --- | --- |
| Physical Responsive Capability (PRC) | A representation of the total amount of system wide On-line capability that has a high probability of being able to quickly respond to system disturbances. The PRC shall be calculated by (i) determining each Resource meeting the requirements of Section 2.5.2.3, Types of Responsive Reserve, of these Guides, (ii) determining for each Resource the lesser quantity of the latest Net Dependable Capability, the Resource Plan High Operating Limit (HOL), or the telemetered Real Time capability, (iii) multiplying the lesser quantity of each Resource by the Reserve Discount Factor (RDF), (iv) using that result to determine the amount of Responsive Reserve capability then available on each Resource, and (v) the sum, for all Resources, of the Responsive Reserve capability as determined for each Resource. The PRC shall be used by ERCOT to determine the appropriate Emergency Notification and Energy Emergency Alert (EEA) levels. |

| Remedial Action Plan (RAP) | Predetermined operator actions to maintain ERCOT Transmission Grid reliability during a defined adverse operating condition. |
| --- | --- |

| Reserve Discount Factor (RDF) | A representation of the average amount of system wide capability that, for whatever reason, is historically undeliverable during periods of high system demand. The RDF will be verified by ERCOT and then approved by the Reliability and Operations Subcommittee (ROS). |
| --- | --- |
| Special Protection System (SPS) | A protective relay system specially designed to detect abnormal system conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable system performance. |

| Telemetry | Equipment for measuring a quantity (e.g., amps, volts, MW, MVAR, MVA) and transmitting the result to a remote location for indication or recording. |
| --- | --- |

| Time Error | An accumulated time difference between ERCOT system time and the time standard. Time Error is caused by a deviation in ERCOT average frequency from 60.0 Hz. |
| --- | --- |

| Transmission Service Provider (TSP) | An Entity that owns or operates for compensation in this state, equipment or Facilities rated at 60 kV or higher used to transmit electricity, and whose rates for Transmission Service are set by the Public Utility Commission of Texas (PUCT). |
| --- | --- |

| Transmission Line Terminal Sign/Direction Terminology | (1) MW or VAR flow out of the bus and into the line is considered to be positive (+) flow. (2) MW or VAR flow into the bus and out of the line is considered to be negative (-) flow. |
| --- | --- |

## 1.7	Entity Definitions and Roles

### 1.7.1	ERCOT Control Area Authority

The ERCOT Control Area Authority is the regional security coordinator for the ERCOT System and is responsible for all regional security coordination as defined in the NERC Operating Manual and applicable ERCOT Operating Manuals or Guides.

The ERCOT Control Area Authority will deploy all Ancillary Services and dispatch transmission in accordance with the ERCOT Protocols, to ensure operational security and to remedy all Commercially Significant Constraints (CSC) and Operational Constraints.

The ERCOT Control Area Authority shall operate the ERCOT Transmission Grid in compliance with Good Utility Practice, NERC, and ERCOT standards, policies, guidelines and operating procedures, including, but not limited to:

- These ERCOT Operating Guides;

- NERC Operating Manuals and Reliability Standards as references during normal and emergency operations of the ERCOT System Transmission Grid; and,

- Individual transmission owners Operating Procedures submitted to ERCOT Control Area Authority to identify specific operating problems that could affect operation of the interconnected ERCOT System Transmission Grid.

### 1.7.2	Qualified Scheduling Entities

Qualified Scheduling Entities (QSE) will provide the primary information interface for market participants with the ERCOT Control Area Authority.  Market participants wishing to transfer energy or services during the operating hour from one participant to another, or from generation to load, or from the participant to ERCOT, or from ERCOT to the participant will submit Balanced Schedules to the ERCOT Control Area Authority through a Qualified Scheduling Entity.

QSEs are not regulated by the Public Utility Commission of Texas.

### 1.7.3	Transmission Operator (TO)

Transmission Operators (TOs) are the subset of Transmission Service Providers (TSPs) or Transmission and/or Distribution Service Providers (TDSPs) that is charged with continuous communication (7x24 basis) with the ERCOT Control Area Authority (CAA) and carrying out Dispatch Instructions directly or on behalf of represented TDSPs.  Each TSP or TDSP will designate either itself or another TSP or TDSP to perform the functions of a TO. TOs must meet all requirements identified in the ERCOT Protocols for TDSPs and TSPs in addition to those requirements stated below for all Transmission Facilities represented:

- Operate and manage the electric Transmission Facilities between energy sources and the point of delivery;

- Accomplish switching of transmission elements.  Develop, maintain, and implement transmission switching policies and procedures to provide for transmission reliability;

- Coordinate emergency communications between the TDSP or TSP and ERCOT CAA;

- Monitor the loading of the transmission system(s);

- Notify the ERCOT CAA of changes to the status of all Transmission Facilities;

- Act as Single Point of Contact for Transmission Outages;

- Maintain operational metering; and,

- Implement Black Start.

Transmission Operators shall provide the ERCOT CAA their written backup control plans to continue operation in the event the Transmission Operator’s control center becomes inoperable.

Each backup control plan shall be reviewed and updated annually and shall meet the following minimum requirements:

- Include description of actions to be taken by TO personnel to avoid placing a prolonged burden on ERCOT and other Market Participants.

- Include description of specific functions and responsibilities to be performed to continue operations from an alternate location.

- Includes procedures and responsibilities for maintaining basic voice communications capabilities with ERCOT.

- Includes procedures for backup control function testing and the training of personnel.

As an option, the backup plan may include arrangements made with another entity to provide the minimum backup control functions in the event the TO’s primary functions are interrupted.

### 1.7.4	Resource Entity

Resource Entities include Power Generation Companies, Opt-in generation, NOIE generation, federal generation facilities and LSEs representing load being used as a resource.

Any Generation Resource that introduces energy into the ERCOT grid must be represented by a Resource Entity.  The sale of the generation produced is negotiated bilaterally with other Market Participants (MPs) with the exception of energy produced as Ancillary Services.  The schedule for the power sale is communicated to the QSE that represents the Generation Entity in the ERCOT Market System.  The QSE will communicate an overall Balanced Schedule for the QSE, including the Generation Entity, to ERCOT.

PGCs that offer Regulation Service and Responsive Reserve Services must be directly connected to the QSE for the purpose of receiving a regulation signal in Real Time.

Reference:  Protocol Section 22, Attachment A, Standard Form Black Start Agreement (In Part)

…Section 8. Operation.

C.	Delivery.

(1)	ERCOT shall notify Participant, through its QSE, when the Black Start Resource must black start.

(2)	If the ERCOT Transmission Grid at the Black Start Resource becomes deenergized and if Participant cannot communicate with either ERCOT or the TDSP serving the Black Start Resource, then Participant shall follow the procedures specified for the Black Start Resource under ERCOT’s Black Start Plan in the Operating Guides, but Participant shall not commence delivering electric energy into the ERCOT System without specific instructions to do so from either ERCOT or the TDSP serving the Black Start Resource...

### 1.7.5	Load Serving Entities (LSE)

LSEs include Non Opt-in Entities, the Texas General Land Office and Competitive Retailers.  These are the only organizations authorized to sell electricity directly to retail customers.  An LSE will forecast its contracted load and negotiate bilaterally with Resource Entities to obtain the forecasted energy.  The schedule resulting from this negotiation will be communicated to the QSE, who in turn will communicate an overall Balanced Schedule for the QSE to ERCOT.

## 1.8	Operational Training

### 1.8.1	Operator Training Objectives

A primary objective of each Operating Entity within the ERCOT System shall be to train Operators such that they will possess the necessary skills and ability to direct the operation of the power system in accordance with the Protocols, these Operating Guides, ERCOT Control Area Operator Procedures as well as individual entity operating goals, plans and procedures.

These training objectives are:

- Maintain the safety of personnel, even during emergency situations involving complex switching and manipulation of control elements.

- Protect system components, particularly major power system elements from serious life degradation or harm.

- Operate the system in a secure manner to minimize violations of operating limits, avoiding customer outages where reasonably possible, and avoiding unstable situations that might result in widespread outages or blackouts.

- Operate the system as economically as possible within continually changing operating constraints.

- Restore the system to its normal operating state as rapidly as practical after a disturbance.

### 1.8.2	System Operator Training Requirements

The System Operator Training Program applies to all Control Area Authority and Transmission Operators who are responsible for the Real-Time operation or reliability monitoring of the bulk electric system and those Qualified Scheduling Entity (QSE) Operators who represent Generation Resources or Loads acting as Resources (LaaRs).  At least thirty-two (32) hours per year of system emergency training and drills, appropriate to each class of operator, must be included in the training program.  QSE Operators who do not represent Generation Resources or LaaRs must participate in at least eight (8) hours per year in system emergency training and drills.

For those operators required to obtain thirty-two (32) hours annually, at least eight (8) hours must be from simulations or realistic drills.

Participation in emergency simulations, Severe Weather Drills, ERCOT Black Start Training, and portions of the ERCOT Operations Training Seminar that relate to North American Electric Reliability Corporation (NERC) recommended topics can be used to satisfy this requirement.  Task specific training carried out internally within an Entity will be considered in full compliance with this requirement.  Training documentation, including curriculum, training methods, and individual training records, shall be available for verification during audits.

### 1.8.3	ERCOT Operations Training Seminar

ERCOT will host a training seminar that, as a minimum, will be held annually.  The purpose of the training seminar is to provide a forum for system wide problems to be effectively addressed and to maintain an operator training consistency across all ERCOT System Operating Entities.

The seminar provides a forum for all ERCOT System Entity Operators and ERCOT System Operators, to meet and analyze common topics and issues as well as participate in formal training sessions.

### 1.8.4	ERCOT Black Start Training

ERCOT shall periodically conduct system restoration seminars for all Transmission and Distribution Service Providers, Qualified Scheduling Entities, Generation Entities and other Market Participants, in accordance with Protocol Section 6.5.8, Black Start Service.

### 1.8.5	ERCOT Severe Weather Drill

ERCOT shall conduct a Severe Weather Drill one time a year.  This drill will be used to test the scheduling and communication functions of the primary and/or back up centers and train operators in emergency procedures.  All Qualified Scheduling Entities that provide Ancillary Services and Transmission Operators are required to participate in the drill.  ERCOT will appoint an ERCOT Drill Coordinator who, with assistance from the Operations Working Group, will develop and coordinate the annual Severe Weather Drill.  The Operations Working Group will review and critique the results of completed Severe Weather Drills to ensure effectiveness and recommend changes as necessary.  ERCOT Compliance will verify and report Entity participation to the Reliability and Operations Subcommittee.

### 1.8.6	Criteria For The Selection Of Operators

To be selected as Operators, candidates should be capable of directing other personnel in their own organization and, at the same time, work harmoniously with the ERCOT System Operators and other Entities’ Operators.  In addition, they must have a high intellectual ability, above average reasoning, mathematical ability, well-developed communication skills and reasonable mechanical aptitude.  To ensure compliance with these criteria, a screening and selection procedure must be considered for prospective Operators.  This procedure should include the following:

- Evaluation against a detailed job description.

- Analysis of the candidate's past work record to determine character, reputation, and previous experience.

- In-depth interview with each candidate.

- Evaluation of intelligence, logic, mathematical, and communication skills along with psychological fitness.

### 1.8.7	Training Practices

Each Operating Entity should establish a clear requirement, define and develop a systematic approach in administering the training, and provide the necessary feedback as a measurement of curriculum suitability and trainee progress.  Each Operating Entity should recognize the importance of training and provide sufficient Operator participation through adequate staffing and work-hour scheduling.

## 1.9	Document Revisions

Change History

| Issue/Date | Reason for issue |
| --- | --- |
| Version 1.0 February 28, 2001 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee |
| Version 1.1 April 10, 2001 | Reference to Market Oversight Division corrected, added ROS responsibility for submitting PRR, minor formatting changes |
| May 1, 2002 | Formatting |
| July 1, 2002 | OGRR102 |
| October 1, 2002 | OGRR115 |
| December 1, 2002 | Corrected diagrams in Sections 1.2 & 1.4. |
| January 1, 2003 | OGRR120 revised Section 1.7.3 to add a backup plan requirement for TOs. |
| March 1, 2003 | Revised header to state “Section.” |
| May 1, 2003 | Revised diagrams on pages 3 & 5 to state “ERCOT Operating Guides” instead of System Operating Guide. Added language from OGRR128 to allow for administrative update of Protocols references included in the Operating Guides. |
| October 1, 2003 | OGRR132 |
| June 1, 2004 | OGRR143 |
| November 1, 2004 | OGRR150, OGRR151 and corrected typographical errors in Protocol references |
| June 1, 2005 | Admin OGRR168 |
| November 4, 2005 | OGRR175 |
| June 1, 2006 | OGRR182 |
| December 1, 2006 | OGRR186 |
| February 1, 2007 | Admin OGRR190 |
| May 1, 2007 | Admin OGRR195 |
| September 1, 2007 | OGRR202 |
| May 1, 2008 | OGRR205, Admin OGRR207 |
| March 1, 2009 | OGRR213 |
| March 5, 2009 | OGRR220 |
| April 1, 2009 | OGRR219 |
| May 1, 2009 | OGRR213 (unboxed due to effective date) |
| July 1, 2009 | OGRR218 |
| October 1, 2009 | OGRR229 |