| OGRR Number | 232 | OGRR Title | Revise the Process for Submitting Biennial Unit Reactive Limits (Lead and Lag) |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | September 15, 2009 |  |  |
| Operating Guide Sections Requiring Revision |  | 3.1.4.3.1, Corrected Unit Reactive Limits (CURL) 3.1.4.3.2, Non-Coordinated Testing 3.1.4.3.3, Coordinated Testing 6.2.3, Biennial Unit Reactive Limits (Lead and Lag) Verification (deleted) |  |  |
| Proposed Effective Date |  | To be determined |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) deletes Section 6.2.3. The form within that Section is no longer used as results are submitted through the Market Information System (MIS). This OGRR also updates other sections to align with the current process. |  |  |
| Overall Market Benefit |  | Market Participants will be less confused if they use the proposed process of submitting biennial unit reactive limit tests using the MIS vs. using an outdated form. This change allows the Power Generation Company (PGC) to accomplish the biennial reactive limit test without transmission constraints. |  |  |
| Overall Market Impact |  | Unknown. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Procedural History |  | - On 7/9/09, OGRR232 was posted. - On 7/22/09, the CEO Revision Request Review for OGRR232 was posted. - On 8/17/09, Luminant comments were posted. - On 8/19/09, the Operations Working Group (OWG) considered OGR232. - On 9/8/09, an Impact Analysis was posted. - On 9/15/09, OWG again considered OGRR232. |  |  |
| OWG Decision |  | On 8/19/09, OWG was in consensus to recommend approval of OGRR232 as amended by the 8/17/09 Luminant comments and as revised by OWG. On 9/15/09, OWG was in consensus to table OGRR232 for one month. |  |  |
| Summary of OWG Discussion |  | On 8/19/09, the Luminant comments were discussed. OWG agreed that although a TAC-approved procedure for granting an exemption from the reactive capability test currently exists, a new one would be developed. On 9/15/09, ERCOT Staff requested clarification on the language which would require TAC to review a procedure. OWG participants stated that the intention is for ERCOT to develop the procedure for TAC to consider and approve. ERCOT Staff requested additional time to review the language and agreed to work with Market Participants on a solution to present at the next OWG meeting. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Reduces confusion by clarifying that Market Participants should use the proposed process vs. using an outdated form. This change also allows the PGC to accomplish the biennial unit reactive limit test without transmission constraints. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Luminant 081709 | Proposed language changes which would require certain exemptions of seasonal units be granted using a TAC-approved procedure. |

| Original Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen |
| Company | Lower Colorado River Authority (LCRA) |
| Market Segment | Cooperative |

Proposed Guide Language Revision

- 3.1.4.3.1	Corrected Unit Reactive Limits (CURL)

The reactive capability curve for each unit on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) containing the most limiting elements for the leading and lagging reactive output.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing may be produced on the corrected reactive capability curve.  The corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURL) at the unit terminals that ERCOT Planning and ERCOT Operations will use for their studies.  ERCOT Operations, after reviewing the updated curves and checking them for reasonableness, will forward copies to the Steady State Working Group (SSWG), for use in modeling such capability in the ERCOT transmission planning cases.  If ERCOT finds the submitted CURL unreasonable, ERCOT will follow  Section 3.1.4.3.4, ERCOT Implementation, for implementation of this procedure.  The reactive capability represented in the CURL will be used in operation and planning studies.  For all intents and purposes, this new curve would take the place of the original manufacturer’s unit reactive capability curve.

- 3.1.4.3.2	Non-Coordinated Testing

The QSE representing the generating unit shall give ERCOT at least two (2) hours advance notice prior to the start of the test.  ERCOT retains the right to cancel the reactive test if ERCOT believes, in its sole judgment, that conducting the test at the requested time could jeopardize the reliability of the ERCOT System.  For example, ERCOT can cancel a requested leading capability test during a time when system voltages are low or expected to be low due to factors such as high import power levels, transmission line Outages, capacitor bank Outages, or generating unit Outages or exciter limitations.

Tests to verify maximum lagging reactive capability shall be conducted during times when ERCOT System Loads are typically high during the months of May through September or when the ERCOT Load is in excess of 50,000 MW, but not necessarily at the time of system peak.  Units being tested shall be operating at or above ninety-five percent (95%) of net dependable real power (MW) output.  If the unit being tested is unable to achieve adequate lagging reactive capability per the CURL, the unit, at its discretion, may utilize the capability of another unit in the same plant to offset (take in VARs) the lagging test that is under way.  This circulation of VARs must leave the high side of the Generator Step-Up (GSU) of the unit being tested and flow through the GSU of the unit taking in the VARs.  Under no circumstances shall VARs be circulated between units on the same low side bus.

Tests to verify maximum leading reactive capability shall be conducted during times when ERCOT System Loads are typically low during the months of October through April or when the ERCOT Load is less than 35,000 MW.  Units being tested shall be operating at a real power (MW) output representative of its usual loading during such light Load periods.

The PGC shall measure the tested reactive capability at the generator terminals minus the auxiliary reactive consumption.  Additionally, the tested reactive capability shall be measured at the high side of the generator step-up transformer if metering is available. If metering is not available at the high side, the PGC shall calculate the reactive capability at the high side.  Both high side and generator terminal values are required  and must be submitted through the MIS.

The QSE representing a generating unit shall be responsible for scheduling reactive verification tests in accordance with the conditions outlined above.

ERCOT shall have the option to waive the requirement to test and verify the maximum leading reactive capability of any generating unit that seldom runs during such light Load periods in accordance with the TAC-approved procedure for exemption of Leading Reactive Capability Tests for seasonal units.  The granting of such a waiver shall be effective for two (2) years.  Results of the initial and two (2)-year test shall be posted to the Market Information System (MIS).

The minimum duration for any reactive verification test, leading or lagging, is fifteen (15) minutes.  The corrected curves (CURL) should be posted in the PGC’s control room, where the tests are conducted, at the QSE’s Real Time/generation dispatch desk, and copies should be provided to ERCOT Operations.  During any test, the unit must maintain its generator cooling system at normal operating level.  Tests will be conducted to produce MVARs at a level not less than ninety-percent (90%) of the amount indicated by the existing reactive capability curve (original manufacturer’s unit reactive capability curve, or the most recent CURL).

The QSE representing a generating unit shall be responsible for the timely and accurate reporting of test results to ERCOT.  The QSE representing a generating unit shall be responsible for the timely submittal to ERCOT of an updated CURL reflecting any known changes in the reactive output of the unit.  All required data fields on the MIS must be properly completed for a test to be considered valid.

- 3.1.4.3.3	Coordinated Testing

Coordinated Testing is the testing of a generator’s reactive capability to verify the generating unit’s most current CURL.  The verification test will be a coordinated effort between the PGC, the PGC’s QSE, the TO which the PGC is connected, and ERCOT Operations.  Coordinated Testing is at the option of the PGC or can be ordered by ERCOT if a retest is required for an established non-valid test performed using the Non-Coordinated Testing Procedure.

The PGC requesting to perform a coordinated test will provide ERCOT Operations Engineering Support and the TO with a minimum of forty-eight (48) hours notice of the proposed test date.  Requests shall be made weekdays between 8 AM to 5 PM excluding recognized ERCOT holidays.  Upon receipt of a request for test, ERCOT Operations Engineering Support and the TO will evaluate the expected conditions and determine whether transmission system conditions conducive to a valid test can be created through coordinated network switching, modification of the generation reactive Dispatch of nearby generating units, or by some other means.  Having established that suitable transmission system conditions exist or can be created, ERCOT Operations Engineering Support and the TO shall provide the PGC and the QSE a concurrence of the test time and date or a rejection of the test time and date within twenty-four (24) hours of the receipt of the request.

The coordinated test shall begin and end within the ERCOT Operations Engineer’s standard work day (nominally 8 AM to 5 PM).  Since leading tests will often occur in off-peak periods, the coordinated leading test shall begin and end at times agreed upon by ERCOT, the TO, QSE and PGC.  The minimum duration for any reactive verification test, leading or lagging, is fifteen (15) minutes.  The corrected curves (CURL) should be posted in the PGC’s control room, where the tests are conducted, at the QSE’s Real Time/generation Dispatch desk, and copies should be provided to ERCOT Operations.  The testing period shall be scheduled such that adequate time is given for any transmission switching that may be performed to accommodate adequate system conditions for the appropriate reactive test.  During the test, the QSE Operator shall be in communication with the TO in order to coordinate the reactive output of adjacent units, capacitor switching, reactor switching, and any other activity needed to perform the scheduled reactive test accurately.

LAGGING REACTIVE TESTS

Generating units shall be tested to verify lagging reactive capability at or above ninety-five percent (95%) of net dependable real power (MW) output as indicated on the CURL.  It is during times when ERCOT System Loads are typically high and transmission system voltages are relatively low (specifically during the months of May through September or when the ERCOT Load is in excess of 50,000 MW) that maximum lagging capability is most likely to be needed.  The transmission voltage at the switchyard to which the generating unit is connected should be at or below the ERCOT currently scheduled voltage prior to starting the test.  All efforts should be made to maintain the ERCOT Voltage Profile during the test, but this may be varied at ERCOT’s discretion.  If the unit being tested is unable to achieve adequate lagging reactive capability per the CURL, the unit, at its discretion, may utilize the capability of another unit in the same plant to offset (take in VARs) the lagging test that is under way.  This circulation of VARs must leave the high side of the GSU of the unit being tested and flow through the GSU of the unit taking in the VARs.  Under no circumstances shall VARs be circulated between units on the same low side bus.

LEADING REACTIVE TESTS

Generating units shall be tested to verify leading reactive capability at a MW loading level representative of expected generating unit MW loading during minimum Load conditions as indicated on the CURL.  It is during times when ERCOT System Loads are typically light and transmission system voltages are relatively high (specifically during the months of October through April or when the ERCOT Load is less than 35,000 MW) that maximum leading capability is most likely to be needed.  The transmission voltage at the switchyard to which the generating unit is connected should be at or above the ERCOT currently scheduled voltage prior to starting the test.  All efforts should be made to maintain the ERCOT Voltage Profile during the test, but this may be varied at ERCOT’s discretion.  At ERCOT’s sole discretion, the requirement to test leading capability may be waived for peaking generating units which seldom, if ever, run during light Load conditions.

The PGC shall measure the tested reactive capability at the generator terminals.  The reading recorded shall represent the net MVAR output of the generator and shall have the unit’s auxiliary reactive consumption deducted from the generator’s gross reactive output at the machine’s terminals.  Additionally, the tested reactive capability shall be measured at the high side of the generator step up transformer if metering is available.  If metering is not available at the high side, the PGC shall calculate the reactive capability at the high side.  Both high side and generator terminal values are required on the  MIS for proper submittal of the test results.

The QSE representing a generating unit shall be responsible for scheduling reactive tests in accordance with the conditions outlined above, and for the timely and accurate reporting of test results to ERCOT.  All test documents (the CURL and the CURL with the test point indicated) shall be submitted by the PGC’s QSE.  All required data fields on the MIS must be properly completed for a test to be considered valid.