| NOGRR Number | 027 | NOGRR Title | Revise the Process for Submitting Biennial Unit Reactive Limits (Lead and Lag) |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | December 16, 2009 |  |  |
| Nodal Operating Guide Sections Requiring Revision |  | 3.3.2.1, Corrected Unit Reactive Limits (CURL) 3.3.2.2, Non-Coordinated Reactive Testing 3.3.2.3, Coordinated Reactive Testing Section 8, Attachment E, Biennial Unit Reactive Limits (Lead and Lag) Verification (delete) |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) deletes Attachment E, Biennial Unit Reactive Limits (Lead and Lag) Verification, in Section 8. Attachment E is no longer used as test results are submitted through the Market Information System (MIS) Certified Area. This NOGRR also updates other sections to align with the current process. |  |  |
| Overall Market Benefit |  | Market Participants will be less confused if they use the proposed process of submitting biennial unit reactive limit tests using the MIS Certified Area vs. using an outdated form. This change allows the power generation company to accomplish the biennial reactive limit test without transmission constraints. |  |  |
| Overall Market Impact |  | Unknown. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Procedural History |  | - On 7/17/09, NOGRR027 and the CEO Revision Request Review were posted. - On 8/19/09, the Operations Working Group (OWG) considered NOGRR027. - On 9/8/09, an Impact Analysis was posted. - On 9/15/09, OWG again considered NOGRR027. - On 10/20/09, ERCOT comments were posted. - On 10/21/09, OWG again considered NOGRR027. - On 11/17/09, OWG again considered NOGRR027. - On 12/16/09, OWG again considered NOGRR027. |  |  |
| OWG Decision |  | On 8/19/09, OWG was in consensus to recommend approval of NOGRR027 as revised by OWG. On 9/15/09, OWG was in consensus to table NOGRR027 for one month. 10/21/09, OWG was in consensus to table NOGRR027 for one month. On 11/17/09, OWG was in consensus to table NOGRR027 for one month. On 12/16/09, OWG was in consensus to table NOGRR027 for one month. |  |  |
| Summary of OWG Discussion |  | On 8/19/09, the Luminant comments for the corresponding Operating Guide Revision Request (OGRR) 232, Revise the Process for Submitting Biennial Unit Reactive Limits (Lead and Lag), were discussed. OWG agreed that the language changes proposed by their comments are also necessary in NOGRR027 to keep the Nodal Operating Guides synchronized. On 9/15/09, ERCOT Staff requested clarification on the language which would require TAC to review a procedure. OWG participants stated that the intention is for ERCOT to develop the procedure for TAC to consider and approve. ERCOT Staff requested additional time to review the language and agreed to work with Market Participants on a solution to present at the next OWG meeting. On 10/21/09, OWG discussed the need to review and compare the test requirements on the MIS with what is being struck by this NOGRR and decide if the requirements/limits should be part of the Operating Guide language. OWG also discussed the language pertaining to testing that can only be conducted when the Load is less than 35,000 MW and requested that ERCOT review if in fact tests could only be performed during that time or, if units are capable, they could perform their test at any time. On 11/17/09, there was discussion regarding the limitations to conduct tests when Load is less than 35,000 MW. It was asked that ERCOT develop language that would allow units to be tested outside of current threshold with the understanding that ERCOT would have discretion to either approve or deny the request for those tests. On 12/16/09, there was concern regarding ERCOT comments and a request was made to have ERCOT work with Market Participants to develop language that would address when units could be tested and to discuss the need for the test form to be included in the Nodal Operating Guides. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Reduces confusion by clarifying that Market Participants should use the proposed process vs. using an outdated form. This change also allows the power generation company to accomplish the biennial unit reactive limit test without transmission constraints. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 102009 | Proposed language changes to clarify the requirement for ERCOT to post data to the MIS Certified Area and changes regarding ERCOT’s procedures on voltage control and the testing and utilization of reactive Resources. |

| Original Sponsor |  |
| --- | --- |
| Name | Jack Thormahlen |
| Company | Lower Colorado River Authority (LCRA) |
| Market Segment | Cooperative |

Proposed Guide Language Revision

- 3.3.2.1	Corrected Unit Reactive Limits (CURL)

The reactive capability curve for each unit on the ERCOT System shall be submitted to ERCOT through the Market Information System (MIS) Certified Area and must contain the most limiting elements for the leading and lagging reactive output.  The limiting factors such as under-excitation limiters, over-excitation limiters, ambient temperature limitations across the MW range of the unit at the unit terminals or any other factor that limits the reactive output of the unit and is verifiable through engineering calculations or testing may be produced on the corrected reactive capability curve. The corrected reactive capability curve establishes the Corrected Unit Reactive Limits (CURL) at the unit terminals that ERCOT Planning and ERCOT Operations will use for their studies.  ERCOT Operations, after reviewing the updated curves and checking them for reasonableness, will forward copies to the Steady State Working Group (SSWG) for use in modeling such capability in the ERCOT transmission planning cases.  If ERCOT finds the submitted CURL unreasonable, ERCOT will follow Section 3.5, ERCOT Implementation.

- 3.3.2.2	Non-Coordinated Reactive Testing

(1)	The QSE representing the generating unit shall give ERCOT at least two hours advance notice prior to the start of the test.  ERCOT shall notify the host TO prior to the test.  ERCOT retains the right to cancel the reactive test if ERCOT believes, in its sole judgment, that conducting the test at the requested time could jeopardize the reliability of the ERCOT System.  For example, ERCOT can cancel a requested leading capability test during a time when system voltages are low or expected to be low due to factors such as high import power levels, transmission line Outages, capacitor bank Outages, or generating unit Outages or exciter limitations.

(2)	Tests to verify maximum lagging reactive capability shall be conducted during times when ERCOT System Loads are typically high, during the months of May through September or the ERCOT System Load is no less than 50,000 MW, but not necessarily at the time of system peak.  Units being tested shall be operating at or above 95% of net dependable real power (MW) output.  If the unit being tested is unable to achieve adequate lagging reactive capability per the CURL, the unit, at its discretion, may utilize the capability of another unit in the same plant to offset (take in VARs) the lagging test that is under way.  This circulation of VARs must leave the high side of the Generator Step-Up (GSU) of the unit being tested and flow through the GSU of the unit taking in the VARs.  Under no circumstances shall VARs be circulated between units on the same low side bus.

(3)	Tests to verify maximum leading reactive capability shall be conducted during times when ERCOT System Loads are typically low, during the months of October through April or when the ERCOT Load is less than 35,000 MW.  Units being tested shall be operating at a real power (MW) output representative of its usual loading during such light Load periods.

(4)	The Resource Entity shall measure the tested reactive capability on the low side of the generator terminals.  The reading recorded shall represent the net MVAR output of the generator and shall have the unit’s auxiliary reactive consumption deducted from the generator’s gross reactive output at the machine’s terminals.  Additionally, the tested reactive capability shall be measured at the high side of the generator step-up transformer if metering is available.  If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side.  Both high side and generator terminal values are required and must be submitted through the MIS Certified Area.

(5)	The QSE representing a generating unit shall be responsible for scheduling reactive verification tests in accordance with the conditions outlined above.  If ERCOT does not issue an alternative reactive testing interval, the resource shall complete a reactive qualification test at least every two years.

(6)	ERCOT shall have the option to waive the requirement to test and verify the maximum leading reactive capability of any generating unit that seldom runs during such light Load periods in accordance with the TAC-approved procedure for exemption of Leading Reactive Capability Tests for seasonal units.  The granting of such a waiver shall be effective for two years.  Results of the initial and two-year test shall be posted to the Market Information System (MIS) Certified Area.

(7)	The minimum duration for any reactive verification test, leading or lagging, is 15 minutes.  The CURL should be posted in the Resource Entities control room, where the tests are conducted, at the QSE’s Real-Time/generation dispatch desk, and copies should be provided to ERCOT Operations.  During any test, the unit must maintain its generator cooling system at normal operating level.  Tests will be conducted to produce MVARs at a level not less than 90% of the amount indicated by the existing reactive capability curve (original manufacturer’s unit reactive capability curve, or the most recent CURL).

(8)	The QSE representing a generating unit shall be responsible for the timely and accurate reporting of test results to ERCOT.  The QSE representing a generating unit shall be responsible for the timely submittal to ERCOT of an updated CURL reflecting any known changes in the reactive output of the unit.  A QSE must properly complete all required data fields in the MIS Certified Area for a test to be considered valid.

- 3.3.2.3	Coordinated Reactive Testing

(1)	“Coordinated Testing” is the testing of a generator’s reactive capability to verify the generating unit’s most current CURL.  The verification test will be a coordinated effort between the Resource Entity, the Resource Entity’s QSE, the TO which the Resource Entity is connected, and ERCOT Operations.  Coordinated Testing is at the option of the Resource Entity.  Coordinated Testing can be ordered by ERCOT if a retest is required.

(2)	The Resource Entity requesting to perform a Coordinated Test will provide ERCOT Operations and the TO with a minimum of 48 hours notice of the proposed test date. Requests shall be made between 0800 and 1700 on Business Days.  Upon receipt of a request for test, ERCOT Operations and the TO will evaluate the expected conditions and determine whether transmission system conditions conducive to a valid test can be created through coordinated network switching, modification of the generation reactive dispatch of nearby generating units, or by some other means.  Having established that suitable transmission system conditions exist or can be created, ERCOT Operations, and the TO shall confirm with the Resource Entity and the QSE the agreed upon test time and date or a rejection of the test time and date within 24 hours of the receipt of the request.

(3)	The Coordinated Test shall begin and end within the standard work day (nominally 0800 to 1700).  Since leading tests will often occur in off-peak periods, the coordinated leading test shall begin and end at times agreed to by ERCOT, the TO, QSE and Resource Entity. The minimum duration for any reactive verification test, leading or lagging, is 15 minutes.  The CURL should be provided to ERCOT Operations and posted in the Resource Entity’s control room and at the QSE’s Real-Time/generation dispatch desk.   The testing period shall be scheduled such that sufficient time is given for any transmission switching.  During the test, the QSE operator shall be in communication with the TO in order to coordinate the reactive output of adjacent units, capacitor switching, reactor switching, and any other activity needed to perform the scheduled reactive test accurately.

(4)	Lagging Reactive Tests - Generating units shall be tested to verify lagging reactive capability at or above 95% of net dependable real power output as indicated on the CURL.  Maximum lagging capability is most likely to be needed during times when ERCOT System Loads are typically high and transmission system voltages are relatively low, specifically during the months of May through September or when the ERCOT System Load is no less than 50,000 MW.  The transmission voltage at the switchyard to which the generating unit is connected should be at or below the ERCOT currently scheduled voltage prior to starting the test.  If the unit being tested is unable to achieve adequate lagging reactive capability per the CURL, the unit, at its discretion, may utilize the capability of another unit in the same plant to offset (take in VARs) the lagging test that is under way.  This circulation of VARs must leave the high side of the GSU of the unit being tested and flow through the GSU of the unit taking in the VARs.  Under no circumstances shall VARs be circulated between units on the same low side bus.

(5)	Leading Reactive Tests - Generating units shall be tested to verify leading reactive capability at a MW loading level representative of expected generating unit MW loading during minimum Load conditions as indicated on the CURL.  Maximum leading capability is most likely to be needed when ERCOT System Loads are typically light and transmission system voltages are relatively high, specifically during the months of October through April or when the ERCOT load is less than 35,000 MW.  The transmission voltage at the switchyard to which the generating unit is connected should be at or above the ERCOT currently scheduled voltage prior to starting the test.  At ERCOT’s sole discretion, the requirement to test leading capability may be waived for peaking generating units which seldom, if ever, run during light Load conditions.

(6)	The Resource Entity shall measure the tested reactive capability at the generator terminals.  The reading recorded shall represent the net MVAR output of the generator and shall have the unit’s auxiliary reactive consumption deducted from the generator’s gross reactive output at the machine’s terminals.  Additionally, the tested reactive capability shall be measured at the high side of the generator step up transformer if metering is available.  If metering is not available at the high side, the Resource Entity shall calculate the reactive capability at the high side.  Both high side and generator terminal values are required for proper submittal of the test results.

(7)	The QSE representing a generating unit shall be responsible for scheduling reactive tests in accordance with the conditions outlined above, and for the timely and accurate reporting of test results to ERCOT.  All test documents (the CURL and the CURL with the test point indicated) shall be submitted by the Resource Entity’s QSE.  The Resource Entity must properly complete all required data fields in the MIS Certified Area for a test to be considered complete.