## Slide 1: PDCWG Report to ROS
March 11, 2010
Sydney Niemeyer

## Slide 2: PDCWG Activities
Will meet March 10.
  Review February and remaining January disturbances.
  Operating Guide and Protocol synchronization.
  Review and prepare report on Wind Event January 28, 2010.
  PRR833 Primary Frequency Response Requirement from Existing WGRs. – Submitted recommendation to the ROS.
  Updated Scope.
Next meeting April 7.

## Slide 3
CPS1 = 150.46*
*Unofficial score.

## Slide 4
*
*

## Slide 5
*

## Slide 6
of ERCOT Frequency
January 28, 2010
June 1, 2004
April 17, 2006

## Slide 7
February 18, 2010

## Slide 8
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 142.35*
*Unofficial score

## Slide 9
*ERCOT as a single control area is exempt from CPS2. These scores are For Information Only
90.60

## Slide 12: Comparison of Governor Deadband & Droop Settings of a Single 600 MW Unit
A 0.01666 Hz Deadband with a Straight Line Proportional 5% Droop Curve Compared to a 0.036 Hz Deadband with a “Step” Straight Line Proportional 5% Droop Curve from the Deadband.
Sydney Niemeyer – February 9, 2010

## Slide 13: Governor Settings Prior to November 2008
2008 Had Ten Months of Operation with no Governor setting changes.
  ERCOT Operating Guides called for a maximum +/-0.036 Hz deadband on Governors.
  5% Droop Setting with no clarification as to implementation. With or without a step function at the deadband.
  To meet the 5% droop performance, Governors were encouraged to “step” into the 5% droop curve at the deadband.

## Slide 14: Governor Settings After November 3, 2008
Deadbands were decreased to +/-0.0166 Hz (1 rpm on a 3600 rpm turbine).
The Droop curve implemented was a straight line proportional curve from the deadband eliminating any “step” function.
Initially only 4 Unit’s Governors were changed. Total Capacity of 2486 MW or approximately 82.8 MW/0.1 Hz of Primary Frequency Response.
The coordinated Boiler Control System implemented the same Droop curve and deadband as the turbine Governor.
Additional Units changed their Governor settings throughout 2009 and 2010, mostly after July 2009.

## Slide 15: Status as of March 1, 2010
Units with Governors presently set with an intentional deadband less than or equal to +/-0.01666 Hz and droop curve with no step function.
  11,767 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    4139 MW Coal
    3780 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    399 MW Steam Turbine – natural gas fired
    240 MW Hydro

## Slide 16
MW-Minute Primary Frequency Response of a 600 MW Unit To All Frequency Deviations During The First 10 Months of 2008
Minute
This compares the difference a single 600 MW unit would have experienced as a result of Primary Frequency Response if on-line the first 10 months of 2008 and had margin to move.

## Slide 17
MW-Minute Primary Frequency Response of a 600 MW Unit To All Frequency Deviations in 2008
Minute
This compares the difference a single 600 MW unit would have experienced as a result of Primary Frequency Response if on-line all of 2008 and had margin to move.

## Slide 18
However, the 692039.8 MW Response of the 0.0166 db unit is only 29465.8 MW more than the 2008 MW Response of the 0.036 db unit (662574.0 MW). A 4.45% increase with the benefit of the improved frequency profile.
The MW response of the 0.036 db unit decreased 216330.0 MW in 2009 from 2008. This is a 32.645% decrease in movement.
MW-Minute Primary Frequency Response of a 600 MW Unit To All Frequency Deviations in 2009
Minute
The MW response of the 0.0166 db unit decreased 201124.4 MW in 2009 from 2008. This is a 22.518% decrease in movement.

## Slide 19
2009 Frequency Profile more “Normal” than 2008. Note: 2008 had two months of operation at the lower governor deadband settings (Nov & Dec).
ERCOT Frequency Profile 2008 and 2009

## Slide 20
ERCOT Frequency Profile Had Additional Improvement in December 2009 and January 2010

## Slide 21
MW-Minute Primary Frequency Response of a 600 MW Unit To All Frequency Deviations During January 2010

## Slide 22: Conclusions
Clearly the MW-Minute Movement of a Unit with a lower deadband setting is more than that of a larger deadband.
The MW-Minute movement of the lower deadband has a gradual injection of Primary Frequency Response compared to the “step” implementation of the larger deadband.
  Better Unit stability
  Better Frequency stability
As more Units implement the lower deadband and non-”step” droop curve, the frequency profile improves and the total MW-Minute movement of the grid decreases.