| PRR Number | 833 | PRR Title | Primary Frequency Response Requirement from Existing WGRs |
| --- | --- | --- | --- |
| Date |  | March 26, 2010 |  |
| Submitter’s Information |  |  |  |
| Name |  | Barbara Clemenhagen on behalf of the Wholesale Market Subcommittee (WMS) |  |
| E-mail Address |  | bclemenhagen@topazpowergroup.com |  |
| Company |  | Topaz Power Group |  |
| Phone Number |  | (512) 314-8621 |  |
| Market Segment |  | Independent Generator |  |

Comments

At the March 24, 2010 WMS meeting, WMS considered Protocol Revision Request (PRR) 833.  After discussion, WMS voted to endorse PRR833 as amended by the 3/12/10 ROS comments and as revised by WMS.

Revised Proposed Protocol Language

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Standard Generation Interconnection Agreements (SGIAs) signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional steam generators.  For WGRs with SGIA executed on or prior to January 1, 2010, those not already equipped with Primary Frequency Response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with Primary Frequency Response capability shall submit an attestation to ERCOT by June 1, 2010 explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for which Primary Frequency Response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within one hundred eighty (180) days of receipt of the attestation.  If ERCOT does not grant an exemption, the WGR shall acquire the capability to provide Primary Frequency Response within twenty-four (24) months of being notified of that determination.  If ERCOT grants the exemption, then ERCOT may require the WGR to install alternate measures, such as over-frequency relays, that are technically feasible and would approximate Primary Frequency Response to Measurable Events.