## Slide 1: PDCWG Report to ROS
April 12, 2010
Sydney Niemeyer

## Slide 2: PDCWG Activities
Met April 7.
  Reviewed one February and four March disturbances.
  Discussed BAL-003-0 FERC directive.
    Requirements needed for individual Generation Resource Primary Frequency Response similar to ERCOT Protocols, Operating Guides and BAL-001-TRE regional draft standard.
    Manage Interconnection Frequency Response by managing Generation Resource operating margins (Reserves) knowing that Governors are in service and working properly.
    Measure and Track Interconnection Frequency Response.
  Discussed Nodal Operating Guide review.
Next meeting May 12.

## Slide 3
CPS1 = 138.60

## Slide 5
*

## Slide 6
of ERCOT Frequency

## Slide 8
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 142.51

## Slide 9
*ERCOT as a single control area is exempt from CPS2. These scores are For Information Only
87.81

## Slide 13: Status as of April 7, 2010
Units with Governors presently set with an intentional deadband less than or equal to +/-0.01666 Hz and droop curve with no step function.
  12,317 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    4689 MW Coal
    3780 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    399 MW Steam Turbine – natural gas fired
    240 MW Hydro

## Slide 14: Historical Frequency Response
A Point (Pre-disturbance frequency)
C Point (spike)
B Point (reset frequency)
B+30 seconds (evaluation of sustained governor response)

## Slide 15: Frequency Response Evaluation
Point C
  Inertia and Load Dampening
  Initial Response from High Pressure Steam Turbines
  Initial Response from Combustion and Hydro Turbines
Point B
  Response from Intermediate and Low Pressure Steam Turbines
  Response from Combustion and Hydro Turbines
Point B + 30 seconds
  Measures Sustained Frequency Response. Determines if plant controls reduce frequency response, commonly called “outer loop MW control”. ERCOT Protocol Section 5 initiated this evaluation point in late 2003.