| NOGRR Number | 032 | NOGRR Title | Use of Consistent Rating Terminology |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | February 19, 2010 |  |  |
| Proposed Effective Date |  | To be determined |  |  |
| Priority and Rank Assigned |  | To be determined |  |  |
| Nodal Operating Guide Section Requiring Revision |  | 3.9.4, Responsibility for Equipment Ratings |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) proposes language changes to align rating terminology in the Nodal Operating Guides with the terminology in the Nodal Protocols. Utilization of the same verbiage helps alleviate communication issues and also removes the possible interpretation of additional rating requirements. |  |  |
| Reason for Revision |  | Currently there are three defined ratings in the Nodal Protocols: Normal Rating, Emergency Rating, and 15-Minute Rating. Requirements for use of the three ratings are contained throughout the Nodal Protocols. In the Nodal Operating Guides there are three defined ratings: Continuous Rating, Emergency Rating, and 15-Minute Rating. Requirements for the use of these ratings are contained throughout the Nodal Operating Guides and are Nodal Operating Guide embodiments of the Nodal Protocol requirements for Normal Rating, Emergency Rating, and 15-Minute Rating, respectively. Additionally, there is a distinction between Transmission Facility and Transmission Element as it pertains to the Ratings definition. The use of the term Transmission Facility is more encompassing than the term Transmission Element. Per the Nodal Protocols, Ratings pertain to Transmission Elements. This NOGRR proposes a corresponding revision to the Nodal Operating Guides. |  |  |
| Overall Market Benefit |  | Clarifies language to prevent confusion or miscommunication. |  |  |
| Overall Market Impact |  | None |  |  |
| Consumer Impact |  | None |  |  |
| Procedural History |  | - On 12/3/09, NOGRR032 and CEO Revision Request Review were posted. - On 1/18/10, OWG considered NOGRR032. - On 2/19/10, OWG again considered NOGRR032. |  |  |
| OWG Decision |  | On 1/18/10, OWG was in consensus to table NOGRR032. On 2/19/10, OWG was in consensus to recommend approval of NOGRR032 as submitted. |  |  |
| Summary of OWG Discussion |  | On 1/18/10, there was concern regarding the changes proposed in this NOGRR and that although the alignment with the Nodal Protocols is necessary, Steady State Working Group (SSWG) should be allowed to comment to be sure the terminology is consistent with their process. On 2/19/10, it was noted that the SSWG reviewed NOGRR032 and found no issues with the proposed language. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Rating language was intended to be the same in the Nodal Protocols and the Nodal Operating Guides. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | No impact. | N/A |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Clarification of the Nodal Operating Guides will diminish possible confusion. | N/A |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Utilizing the same language as it pertains to Rating definitions is in the best interest of ERCOT and the Market Participants. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | It is understood that the language of the Nodal Protocols has precedence and authoritative governance over the Nodal Operating Guide language. If the Nodal Operating Guide language is left unchanged, there are several uses of the term “Continuous Rating” that could be interpreted as a fourth rating. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Ebby John on behalf of the Network Data Support Working Group (NDSWG) |
| E-mail Address | ebby.john@centerpointenergy.com |
| Company | CenterPoint Energy |
| Phone Number | 713-207-2136 |
| Cell Number |  |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

- 3.9.4	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Element Ratings:

(a)	Normal Rating:  Represents the continuous MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	Emergency Rating:  Represents the two-hour MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Element can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	15-Minute Rating:  Represents the 15 minute MVA rating of a Transmission Element, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Normal Rating.  The Transmission Element can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Normal Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Normal Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Element post contingency or the pre-contingency loading is greater than 90% of the Normal Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Normal Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Element within 15 minutes, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Element to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Element to within Normal Ratings as soon as practicable, based on Good Utility Practice.