Texas Renewables Integration Plan (TRIP)

Prepared by the Renewable Technologies Working Group of the ERCOT Technical Advisory Committee

DRAFT version 6

April 20, 2010

Preface

The combination of several forces has led to a rapid and significant addition of renewable energy generating capacity within the Electric Reliability Council of Texas (ERCOT) in recent years, primarily in the form of utility-scale wind generation resources.

The ERCOT Independent System Operator (ISO) and the ERCOT stakeholders embrace the open access network paradigm adopted by the Texas Legislature; strive to effectively and efficiently implement the policy directives to integrate widespread renewable energy development; and endeavor to allow market forces, to the greatest extent possible, to provide the generation resources, ancillary services, and other technical solutions necessary to ensure adequate system security is maintained.  However, those parties responsible for system planning and operational security also recognize that the widespread introduction of variable output renewable generation resources presents significant challenges which must be addressed in order to effectively and efficiently maintain system reliability.

Meeting the Texas Legislature’s goal for increasing amounts of installed renewable energy capacity and the order of the Public Utility Commission of Texas (PUCT or Commission) designating Competitive Renewable Energy Zones (CREZs) requires a comprehensive review and potentially significant improvements to ERCOT planning models and assumptions, operational capabilities and procedures, and certain elements of the ERCOT Zonal and Nodal market designs and systems.  The Texas Renewables Integration Plan (TRIP) is the guiding document for this effort.

The TRIP is the work product of the ERCOT Technical Advisory Committee (TAC) by and through its Renewable Technologies Work Group (RTWG).

Table of Contents

| Executive Summary . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  |  | . . . 8 |
| --- | --- | --- | --- | --- | --- |
| 1. | Introduction . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . 10 |
| 2. | Texas Renewables Integration Plan Overview . . . . . . . . . . . . . . . . . . . |  |  |  | . . . 13 |
|  | 2.1. | TRIP Purpose . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . 13 |
|  | 2.2. | TRIP Structure . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . 13 |
|  |  | 2.2.1. | Phases . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 14 |
|  |  | 2.2.2. | Goals . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 14 |
|  |  | 2.2.3. | Recommendations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 15 |
|  |  | 2.2.4 | Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 15 |
|  |  | 2.2.5. | Issues Identification and Prioritization . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 16 |
|  |  | 2.2.6 | Issues Organization . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.7 | Strategies for Resolution and Follow-Up . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.8 | Schedule . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.9. | Activities for ERCOT and Market Participants . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.10 | Issues Tracking . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.11. | Quarterly Reports . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.12. | RTWG Work Plan . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 19 |
|  | 2.3. | TRIP Input Process, Change Procedure, and Revision Schedule . . . . . . . |  |  | . . . X |
| 3. | Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 3.1. | Public Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.1.1. | Federal Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | XX |
|  |  |  | 3.1.1.1. | Federal Tax Policy . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.1.2. | Federal Energy and Environmental Policy . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  | 3.1.2. | State Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | XX |
|  |  |  | 3.1.2.1. | Competitive Renewable Energy Zones . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.2. | Energy Efficiency and Advanced Meters . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.3. | Solar Generation Technologies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.4. | Distributed Generation and Energy Storage Technologies . . . . . . . . | XX |
|  |  | 3.1.3. | Policy Issues Raised by Integration of Renewable Technologies . . . . . . . . . . . . . |  | XX |
|  | 3.2. | System Reliability Considerations . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.2.1. | System Planning Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  |  | 3.2.1.1. | Quality of Data and Models . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.2. | Generation Interconnection . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.3. | Transmission Planning . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.4. | System Planning Studies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.5. | ERCOT Planning Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  | 3.2.2. | System Operations Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  |  | 3.2.2.1. | Quality of Data, Models, and Systems . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.2. | Dispatchable Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.3. | Generation Ramping Capability and Limitations . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.4. | Frequency Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.5. | Ancillary Services . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.6. | Voltage Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.7. | Renewable Generation Forecasting . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.8. | ERCOT Operations Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  | 3.3. | Technical Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.3.1. | Technical Capabilities and Integration Challenges . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.2. | Technical Approach to Renewable Technologies . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.3. | Technical Challenges to System Planning . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.4. | Technical Challenges to System Operations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.5. | Technical Education and Institutional Knowledge . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 3.4. | Market Design Considerations . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.4.1. | Principles of ERCOT Market Design . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.4.2. | Impacts of Renewable Technologies on ERCOT Markets . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.4.3. | Market Design Approach for Renewable Technologies . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 3.5. | Performance Criteria and Compliance Metrics . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.5.1. | Principles of Performance Criteria and Compliance Metrics . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.5.2. | Application of Performance Criteria to Renewable Technologies . . . . . . . . . . . . |  | X |
|  |  | 3.5.3. | Application of Performance Data to Renewable Technologies Integration . . . . . . |  | X |
|  | 3.6. | Cost Allocation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.6.1. | Principles of Cost Allocation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.6.2. | Cost Allocation Task Forces . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.6.3. | Application of Cost Allocation Principles to Renewable Technologies . . . . . . . . |  | X |
|  | 3.7. | Texas Nodal Market Implementation . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.7.1. | Renewable Technologies Integration Benefits of the Texas Nodal Market . . . . . |  | X |
|  |  | 3.7.2. | Addressing Renewable Technology Issues in Nodal Testing and Start Up . . . . . . |  | X |
|  |  | 3.7.3. | Texas Nodal Market Implementation Schedule and Resource Requirements . . . . |  | X |
|  |  | 3.7.4. | Post-TNMID Evaluation of Wind Operations Issues . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.7.5. | Nodal Parking Deck . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
| 4. | Key Issues and Strategies for Resolution . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 4.1. | System Planning Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | SP-01 | Verify Wind Turbine Technical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-02 | Wind Turbine Computer Models . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-03 | Wind Turbine Fault Tolerance . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-04 | Voltage Transient and Small Signal Stability Study . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-05 | Impact of Wind Turbines on System Inertia . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-06 | Use of Variable Frequency Transformers to Solve Stability Problems . . . . . . . . . |  | X |
|  |  | SP-07 | Voltage Control Process . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-08 | Voltage Ride-Through Study . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-09 | Wind Turbine Model Validation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-10 | DOE Long-Term Planning Study . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.2. | System Operations Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | SO-01 | Inventory of Wind Generation Facilities . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-02 | Nodal Tools to Integrate Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-03 | Wind Generation Response and Schedule Control Error (SCE) . . . . . . . . . . . . . . |  | X |
|  |  | SO-04 | Smart Grid Implications for Renewable Resources . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-05 | Operational Studies Related to Wind Integration . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-06 | Testing Reactive Capability of Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-07 | Wind Generation and High System Frequency . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-08 | Wind Generation and System Inertia . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-09 | SCADA Control of Generation Circuit Breakers . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-10 | Voltage Management Practices Applicable to Wind Generators . . . . . . . . . . . . . . |  | X |
|  |  | SO-11 | Technology-Specific Procedures and Protocol Changes . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-12 | Low-Voltage Ride-Through for Wind Generators . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-13 | Performance Metrics for Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-14 | Impact of Transmission Outage Planning on Wind Generation . . . . . . . . . . . . . . |  | X |
|  |  | SO-15 | Communications Between Wind Farms and TSPs . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-16 | Wind Generation Ramp Limits . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-17 | Mid-Term and Short-Term Load Forecast Weather Sensitivity . . . . . . . . . . . . . . |  | X |
|  |  | SO-18 | Evaluate Transmission Line and Wind Power Production Outage Criteria . . . . . . |  | X |
|  |  | SO-19 | Improve Competitively Sensitive Constraint (CSC) Process . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-20 | Dynamic Transmission Line Ratings . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-21 | Evaluate Emergency Electric Curtailment Plan (EECP) Steps . . . . . . . . . . . . . . . |  | X |
|  |  | SO-22 | Open . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-23 | Impact of Advanced Meters on Integration of Renewable Resources . . . . . . . . . . |  | X |
|  |  | SO-24 | Settlement of Advanced Meters in the Nodal Market . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-25 | Generator Governor Response for Wind Generators . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-26 | Impact of Solar Generation on System Operations . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-27 | Manual Curtailment of Wind Generation to Resolve Local Congestion . . . . . . . . |  | X |
|  |  | SO-28 | SPS Actuation for N-0 Conditions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-29 | Transmission Outage Planning for CREZ . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-30 | Application of Wind Generation Forecast to PASA . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-31 | Tension Monitors on Transmission Lines . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-32 | Real-Time Wind Generation Capacity . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-33 | Real-Time Wind Turbine Availability . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-34 | SCED Line Ratings . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.3. | Market Design Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | MD-01 | Ancillary Services Cost Allocations Applicable to Wind . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-02 | Ancillary Services Procurement Optimization for 2009 . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-03 | Non-Spin Requirements . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-04 | New Ancillary Services Products Needed for Reliability . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-05 | Benefits of Storage Technologies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-06 | Ancillary Services Procurement Methodology . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-07 | Wind Generating Resources Providing Ancillary Services . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-08 | Reactive and Voltage Requirements Applicable to Wind Generators . . . . . . . . . . |  | X |
|  |  | MD-09 | Wind Generation Dispatch in the Nodal Protocols . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-10 | Wind Generation Performance Metrics in the Nodal Protocols . . . . . . . . . . . . . . . |  | X |
|  |  | MD-11 | Wind Generation and Base Point Deviation in the Nodal Protocols . . . . . . . . . . . |  | X |
|  |  | MD-12 | Wind Generation Resource LSL as a Percentage of HSL . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-13 | Use of State of the Art Wind Forecast . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.4. | Workshop and Training Issues . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | WT-01 | Resource Plan and Schedule Update Process . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-02 | Wind Workshop III – Summer 2009 . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-03 | Wind Turbine Operator Training . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-04 | Wind in the Nodal Market . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-05 | Wind Workshop IV . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-06 | Solar Workshop . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-07 | Energy Storage Workshop . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
| 5. | 2010-2011 RTWG Work Plan . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 5.1. | RTWG Charter . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.2. | RTWG Goals . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.3. | RTWG Activities . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.4. | RTWG Work Product . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
| 6. | Summary Tables . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |
|  | 6.1. | Summary Table of TRIP Goals . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 6.2. | Summary Table of TRIP Recommendations . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 6.3. | Summary Table of Recommended ERCOT Activities . . . . . . . . . . . . |  |  | . . . X |
|  | 6.4. | Summary Table of Recommended Market Participant Activities . . . . . . |  |  | . . . X |
|  | 6.5. | Summary Schedule of Major TRIP Activities . . . . . . . . . . . . . . . . . |  |  | . . . X |
| 7. | Appendices . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |
|  | 7.1. | 2009 RTWG White Papers |  |  | . . . X |
|  | 7.2. | 2008-2009 Wind Workshop Presentations |  |  | . . . X |
|  |  | 7.2.1. | Wind Workshop I, March 17, 2008 |  |  |
|  |  |  | 7.2.1.1 | Presentation Title |  |
|  | 7.3. | 2009 RTWG Presentations |  |  | . . . X |
| 8. | References . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |

Executive Summary

Text.

1.	Introduction

In early 2008, ERCOT Staff approached the TAC leadership with a request to hold a workshop focused on operational challenges related to the ever-increasing amount of wind energy production on the ERCOT system.  The workshop, which has since become known as Wind Workshop I, was scheduled for mid-March 2008.  In the intervening period, ERCOT experienced a significant system disturbance on Feb. 26, 2008.  During this event, which had numerous causes and complicating factors, dramatic variations in wind energy output and deviation from wind energy schedules were noteworthy contributing factors.  This event added urgency to the scheduled workshop as more and more stakeholders came to realize the near-term importance of addressing operational challenges posed by wind energy production.

Wind Workshop I kicked off a 2-year period of intense focus by Staff and stakeholders to address wind integration challenges.  The immediate task was to address the issues raised by Staff at Wind Workshop I because they were viewed by ERCOT Operations to be critical to system security.  The key issues and their resolution are summarized below.

- Develop a common understanding of the impact of wind generation on operations:  ERCOT provided examples of recent operational experiences with wind generation under various scenarios and noted that a lack of understanding regarding the details of certain operational procedures by market participants produced inconsistent results in unit responses to instructions and introduced operational challenges.

TAC assigned workshop follow-up items to WMS and ROS.  Numerous Revision Requests flowed from the subcommittee efforts to address the workshop issues raised by ERCOT and other issues which surfaced through the focused follow-up discussions.  The ROS created the Wind Operations Task Force to work closely with ERCOT Operations to quickly focus on the operational issues.  The TAC created the Renewable Technologies Work Group to, in part, maintain a centralized issues list so market-wide education on wind issues could be facilitated.

Focused collaboration between ERCOT and stakeholders led to numerous procedural changes and data collection projects which did not require Revision Requests to implement.  Noteworthy examples of issues addressed identified and resolved in this manner include:

  - Improved communication between Wind Generation Resources (WGRs) and Transmission Service Providers (TSPs) regarding operational practices

  - Clarification and strengthening of voltage support requirements and timelines

  - Improved quality and quantity of ERCOT data on WGR unit designs and capabilities

  - More frequent CSC limit calculations to improve zonal transfers

- Identification of current problems, anticipated future problems, changes to be implemented in the zonal market, and changes to be implemented in the nodal market:  In the weeks following Wind Workshop I, ERCOT and stakeholders identified a range of issues which required Revision Requests to implement.  Resource constraints related to the nodal market transition effort forced parties to reach solutions with minimized systems impacts and maximized ease of implementation.  Many of the Revision Requests were granted Urgent status.  The full list of approved Revision Requests stemming from this effort are described below, but some noteworthy examples include:

  - Replace WGR QSE wind schedules with ERCOT wind forecast

  - Impose WGR ramp rate limitations

  - Requirement for WGRs to accelerate implementation of nodal telemetry standards

  - Clarified definitions and performance measures for WGR scheduling practices

  - WGR voltage ride-through requirements

- Replace WGR QSE wind schedules with ERCOT wind forecast:  ERCOT observed that the accuracy of WGR Resource Plans varied widely across the market and illustrated the consequences of poor forecasting on Day Ahead and Hour Ahead capacity adequacy studies.  Because the studies automatically use Resource Plan data from the Scheduling Pricing Dispatch (SPD) system, any modifications to the software would have significant impacts on Staff resources and budget.  A quicker and more cost-effective solution was developed (PRR 763) that required WGR QSEs to make the changes in their own Resource Plans using ERCOT-provided forecast data (the AWS TrueWind forecast).  PRR 763 became effective July 1, 2008.

- Establish wind ramp rate requirements:  ERCOT provided examples of wind units with extremely vertical ramp rates, especially when released from down balancing instructions during windy periods.  The steep ramps presented challenges to key operational functions, including system frequency control.  Due to variations in wind turbine technical capabilities, stakeholders bifurcated the issue into two solutions.  The first (PRR 771), applied a ramp rate limit when responding to or releasing from an ERCOT deployment instruction to all new turbines installed in ERCOT.  The second (PRR 788), applied to the same standard to most existing wind turbines in ERCOT.  PRRs 771 and 788 were effective Jan. 1, 2009 and Feb. 1, 2009, respectively.

Following Wind Workshop I and the subsequent related work of resolving the identified issues of immediate concern, TAC and the Board directed Staff and the stakeholder process to undertake a variety of efforts to more holistically address the wide array of issues related to integration of renewable technologies with a particular focus in the near term on operational challenges associated with WGRs.  TAC formed the RTWG and charged it to develop a renewable technologies integration plan.

In this plan, the RTWG has endeavored to provide sufficient background discussion and information to give the broader document contextual meaning.  However, this document is not intended to be a primer on general renewable technologies integration opportunities and challenges.  Section 8 of this document provides references to such material.  Rather, this document and its quarterly updates are intended to be regularly used by active ERCOT market policy makers and stakeholders to plan, track, and complete the range of activities and work products required to successfully integrate renewable energy technologies into the ERCOT system.

It should also be noted that although the specific directive from the ERCOT Board and TAC was to address the integration of renewable generation technologies, the RTWG strongly recommends equal attention be paid to energy storage technologies and certain “smart grid” technologies, either because they may be “renewables-enabling” technologies or because they are likely to have impacts on ERCOT functions, processes, and systems similar to renewable technologies.

2.	Texas Renewables Integration Plan Overview

The Texas Renewables Integration Plan (TRIP) is a work product of the Electric Reliability Council of Texas (ERCOT) Technical Advisory Committee (TAC) by and through its Renewable Technologies Work Group (RTWG) and is the guiding document describing the efforts of the ERCOT Independent System Operator and market stakeholders to integrate significant levels of utility-scale and distributed renewable generation technologies into the ERCOT system as well as to address issues raised by other emerging technologies associated with or enabling renewable technologies such as energy storage devices.

2.1.	TRIP Purpose

The TRIP serves six key purposes, each of which is stated as a goal of the plan.

| Goal 01 | Identify and communicate issues of interest related to the integration of renewable resources to market participants and industry stakeholders. |
| --- | --- |

| Goal 02 | Develop strategies to resolve identified issues. |
| --- | --- |

| Goal 03 | Communicate the long-term plan for ERCOT activities related to renewable technologies integration to market participants and industry stakeholders. |
| --- | --- |

| Goal 04 | Communicate progress on renewable technologies integration and raise issues for resolution to Texas policy makers and ERCOT ISO decision makers. |
| --- | --- |

| Goal 05 | Document the renewable technologies integration activities within the ERCOT Region as a resource for electric power industry stakeholders. |
| --- | --- |

| Goal 06 | Document “lessons learned” through the ERCOT renewable technologies integration effort to preserve institutional memory and better inform ongoing integration activities. |
| --- | --- |

2.2.	TRIP Structure

The TRIP is divided into three phases, each with goals and recommendations for action.  The plan is organized around the specific issues identified to enable renewable technologies integration.  The issues are divided into four broad categories – system planning, system operations, market design, and workshops and training.  A consistent set of considerations are applied to each issue to ensure all angles are thoroughly vetted.  Each issue is assigned a priority, a schedule for resolution, and one or more parties responsible for the required work product.  A summary spreadsheet of progress towards issues resolution is provided quarterly to the TAC, ERCOT Board, and PUCT.

2.2.1.	Phases

As discussed in greater detail below, the significance and scope of the Texas Nodal Market implementation project presents a variety of challenges to other efforts to revise ERCOT market rules, systems, and procedures.  Accordingly, the TRIP is divided into three distinct phases.

- Phase One:  High priority utility-scale wind issues to be resolved in the Zonal Market and those with ERCOT systems changes deemed necessary for the Texas Nodal Market Implementation Date (TNMID).  Phase One began with the March 17, 2008 Wind Workshop I and ends with the “pens down” date for zonal systems changes and TNMID systems changes.

- Phase Two:  Identify post-TNMID utility-scale wind issues and strategies for resolution.  Where needed, work with standing TAC Subcommittees to anticipate opportunities and challenges associated with other utility- and distributed-scale renewable technologies such as solar generation and energy storage and develop any required Texas Nodal Market v1.X and/or v2 solutions.  Continue Phase One follow-up activities.

- Phase Three:  Tracking and communicating implementation of Phase Two solutions and follow-up activities.

Due to the large number and urgent nature of challenging wind issues to be addressed at the same time the ERCOT stakeholder leadership directed the formation of this long-range plan to address renewable technologies integration issues, most Phase One activities described in the plan occurred concurrently with the plan’s development and are shown in this document as completed activities.

2.2.2.	Goals

Goals of the TRIP and the RTWG are included throughout the document.  A summary table of goals is found in Section 6.1.

2.2.3.	Recommendations

The TRIP includes specific recommendations to resolve each identified renewable technologies integration issue.  A summary table of recommendations is found in Section 6.2.

2.2.4.	Considerations

As renewable technologies integration issues are identified, stakeholders must address a wide array of considerations to ensure each issue is vetted from all sides and unintended consequences are minimized.

- Public Policy:  Some issues arise from public policy directives which must be followed.  Some public policy initiatives may result in outcomes which significantly impact the ERCOT system and markets.  Some issues present policy questions which should be forwarded to the appropriate body for resolution.  Each issue is examined for public policy impacts.

- System Reliability: Both the system planning function and the system operations function play critical roles in ensuring electric system reliability.  Many renewable technology integration issues present challenges to one or both of these functions.  Each issue is explored from both perspectives to ensure the integration of emerging renewable technologies does not compromise system reliability.

- Technical: Many of the emerging technologies addressed by the TRIP have very different operating abilities and characteristics than the conventional generation technologies familiar to system planners and operators.  These new technologies may present both opportunities and challenges for ERCOT, market participants, and consumers.

- Market Design:  Application of principles of sound market design can address some integration issues.  In other instances, issues may arise from existing market design elements.  Recommendations must consider market impacts and market design impacts.

- Performance Criteria and Compliance Metrics:  Some integration issues may be resolved through clarification or creation of performance criteria for renewable generators or other market participants.  In some instances, compliance metrics may also be required to provide regular, transparent reporting on renewable technology adherence to market rules or procedures, both as a dashboard gauge for policy makers and to enable follow-up measurement and analysis for ongoing integration efforts.

- Cost Allocation:  The ERCOT market design utilizes various cost allocation methodologies, some are directly asssigned to one or more market participants based on causation principles while others are assigned across a number of market participants on a pro rata basis.  Cost causation or allocation questions are considered for each issue.

- Texas Nodal Market Implementation:  The recommended solution for any identified renewable technologies integration issue must respect the boundaries resulting from the Texas Nodal Market implementation project and must consider whether solutions should be implemented in the Zonal and/or Nodal markets.

2.2.5.	Issues Identification and Prioritization

The heart of the TRIP is the exploration of all likely facets of interaction between emerging renewable technologies and the ERCOT system and markets to identify issues requiring resolution.  Issues may be raised in a variety of ways – through the normal course of business in the stakeholder process, by individual market participants, by ERCOT Staff observations of operational practices, or as directed by policy makers, to name a few.  To facilitate the identification, coordination and tracking of issues, the RTWG appointed liaisons to the ERCOT Reliability and Operations Subcommittee (ROS), Wholesale Market Subcommittee (WMS), Nodal Advisory Task Force (NATF), and Regional Planning Group (RPG).  Once identified, issues are named, numbered, described, prioritized, analyzed, addressed, and tracked.

Each identified issue is prioritized for resolution.  The four categories of prioritization are Near-Term, Long-Term, Undetermined, and Complete.  The prioritization of issue resolution depends upon several factors including significance to system reliability or market functionality, time required to complete associated tasks, resource availability, and any other identified dependencies.  Prioritization of issues is expected to assist ERCOT and market participants with the allocation of resources to renewable technologies integration efforts in a timely, methodical, coordinated, and cost-effective manner.  Identified issues presenting immediate concerns for system reliability or significant market impacts are escalated for rapid resolution.

2.2.6.	Issues Organization

The TRIP is organized around the identified renewable technologies integration issues.  These issues, once identified and defined, are organized by general area of impact as follows:

- System Planning (SP):  Issues which impact or are impacted by the system planning function or require system planning activities to achieve resolution.

- System Operations (SO):  Issues which impact or are impacted by the system operations function or require system operations activities by ERCOT and/or market participants to achieve resolution.

- Market Design (MD):  Issues primarily concerning market activities or market outcomes.

- Workshops and/or Training (WT):  Issues which require stakeholder education and/or brainstorming.  Also, the activities related to effective communication of issues resolutions to market participants and the industry for implementation and operations.

2.2.7.	Strategies for Resolution and Follow-Up

For each identified issue, a strategy is developed to resolve the issue.  Tasks required to resolve the issue are assigned to a responsible party.  The completion of tasks is tracked and published to promote progress and transparency.  Resolved issues are reported to the ERCOT Board and PUCT in the quarterly updates.  A complete list of resolved and tabled issues is also included in the TRIP and the RTWG Issues List to preserve institutional memory.  Where appropriate, the TRIP describes processes for monitoring, evaluating, and reporting on the effectiveness of renewable technology implementation solutions developed through the TRIP which may, in some instances, require follow-up activities after the issue is deemed completed.

2.2.8.	Schedule

For each identified issue, a schedule for resolution is suggested, including timelines for required studies, systems projects implementation, market testing, etc.  The priority assigned to the issue and the resources available to identify and implement a solution are key inputs to the recommended schedule.

2.2.9.	Activities for ERCOT and Market Participants

Some actions will be required of ERCOT and others of the stakeholder process or market participants.  A summary table of recommended activities for ERCOT and market participants is found in Sections 6.3 and 6.4.

2.2.10.	Issues Tracking

Identified integration issues are tracked on the RTWG Issues List, which is an abbreviated and more frequently updated version of Section 4 of the TRIP.  The Issues List is updated at least quarterly.  For each identified issue, the Issues List includes:

- the issue identification number;

- a brief description of the issue;

- the stakeholder group to which the issue is assigned for resolution;

- the issue priority ranking;

- the mechanism for issue resolution, if known (such as PRR, OGRR, etc.);

- the current status of the issue, including keeping track of completed issues to preserve institutional knowledge; and

- any cross-references to other ERCOT documents addressing the issue to enable full-spectrum issues tracking.

2.2.11.	Quarterly Reports

In fulfillment of the PUCT Order requiring ERCOT to provide quarterly updates on the resolution of wind integration issues, the RTWG prepares quarterly reports on TRIP progress to the TAC which, in turn, updates the ERCOT Board and PUCT.  Each quarterly report features:

- the amount of installed renewable generation capacity in ERCOT;

- a summary of renewable technologies interconnection activities;

- a review of significant events in the previous quarter related to renewable technologies;

- an update on issues completed in the previous quarter;

- an update on new issues identified in the previous quarter;

- the most recent version of the RTWG Issues List; and

- any other relevant information.

2.2.12.	2010-2011 RTWG Work Plan

The monthly meetings of the RTWG provide a forum for market participants to identify, resolve, and track renewable technologies integration issues as well as to share and maintain technical knowledge.  Additionally, the RTWG sponsors workshops featuring in-depth discussion of particular issues to ensure recent changes in technical standards or market rules are communicated to industry participants.  Section 5 describes the RTWG work plan and anticipated work product for the period between the adoption of this plan and the next expected update of the TRIP in the first quarter of 2012.  The RTWG anticipates Phase One activities ending in early 2010 and focusing on Phase Two activities through early 2012.

2.3.	TRIP Input Process, Change Procedure, and Revision Schedule

TAC and the RTWG welcome input to the TRIP from a variety of sources.  All meetings of TAC and its subgroups are open to public participation and the meeting locations and agendas are listed on the calendar page of the ERCOT web site at least one week in advance of the meeting.  Issues related to the integration of renewable resources may be introduced for inclusion in the TRIP at any meeting of the TAC or its subgroups.  Additionally, TAC seeks the input of the ERCOT Board of Directors and PUCT at least quarterly.  At the direction of TAC, the RTWG maintains the responsibility for incorporating identified issues into the TRIP and the accompanying RTWG Issues List.

All changes or updates to the TRIP are made by the RTWG.  As a working group of the TAC, the RTWG operates on a consensus-based paradigm with reporting to TAC of majority and minority positions when consensus cannot be achieved.  The TAC maintains sole authority for the final stakeholder recommendations on all issues in the TRIP.

The next full revision of the TRIP is planned to be presented to the TAC approximately 1 year after the TNMID or earlier if circumstances warrant.

3.	Considerations

Each renewable technology integration issue identified by the RTWG is examined in light of a number of considerations to ensure completeness of thought, coordination with other issues, and to minimize unintended consequences of proposed changes to market rules, technical standards, and procedures.

3.1.	Public Policy Considerations

The TRIP sets forth both reactive and proactive approaches to the public policy decisions made by jurisdictional entities.  The ERCOT TAC does not make or seek to influence public policy regarding any electric power generation technology.  However, the TRIP must be responsive to public policy directives where required and provide solutions to the impacts of public policy directives regarding the introduction of new renewable technologies onto ERCOT transmission and distribution systems and into ERCOT markets.

3.1.1.	Federal Policy Considerations

Although the ERCOT market is somewhat unique in the limited scope of federal government jurisdiction over the market design and other areas, federal policy nonetheless can have significant impact on the ERCOT grid.  In some respects, the lack of stakeholder anticipation of the influx of large amounts of renewable generation capacity in ERCOT can be attributed to a failure to recognize a likely outcome of federal tax policies which encouraged the development of utility-scale wind generation facilities.

| Goal 07 | Remain informed of federal policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. |
| --- | --- |

3.1.1.1	Federal Tax Policy

Federal tax policy has perhaps been the most significant single driver for the installation of renewable generation technologies in the past two decades.  Since the passage of the federal Production Tax Credit (PTC) in the Energy Policy Act of 1992, installations of wind farms have typically surged when the PTC is available.  Likewise, when the credit lapsed, wind farm development ground to a halt.  The PTC was extended through Dec. 31, 2012 by the American Recovery and Reinvestment Act (ARRA) of 2009.  It is anticipated that extended PTC availability during this time period will provide a continued incentive for wind farm development in ERCOT in high-capacity factor areas.

The availabililty of an Investement Tax Credit (ITC), which was also included in the ARRA and which may be converted to a cash grant, provides further momentum to the likely installation of a significant amount of both utility-scale and distributed-scale wind and solar generation technologies in the near-term, possibly even in areas of the state with lower capacity factors since the ITC incentive is not production-based.

3.1.1.2	Federal Environmental and Energy Policy

Federal environmental and energy policy may also play a significant role in either encouraging the installation and use of renewable technologies through mechanisms such as a Renewable Portfolio Standard or limitations of emissions which discourage the use of certain conventional technologies, such as those with higher levels of carbon dioxide (CO2) emissions.  At the direction of the PUCT, ERCOT performed an analysis of possible impacts of proposed legislation to limit CO2 emissions and found that such a policy decision could have significant market and technical impacts on the ERCOT system and that significant penetration of renewable generation can mitigate the potential costs of C02 limits.

3.1.2.	State Policy Considerations

The State of Texas exercises a high degree of jurisdictional control over most facets of the ERCOT network and markets and has consistently adopted policies to encourage the installation of renewable power generation technologies in ERCOT since the passage of the state’s first 2,000 MW renewable portfolio standard in 1999’s Senate Bill 7.

3.1.2.1.	Competitive Renewable Energy Zones

In 2005, the Texas legislature passed Senate Bill 20 which set a goal of 5,880 MW of total installed renewable generating capacity by January 1, 2015, and a target of 10,000 MW by January 1, 2025.  The bill also required the PUCT to

- designate Competitive Renewable Energy Zones (CREZs) throughout the state based on renewable energy resources and developer commitments and

- develop a plan to construct the transmission capacity necessary to deliver this electricity from renewable energy resources to major load centers.

In PUCT Docket  No. 33672, the Commission designated five geographic areas as CREZs (including two in the Texas panhandle, an area normally served by the Southwest Power Pool (SPP).  To interconnect the designated CREZs to the ERCOT system, the Commission also selected ERCOT's "Scenario 2" transmission plan which called for the construction of 2,334 miles of new transmission designed to serve 18,456 MW of wind generation.  The Commission found that certain transmission lines were critical in relieving current transmission congestion in areas with existing wind generation and ordered that those "priority" lines be constructed first.  Certain Transmission Service Providers (TSPs) were ordered to fully implement the CREZ Plan by Dec. 31, 2012.  It is anticipated that the vast majority of “CREZ generators” will be utility-scale wind units.

| Recommendation 01 | For system planning purposes and operational readiness activities, ERCOT should assume full implementation of the PUCT CREZ Plan by Dec. 31, 2013. Studies and preparations should assume at least 19,000 MW of installed wind generation capacity. |
| --- | --- |

| Goal 08 | Guide and track stakeholder efforts to facilitate implementation of and adaptation to the PUCT’s CREZ Plan. |
| --- | --- |

| Goal 09 | Ensure the ERCOT planning function addresses the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. |
| --- | --- |

| Goal 10 | Ensure the ERCOT operations function is prepared for the operating conditions resulting from the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. |
| --- | --- |

3.1.2.2.	Energy Efficiency and Advanced Meters

Ongoing energy efficiency efforts and developing energy efficiency technologies may play significant complementary or complicating roles in renewable technologies integration.  Need brief description of Strauss HB XXXX and related PUCT/IOU/Muni/Coop activities/programs.

3.1.2.3.	Solar Generation Technologies

Brief discussion of solar incentive bills in 2009 session.  Any state action coupled with continued federal solar ITC/cash grant would likely spur installation of utility scale solar in Texas.

3.1.2.4.	Distributed Generation and Energy Storage Technologies

Text.  (Brief overview of DRG, net metering, and solar incentives bills of 2009 session and brief discussion of possible impacts or other relationship to TRIP.)

| Goal 11 | Remain informed of state policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. |
| --- | --- |

3.1.3.	Policy Issues Raised by Integration of Renewable Technologies

As previously discussed, the TRIP recommends ERCOT and market participants be aware of public policy initiatives likely to increase the amount and types of renewable technologies on the ERCOT system and take reasonable steps to plan for the impacts of such policies.  However, it should also be noted that the widespread introduction of new technologies often raises policy issues which may or may not be suitable to be addressed by the ERCOT stakeholder process.  For example, there is some ambiguity in Texas law whether energy storage devices are properly considered a generation technology or a transmission/distribution system technology.  The implications are significant because Texas law imposes strict limitations on ownership, operation, and market activity or cost recovery of the devices depending on which category is applied.

3.2.	System Reliability Considerations

A primary mission of the ERCOT Independent System Operator is to maintain the reliability of the ERCOT bulk power system at all times through appropriate system planning and operations practices.  The widespread introduction of variable generation technologies, technologies which directly interact with variable generation technologies, and other technologies which directly impact system planning and operations functions in similar fashion as variable generation technologies create potential economic benefits for ERCOT consumers and potential reliability challenges for ERCOT planners and operators.

| Goal 12 | Identify and capture the economic benefits and reliability enhancements offered by renewable generation technologies and related applications and practices while maintaining ERCOT system reliability. |
| --- | --- |

3.2.1.	System Planning Considerations

The ERCOT system planning function entails a wide array of activities essential to system security.  The rapidity with which new power generation and load management technologies have been introduced to the system and, in particular, the significant penetration of variable generation technologies creates numerous system planning complications which must be addressed to enable prudent and effective system planning.

3.2.1.1.	Quality of Data and Models

In many respects, ERCOT’s ability to effectively integrate renewable technologies has been hampered by the poor quality of critical information.  Much of the information collected for conventional generation resources is not applicable to renewable generation technologies and much of the information relevant to renewable technologies is not collected by ERCOT or TSPs in a consistent manner, if at all.  Additionally, there is some uncertainty as to the accuracy or completeness of renewable generation technology capability specifications and operations models under a variety of system conditions.

| Goal 13 | Improve the quality of data and accuracy of models used to support the ERCOT system planning function. |
| --- | --- |

| Recommendation 02 | As integration issues are examined, data and model quality should be considered and, where possible, improved. ERCOT and stakeholders should collaborate in specific activities to improve ERCOT’s access to quality technical data related to renewable generation technologies. |
| --- | --- |

3.2.1.2.	Generation Interconnection

The ERCOT generation interconnection process is often the first point at which new Resources are included in system planning activities and is the process through which much of the unit-specific data used by TSPs and ERCOT is collected.  Where appropriate, the TRIP considers whether integration issues can and/or should be addressed through improvements to the generation interconnection process.

3.2.1.3.	Transmission Planning

As the electric power industry enters a phase of significant technological development, transmission planning activities are complicated by a wider and more uncertain range of possible future operational scenarios.  Other recent developments, such as generation resources with multiple points of interconnection within the ERCOT system create additional complications.  Where integration issues identify uncertainty or complications in the transmission planning function, recommendations are offered.

3.2.1.4.	System Planning Studies

System planning studies are used to identify areas of near-term and long-term concern and devise and test possible solutions.  In recent years, ERCOT has been required to update assumptions and devise new studies to address the array of issues presented by renewable technologies.  As these technologies continue to evolve and as new technologies enter the market, additional useful studies should be identified and performed.

3.2.1.5.	ERCOT Planning Resources

The ERCOT system planning function is a shared function between the ISO and stakeholders, primarily TSPs.  Much of the regular system planning work is performed by TSPs through the working groups of the ROS and the Regional Planning Group (RPG) under ERCOT supervision.  As ERCOT’s capabilities have increased in recent years, the ISO has assumed a more direct role in system planning activities.  However, in many respects, ERCOT system planning resources are still stretched thin to the point that concerns about “study horsepower” have entered the stakeholder lexicon.

| Goal 14 | Assess ERCOT system planning capabilities in light of activities required to effectively plan for further integration of renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. |
| --- | --- |

| Recommendation 03 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system planning resources to keep pace with rapidly evolving grid-connected technologies. |
| --- | --- |

3.2.2.	System Operations Considerations

As challenging as variable generation technologies can be for system planning, the task of effectively and efficiently integrating renewable technologies in Real Time system operations is the primary focus of near-term TRIP activities.  The ERCOT system must become more flexible to manage greater inherent variability in generation, load, and net load with an evolving mix of available resources for operational purposes.  The operational decisions made by ERCOT have tremendous impact on system security, Real Time and near-term market economics, and long-term market health and sustainability.  Because renewable technologies offer Texans significant environmental and economic benefits, their utilization should be maximized.  However, it is essential ERCOT be able to posture the system in the Day Ahead and Real Time to mitigate the uncertainty which can accompany high levels of renewable generation penetration.

3.2.2.1.	Quality of Data, Models, and Systems

Just as quality data and models are essential to conduct meaningful system planning activities, system operations must be informed by accurate information reflecting technical capabilities and availability.  Where integration issues identify areas of concern or potential improvement in the useful quantity or quality of data available to system operators, such issues must be addressed.

3.2.2.2.	Dispatchable Resources

Maintenance of system security requires ERCOT be able to dispatch generation resources up and down to follow load and manage transmission system congestion.  Inherent limitations in the dispatchability of many renewable generation technologies pose several challenges, particularly during conditions in which high renewable energy production is concurrent with low system load and the number and variety of dispatchable generation units may be limited.

3.2.2.3.	Generation Ramping Capabilities and Limitations

The prevalence of geographically concentrated wind farms in West Texas as the dominant form of renewable energy production has subjected the ERCOT network to “ramping events” characterized by rapid, steep increases or decreases in the energy output of multiple renewable generation facilities.  Therefore, not only must ERCOT have a sufficient quantity of dispatchable generation available to address the variability of renewable energy output but the available resources must also be technically capable of meeting the steep ramping needs of the system.

| Goal 15 | Ensure particular attention is paid to ramping events, including taking steps to mitigate ramp event impacts, improve ramp event forecasting and pre-event system posturing, and devising more effective and/or efficient use of market and operational tools during ramp events. |
| --- | --- |

3.2.2.4.	Frequency Control

The ERCOT ISO is required by NERC standards to maintain system frequency within a specified range and to quickly restore system frequency when deviations occur.  Renewable generation technologies exhibit a range of both challenges and contributions to system frequency control.  There is some concern that a frequency control issue which may manifest itself in the future as renewable technologies penetration increases is that certain periods may lack sufficient spinning mass from synchronously connected generators to maintain the system inertia, which can carry the system through a frequency decline until spinning reserves can ramp to sufficiently high output to arrest the decline.

| Goal 16 | Identify and address current and anticipated challenges to the maintenance of system frequency control. |
| --- | --- |

3.2.2.5.	Ancillary Services

ERCOT procures a number of ancillary services on behalf of the market to provide key system reliability functions.  Capacity, energy, and other services from participating generation and load resources have traditionally been procured to enable the system to maintain frequency and ride through or recover from distinct disturbances and capacity shortage conditions.  However, large amounts of variable energy output can change the scope, frequency, and duration of ancillary services deployments and have a corresponding impact on the kinds and levels of ancillary services which should be procured and available for system operations.

ERCOT has already performed some substantial work on ancillary services-related issues, including directing a study performed by General Electric as part of the PUCT’s CREZ designation process.  The General Electric Study evaluated the likely need for additional Regulation Service to manage wind variability at high penetration levels and suggested ERCOT explore the possibility of adding a 10-minute Non-Spinning Reserve Service (NSRS).  ERCOT has also approved a series of revisions to the ISO’s ancillary services procurement methodology to modify the amount of NSRS procured, increase the number of hours in which NSRS is procured, and provide a mechanism for increasing the procurement of additional Regulation Service if system control performance slips below a predetermined limit.

As discussed in greater detail below, it is anticipated the Texas Nodal Market conversion will necessitate a further evaluation of the necessity and adequacy of the various ancillary services.  The ancillary services procurement methodology is likely to be regularly updated in the future as ERCOT gains experience with nodal market operations and increased levels of renewable energy generation.

| Goal 17 | Develop a near-term process by which the range of issues associated with the kinds of ancillary services available to the ERCOT market and the procurement methodologies for those services are evaluated and, if necessary, adjusted to facilitate the integration of renewable generation technologies. |
| --- | --- |

3.2.2.6.	Voltage Control

A number of issues relating to voltage control practices emerged from Wind Workshop I and were escalated as critical issues to resolve early in the TRIP development process.  It was discovered that not all relevant parties had complete or accurate data relating to voltage management equipment and stakeholders lacked common understanding of voltage control practices and performance expectations.

| Goal 18 | Assess voltage control requirements, capabilities, and areas of possible clarification or improvement in current procedures and technical standards. |
| --- | --- |

3.2.2.7.	Renewable Generation Forecasting

A fundamental complicating factor of renewable variable generation technologies on system operations is the uncertain nature of energy output at any given point in time.  As installed wind capacity on the ERCOT system grew from 1999-2005, ERCOT observed that the accuracy of any one particular wind farm mattered less than the overall accuracy of ERCOT’s forecast for all wind units on the system.  This recognition informed the trend over several years to lessen ERCOT’s dependence of individual wind farm forecasts and instead provide ERCOT with an improved systemwide view independent of individual generation schedules.  It is generally accepted that this approach more effectively and efficiently enabled ERCOT to posture the system to take advantage of the maximum amount of clean, low-cost, renewable energy.

In many respects, stakeholders included an upgraded renewable generation forecasting system and process in the Texan Nodal Market design, which was delayed along with the rest of the nodal program until late 2010.  Much of the near-term focus of stakeholder activities in the forecasting area has been to accelerate the use of nodal market renewable generation forecasting tools ahead of the rest of nodal market implementation.  An additional area of near-term focus has been the development of forecasting tools specifically focused on wind ramping events as better situational awareness can mitigate the more significant system reliability challenges posed by such events.

| Goal 19 | Evaluate renewable generation forecasting practices and outcomes. Identify areas of possible improvement and develop solutions. |
| --- | --- |

3.2.2.8.	ERCOT Operations Resources

As the number of significant variables impacting system operations increases with renewable technologies penetration, ERCOT operators will require access to additional information and tools to enhance situational awareness and manage system variability.  As the primary users of this new information and tools, ERCOT operators are necessarily involved in the development of these products and must be adequately trained in their use.  These development and training activities are in addition to the operators’ core operational duties.  In addition to the human resource impacts of this operational evolution, the financial and technical challenges to hardware and software development must be recognized and addressed.

| Goal 20 | Assess ERCOT operations capabilities in light of activities required to effectively integrate renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Where operational capabilities are improved, ensure adequate training is performed to maximize benefits. |
| --- | --- |

| Recommendation 04 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system operations resources, including operator training opportunities, to keep pace with rapidly evolving grid-connected emerging technologies. |
| --- | --- |

3.3.	Technical Considerations

One consequence of the introduction of competitive markets and open access transmission networks in North America is the surge in research and development of grid-connected technologies across the planning and operations spectrum – demand management technologies, distribution system devices, retail products and services, transmission system equipment, and generation and storage technologies to name a few.  But while many emerging technologies provide new benefits to the grid, they can also introduce new challenges.  In many respects, the industry is moving away from the model of a few workhorse technologies which provide the full range of grid functionality and toward a more robust, complex system comprised of numerous technologies providing more specialized functionality and, therefore, requiring higher degrees of coordination and integration.

3.3.1.	Technical Capabilities and Integration Challenges

Some renewable technologies, such as biomass-fueled generators, offer many of the technical capabilities of conventional generation resources familiar to system planners and operators while other renewable technologies are fundamentally distinct from the turbine technologies of the past four decades which comprise the majority of resources on the system.  As certain renewable technologies mature, additional capabilities are developed to provide grid services and facilitate network integration.  For example, early wind turbines essentially operate in an on or off mode – they have limited operational flexibility, very simple control systems (if any), and are often incapable of providing functionality common to other technologies such as unit ramp rate control or primary frequency response.  Newer wind turbines and control systems are equipped with greater functionality and can offer more system support services.

Equal to the challenge of keeping pace with emerging and rapidly evolving technologies is the detailed work of ensuring integration of the new technologies with existing grid-connected equipment and computer systems.  Large amounts of wind generation on the ERCOT system has reinforced many of the observed technical limits of the current zonal market operating systems and the portfolio-based 15-minute dispatch cycle.  Successful integration of the renewable energy resources of the future will require faster, more precise, and more flexible control systems than many of those currently used.

| Goal 21 | Improve and maintain stakeholder technical understanding of the capabilities and limitations of relevant emerging and evolving grid-connected technologies; their potential benefits and challenges for the system planning and operations functions; and facilitate collaborative stakeholder communications to solve technical integration issues. |
| --- | --- |

3.3.2.	Technical Approach to Renewable Technologies

ERCOT market rules maintain some technical requirements and standards for generation resources regardless of the generation technology type.  In other instances, ERCOT market rules recognize the technical capabilities of various generation technologies through technology-specific standards which respect the inherent limitations of different equipment types.  This is why many specific rules have been developed over the years applicable to specific resource types– nuclear, hydro, combined cycle, wind, and others.

At this point in time, there are few, if any, technology-specific market rules and technical standards for several of the emerging technologies which can reasonably be expected to connect to the ERCOT system in the near term such as Concentrating Solar Power (CSP), solar photovoltaic (PV), or various energy storage devices such as batteries or flywheels.  In some areas, the technical issues raised by these newer technologies are similar to those identified for wind resources, such as the lack of contribution to system inertia.  In other areas, these newer technologies may present issues not yet confronted by ERCOT planners or operators, such as the near-instantaneous ramping capability of certain solid-state storage technologies.

A key philosophical issue regarding technical requirements and standards for emerging technologies is whether it is appropriate to modify technical requirements to accommodate the unique characteristics of certain technologies in order to capture the market or reliability benefits they offer or whether maintenance of the technical standards developed over time to ensure system reliability outweighs the technical barrier to market entry such standards may create.

| Goal 22 | Strike an appropriate balance which maintains an open access paradigm allowing and encouraging introduction and integration of benficial technological advances while maintaining interconnection, registration, planning, and operating criteria which protect system security. |
| --- | --- |

| Goal 23 | As renewable generation and related technologies mature and enhanced capabilities become available, ensure technical standards are periodically evaluated to ensure best available technologies and practices are utilized where necessary and cost-effective. |
| --- | --- |

| Recommendation 05 | Preference should be given to prospective application of new technical standards except where clearly identified system security needs and/or cost benefit analyses determine application of new technical standards to existing equipment is warranted. Retrofitting and/or upgrading existing equipment is often much more expensive (if even possible) than incorporating required capabilities into the original equipment design and configuration. Retroactive application of technical standards can also raise innovation- and investment-stifling regulatory uncertainty. |
| --- | --- |

3.3.3.	Technical Challenges to System Planning

The technical challenges to effective system planning presented by emerging technologies are threefold.  First, system planners must understand the technical specifications of the equipment to be included in planning functions.  Secondly, they must develop the appropriate assumptions regarding penetration levels and geographic location to be included in planning studies.  Finally, many system planning tools themselves are not fully capable of modeling the various capabilities and limitations of emerging technologies.

| Goal 24 | Contribute to ERCOT’s development of longer-term system planning studies which include reasonable assumptions regarding the installation and capabilities of emerging renewable generation and related technologies. |
| --- | --- |

3.3.4.	Technical Challenges to System Operations

Similarly to the system planning function, system operations processes require accurate understanding and representation of equipment technical specifications.  ERCOT operators also require additional streams of Real Time information and near-Real Time forecasts to effectively and efficiently position the system to manage significant production from variable generation technologies.

| Goal 25 | Focus on near-term refinement and development of tools providing enhanced operational capabilities for ERCOT management of wind-related issues. In the longer term, evaluate potential tools needed to integrate other renewable technologies as operational issues are identified. |
| --- | --- |

3.3.5.	Technical Education and Institutional Knowledge

As technical knowledge is gained and incorporated into ERCOT market rules, systems, and processes, it is important that knowledge be documented and institutionalized to facilitate industry access to current technical information.  TRIP Goals 01, 05, 06, 13, 21 and 23 address this consideration.

3.4.	Market Design Considerations

In many instances it can be challenging to separate market design  issues from system reliability issues – one often impacts the other and the interrelatedness of both areas should be considered.  ERCOT market participants have limited ability to address many market design issues as they are often bound by larger policy decisions made by legislative and regulatory bodies.  As these issues are identified, they are communicated with policy makers.  Where stakeholders can address market design choices, a fundamental goal of the market rules process is to align market design elements and market participant incentives with desired market and reliability outcomes.

3.4.1.	Principles of ERCOT market design

In the search for renewable technology integration solutions, certain principals or core elements of the ERCOT market design must be respected as they are required by jurisdictional entities such as the open access network requirement set by the Texas Legislature or the energy-only market design ordered by the PUCT.  Other market design characteristics such as unit dispatch procedures, credit requirements, or settlement formulas are subject to extensive deliberation and modification through the stakeholder process.

3.4.2.	Impacts of Renewable Technologies on ERCOT Markets

At current penetration levels, renewable technologies have already demonstrated the ability to alter ERCOT market outcomes through downward pressure on energy prices, the need for ERCOT to procure additional capacity services, and ERCOT system dispatch actions to name a few.  Market impacts may have near-term and/or long-term consequences for overall market efficiency and/or sustainability.

.

| Goal 26 | Identify renewable technologies integration market design questions and impacts on market outcomes. Facilitate issues framing for resolution, if desired, by the appropriate stakeholder or policy making body. |
| --- | --- |

3.4.3.	Market Design Approach for Renewable Technologies

There are multiple possible approaches to framing and addressing the market design issues arising from the introduction of new technologies.  New products or services may be defined to facilitate market entry or qualifications for market participation may be modified to accommodate different technical parameters.  On the other hand, the presumption when examining new technologies may be that no modifications are needed to the market design element in question and that new technologies should meet existing qualification or performance criteria in order to participate in the market.  For example, a new generation technology may be able to offer something like the presently defined Regulation Service but may provide the service faster or cheaper but may not meet the qualifications to provide the service as it is currently defined.  However, the ERCOT system may not need a faster Regulation Service, or the market costs of changing systems to utilize a faster Regulation Service may outweigh the potential benefits of such a service.

| Goal 27 | Examine the potential development of market products and/or market design elements which maximize the market value of renewable technologies and/or minimize the impacts of such technologies. |
| --- | --- |

| Recommendation 06 | Text. |
| --- | --- |

3.5.	Performance Criteria and Compliance Metrics

Text.

3.5.1.	Principles of Performance Criteria and Compliance Metrics

Text.

3.5.2.	Application of Performance Criteria to Renewable Technologies

Where appropriate and useful, the TRIP identifies performance criteria and/or compliance metrics for renewable technologies to accomplish one or more of the following purposes:

- inform renwable technologies manufacturers and project developers of the technical capabilities required for units interconnected to the ERCOT system;

- set uniform performance expectations appropriate for each renewable technology;

- provide data to inform the renewable technologies integration process;

- provide data to gauge the success of renewable technologies integration efforts; and

- provide clear, enforceable measurements to ensure compliance with performance criteria.

.

3.5.3.	Application of Performance Data to Renewable Technologies Integration

Text.

3.6.	Cost Allocation

Text.

3.6.1.	Principles of Cost Allocation

Text.

3.6.2.	Cost Allocation Task Forces

Text.

3.6.3.	Application of Cost Allocation Principles to Renewable Technologies

Text.

3.7.	Texas Nodal Market Implementation

Text.

3.7.1.	Renewable Technologies Integration Benefits of the Texas Nodal Market

Text.

3.7.2.	Addressing Renewables Technologies Issues in Nodal Testing and Start Up

Text.

3.7.3.	Texas Nodal Market Implementation Schedule and Resource Requirements

Text.

3.7.4.	Post-TNMID Evaluation of Wind Operations Issues

Text.

3.7.5.	Nodal Parking Deck

Text.

4.	Key Issues and Strategies for Resolution

4.1.	System Planning Issues

| SP-01 Verify Wind Turbine Technical Data: Wind turbines of various vintages in the ERCOT system possess different technical capabilities. Generally speaking, newer turbine types offer more technically advanced features and control systems than older technologies. It is unclear whether ERCOT models for wind units are sufficiently accurate or detailed for system planning and operations purposes. |  |
| --- | --- |
| Priority | High. |
| Considerations | Policy: No policy impacts. |
|  | Reliability: Accurate technical data for use in system planning and operations models is critical to ensuring system reliability. |
|  | Technical: Accurate representation of WGR design, configuration, and technical capabilities and limitations are required inputs for various planning and operation functions. The Resource Asset Registration Form (RARF) for each WGR should reflect all relevant data. |
|  | Market: No market impacts. |
|  | Performance/Compliance: No performance criteria are recommended. No compliance metrics are recommended. |
|  | Cost Allocation: There are no costs to allocate. WGRs are responsible for submitting timely, accurate data to ERCOT through the RARF process. |
| Strategy | Recommendation XX: ERCOT and WGR owners should collaborate to ensure completeness and accuracy of relevant wind turbine technical data for use by ERCOT. |
| Activities | ERCOT XX: ERCOT Operations will develop questionnaire for WGR owners to complete. |
|  | MP XX: WGR owners must submit complete and accurate responses to ERCOT questionnaire. |
| Follow-Up | RTWG is charged to work with ERCOT to ensure updated technical data is transitioned for use by nodal market systems. |
| Schedule | The data update phase of SP-01 is complete. ERCOT sent the questionnaire to WGR owners in July 2008. All responses were deemed complete in January 2009. The follow-up activity should be completed by Sept. 2010. |

| SP-02 Wind Turbine Computer Models: Computer models used in operations and planning have not always been able to represent all wind-turbine technologies accurately. There are several factors affecting the accuracy of the modeling effort. One is the limitations of software geared to modeling conventional generation technologies. Another is the mutual lack of familiarity and understanding between modelers and WGRs leading to misunderstanding. Yet another factor is the rapid growth in the WGR capacity making an orderly response to the new technologies’ characteristics difficult. Lastly, there is the rapidly evolving nature of the WGR technology itself, which makes it difficult to keep models current. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This is a key reliability issue. Proper models are needed to accurately perform planning, design, and operational studies. While a variety of approximations are used for all technologies, the degree of approximation for WGRs has seemed excessive. |
|  | Technical: The modeling issue is partly the result of technical deficiencies in the computer software used to perform the needed studies. In addition, those designing the software and running the studies have limited experience with WGRs and require additional education and training. One major technical issue for the whole industry is the need to create non proprietary standard models for the many different WGR turbine types. |
|  | Market: Indirectly, lack of confidence in the models used for studies can result in unneeded conservatism on the part of system planners which can increase the cost of facilities designs and on the part of system operators which can increase the cost of market operations or lead to inefficient commitment of Resources. |
|  | Performance/Compliance: It is incumbent upon WGRs to provide accurate technical data to TSPs and ERCOT. Existing NERC standards and ERCOT Protocols define responsibilities and time frames. |
|  | Cost Allocation: No |
| Strategy | Near-term focus is to identify discrepancies between equipment on the ground and how that equipment is represented in studies. Two key areas should be addressed – lack of common understanding regarding technical specifications of equipment in the field and the technical capabilities and limitations of the modeling software itself. Recommendation XX: Increase ERCOT and market participant education regarding renewable generation technology and associated modeling issues. Recommendation XX: Encourage stakeholder participation in WGR model improvement efforts in the industry, such as the Electric Power Reasearch Institute (EPRI) Project 17. Recommendation XX: |
| Activities | ERCOT XX: Hold workshops for Market Participants and ERCOT staff to allow WGRs, equipment vendors, Transmission Service Providers, and ERCOT to present their information and issues to each other. Take advantage of study efforts to verify WGR data, to develop more appropriate models, and to initiate software changes. ERCOT and the Transmission Service Providers need to rework all forms and modeling processes to be appropriate for WGRs and use a common database for all studies. |
|  | MP XX: WGRs need to work with equipment suppliers to insure that the vendors provide complete, detailed, and accurate technical data for their equipment as needed to support all required studies. WGRs must update those that need their technical data promptly and completely as their plans and actual facilities change. |
| Follow-Up | Insure that the Voltage Ride Through findings relative to WGR modeling needs as well as the modeling data itself is captured and documented. Initiate revisions to procedures and Protocols to establish a common data collection system and data base for all generators with appropriate modifications to insure there is clear documentation of the actual characteristics of each technology’s facilities. |
| Schedule | Wind Workshop One, March 17, 2008 Wind Workshop Two, August 22, 2008 Wind Workshop Three, June 26, 2009 Wind Workshop Four; ERCOT requirements and Vendor solutions; July 2010 Voltage Ride Through Study phase 2; WGR data and model verification; June 2010 Data Repository; modify data collection and establish data base; after nodal go live |

| SP-03 Wind Turbine Fault Tolerance: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. WGRs had been given specific exemption from fault tolerance requirements. As more WGRs were added to the ERCOT system, it became necessary to evaluate existing WGR fault tolerance capabilities as well as to establish fault tolerance standards for new WGRs. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Yes; the policy issue that became evident was to determine the standard of need that must be demonstrated in order to require existing WGRs to meet any new requirements that could be very expensive. |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. However, existing WGRs may not be easily modified to meet new fault tolerance requirements and there may be a significant technical challenge to determining their actual requirement and then meeting it. In most cases, new WGRs can meet fault tolerance requirement by buying certain options in the wind-powered turbines. In most cases, those options cannot be retrofit onto existing wind-powered turbines; thus, the actual ability to meet new requirements may provide a significant technical challenge. |
|  | Market: New requirements would cause certain wind-powered turbines to no longer be able to be supplied for WGRs in ERCOT. The provision of fault tolerance for new WGRs from other wind-power turbine suppliers will increase WGR capital costs. There will not typically be any significant change in operating costs for new WGRs. There is little expected change in the competitive landscape for new WGRs that comply with new fault tolerance standards. For existing WGRs the possible expense of retrofitting existing equipment could be significant. Compliance may require the addition of very expensive dynamic reactive devices in the WGR substation. The expenses could cause some WGRs to be retired rather than be upgraded. For all WGRs there is likely to be both increased capital cost and operating cost as a result of complying with new standards. There are also commercial issues with inability to control single source prices and with warranty terms and conditions as well as warranty cost. These technical, cost, and commercial issues raise compliance with new standards by existing generators to a policy level. See SP-08 for additional details pertaining to existing WGRs. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: There is no cost allocation issues associated with new WGRs, costs will be borne by the new WGR. For existing WGRs see the discussion for SP-08. |
| Strategy | Establish new requirements for new WGRs that balance WGR capabilities and transmission system design requirements. For existing WGRs, evaluate need. Recommendation. Adopt an Operating Guide Revision Request establishing new standards for WGR Voltage Ride Through to provide WGR fault tolerance capability. Perform detailed studies using well groomed data to evaluate exiting WGRs capability to ride through system faults. |
| Activities | ERCOT (E X): Participate in the process of establishing new standards. Specify scope and contract for studies to evaluate the need for system design changes related to faults affecting existing WGRs. |
|  | Market Participants (MP X): TSPs, generators and all market participants actively participate in the development of new standards for WGRs. |
| Follow-Up | Codify new standards in protocols (see SO-12). Require needed studies for existing WGRs to be completed by a specific date (see SP-08). |
| Schedule | 11/17/2008 Operating Guide Revision Request 208 approved establishing new Voltage Ride Through standards for WGRs (see SO-12). Studies for existing WGRs are underway with results required by June 2010 (see SP-08). |

| SP-04 Voltage Transient and Small Signal Stability Study: The West-to-North Transfer study is performed annually by ERCOT Operations, with input from ERCOT Planning and review by the Dynamics Working Group. The purpose is to calculate how much power can safely be transferred from West to North while maintaining a safe small signal stability margin. The DWG assembles the dynamic data set necessary for ERCOT staff to do the study. |  |
| --- | --- |
| Priority | Medium or Medium-High |
| Considerations | Policy: None |
|  | Reliability: Yes. The results of the study inform ERCOT Operations how much transfer they can allow reliably in the real time operation. Without this information they must operate more conservatively to maintain the system reliability. |
|  | Technical: The technical challenge is to allow as much power transfer as possible without risking a system separation due to the undesired system oscillation. The solution is to do the study every year and limit the west to north power transfer based on small signal stability criteria. |
|  | Market: The market consideration is to maximize the wind-to-load transfer. |
|  | Performance/Compliance: Each transmission owner and DWG member must provide good dynamic models when requested. ‘Good’ in this context means (1) compatible with the version of software being used, and (2) accurately describing the electrical characteristics of the equipment. Re-using old models for old facilities is not always good enough. |
|  | Cost Allocation: None |
| Strategy | Recommendation. ERCOT staff will request an approved case from DWG and do the study annually. The TSPs will provide dynamic models to DWG to create the dynamic data set. ERCOT Operations will send a note or make a presentation to RTWG and other committees when the study is complete to discuss the results. |
| Activities | ERCOT (E X): ERCOT Operations will do the study and bring the results to committees. |
|  | Market Participants: TSPs – Maintain database of dynamic models of all transmission and generation facilities. Provide to DWG when requested. Insist on adequate generator models from developers before allowing energization. Resource Owners – Provide complete dynamic model of generator and provide to TSP and ERCOT staff. |
| Follow-Up | Repeat every year and any other time major system changes occur that may have impact on the study result. |
| Schedule | Each year: November DWG requests TSPs for input models. December TSPs submit modes. February DWG assembles the base case and checks it. March ERCOT does study. June ERCOT reports results. |

| SP-05 Impact of Wind Turbines on System Inertia: Determine the potential impact on system reliability of large amounts of wind turbine generating capacity on ERCOT’s system inertia requirements. This is the second of two entries on this topic. The first one was SO-08 which was resolved in October 2008 by a PDCWG (Performance, Disturbance, Compliance Working Group) presentation to ROS. SP-05 is looking to the future problem of maintaining system frequency as the sum of installed wind power capacity approaches the system minimum load. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: No policy considerations |
|  | Reliability: The reliability concern is that wind plants do not automatically respond to frequency deviations in the same way synchronous generators do. As the proportion of synchronous generation decreases, maintaining frequency will require more operator action, either in advance by under-frequency load-shed relay settings, or in real-time reaction by the operators at the Frequency Desk. Statement regarding the key issue to stabilize system frequency. |
|  | Technical: The technical challenge is how to operate the grid reliably with fewer synchronous generators available to respond automatically to frequency deviations. |
|  | Market Design: There is a long-term question whether units which provide spinning mass or stabilize system frequency will continue to be installed in the ERCOT system and whether such units will be able to remain online during periods of high wind production and correspondingly low prices. |
|  | Performance/Compliance: ERCOT: NERC CPS1 and DCS criteria and Balancing Authority ACE limit QSEs with synchronous generators: Correct SCE bias settings Wind-only QSEs: None now |
|  | Cost Allocation: To be determined. |
| Strategy | ERCOT Planning staff will study the problem. Recommendation: The recommendations will not be known until the study has been done. |
| Activities | ERCOT: ERCOT Planning staff will study the problem. |
|  | Market Participants: Unknown at this time |
| Follow-Up | This will be a periodically recurring study as the wind percentage of all ERCOT generation increases. |
| Schedule | ERCOT already provided data to NERC. When the NERC study is written it will inform ERCOT’s study. ERCOT staff will start this study when the VRT study is done (June 2010). |
| SP-06 Use of Variable Frequency Transformers to Solve Stability Problems: Text. |  |
| Priority | Text. |
| Considerations | Policy: Text. |
|  | Reliability: Text. |
|  | Technical: Text. |
|  | Market Design: Text. |
|  | Performance/Compliance: Text. |
|  | Cost Allocation: Text. |
| Strategy | Text. Recommendation X: Text. |
| Activities | ERCOT (XX): Text. |
|  | Market Participants (MP XX): Text. |
| Follow-Up | Text. |
| Schedule | Text. |
| Status | Text. |

| SP-07 Voltage Control Process: This issue has been raised in recognition of the fact that the West Texas / Panhandle will have many different transmission providers serving a large concentration of wind-powered generation. There has long been a need to coordinate voltage in response to large daily swings in load and the accompanying swings in generation. Transmission Service Providers (TSPs) have designed, installed, and operated the needed reactive devices for their systems. Operationally, the typical pattern has been to do ERCOT wide seasonal studies setting voltage profiles and then letting the Transmission Service Providers (TSPs) manage the day to day and hour to hour variations. Coordination of reactive designs between TSPs was needed only for special circumstances. The eight individual TSPs systems involved in the CREZ projects are intertwined with each other. One TSPs voltage control efforts can be expected to have a large impact on anther TSPs facilities. The large concentration of wind-power served by eight different TSPs requires a detailed and coordinated design effort and operating strategy. Thus this issue has both a planning and operations component. |  |
| --- | --- |
| Priority | High for the design component |
| Considerations | Policy: None |
|  | Reliability: Voltage control is a key reliability issue. The coordinated reactive design effort will determine a holistic solution. |
|  | Technical: Currently available technology will provide the needed reactive components. |
|  | Market: None |
|  | Performance/Compliance: Existing performance and compliance should be adequate to direct the design effort. |
|  | Cost Allocation: No new cost allocation issues are anticipated but there may be some issues when determining appropriate TSP to purchase and operate a particular reactive device. |
| Strategy | Recommendation. Initiate a reactive design study involving all TSPs in West Texas / Panhandle coordinated by ERCOT. |
| Activities | ERCOT (E X): ERCOT assist in developing a study scope and procuring study resources. |
|  | Market Participants (MP X): TSPs actively participate in developing the study scope, providing data, funding, managing the study and implementing the study design requirements. |
| Follow-Up | Normal planning, design, and certification processes provide the needed follow up procedures for the design effort. Additional follow up is needed for the operations component of this issue (see SO-10) |
| Schedule | The reactive design study is currently underway. May 2010 – reactive device requirements portion of the study completed. 2010-2013 TSPs specify, purchase, and install needed reactive devices. |

| SP-08 Voltage Ride-Through (VRT) Study: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. WGRs had been given specific exemption from fault tolerance requirements. As more WGRs were added to the ERCOT system, a process was initiated to establish fault tolerance standards for new WGRs. The process was expanded to include a study of system needs for existing WGRs during fault conditions. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Yes; the policy issue that became evident was to determine the standard of need that must be demonstrated in order to require existing WGRs to meet any new requirements that could be very expensive. |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. The studies needed to evaluate fault tolerance of existing WGRs require extremely detailed modeling of the WGRs. The software and data needed are generally available but the technical challenge results from the volume of data needed from many different organizations. Consistency in interpreting the data needs of the software and fidelity of the representation will require intense, centralized data review efforts. Existing WGRs may not be easily modified to meet new fault tolerance requirements and there may be a significant technical challenge to determining their actual requirement and then meeting it. In most cases, new WGRs can meet fault tolerance requirement by buying certain options in the wind-powered turbines. In most cases, those options cannot be retrofit onto existing wind-powered turbines; thus, the actual ability to meet new requirements may provide a significant technical challenge. It is possible that design changes to the transmission system will be the most effective and economical solution to any problems that are found. |
|  | Market: For existing WGRs the possible expense of retrofitting existing equipment could be significant. Compliance may require the addition of very expensive dynamic reactive devices in the WGR substation. The expenses could cause some WGRs to be retired rather than be upgraded. For all WGRs there is likely to be both increased capital cost and operating cost as a result of complying with new standards. There are also commercial issues with inability to control single source prices and with warranty terms and conditions as well as warranty cost. These technical, cost, and commercial issues raise compliance with new standards by existing generators to a policy level. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: The cost of any new equipment to resolve any issues associated with existing WGRs must be determined from the results of the VRT study. The study results may indicate that equipment changes at some WGRs will resolve any system problems for all WGRs. Transmission system changes may provide the needed solution to any problems. The study results are thus needed to identify cost allocation issues, if any. |
| Strategy | For existing WGRs, evaluate need for any VRT related design changes. Recommendation. Perform detailed studies using well groomed data to evaluate exiting WGRs capability to ride through system faults. The study scope shall include detailed modeling. A major effort to collect consistent and correct detailed data needs to be a part of the study effort. |
| Activities | ERCOT (E X): Specify scope and contract for studies to evaluate the need for system design changes related to faults affecting existing WGRs. Provide staff to oversee the study. |
|  | Market Participants (MP X): WGRs gather needed detailed data from vendors and cooperate with ERCOT in insuring consistency and fidelity of the modeling. |
| Follow-Up | ERCOT manage the study effort. Study results need to be communicated to market participants. The Regional Planning Group and the Reliability and Operations Subcommittee must review the study results and establish required equipment changes. A follow up protocol revision may be required to designate the parties required to implement the required equipment changes. |
| Schedule | Studies for existing WGRs are underway with results required by June 2010. Study results should be reviewed by October 2010 with any follow up protocol revisions initiated in November 2010. |

| SP-09 Wind Turbine Model Validation: ERCOT Operations, ERCOT Planning, and the Dynamics Working Group do a variety of studies that require dynamic models of individual wind generator turbines and entire wind farms. The existing dynamic models are of mixed vintage and quality. The behavior of the models in time-simulations should be compared to the in-service behavior of wind farms to assure everyone that all the studies run with them are accurate. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: Should any machine or device be allowed to be connected to the grid without being studied? |
|  | Reliability: Not a grid reliability issue. |
|  | Technical: Ideally ERCOT should have an industry or academic or government partner for this. The validation of the dynamics models will benefit other ISOs and the entire industry. Possible partners are UWIG, NREL, DOE, EPRI, and UT Arlington. |
|  | Market: Not a market issue. |
|  | Performance/Compliance: Not a compliance issue. |
|  | Cost Allocation: Unknown |
| Strategy | Recommendation: RTWG member Howard Daniel could check EPRI Project 173 and bring the details to ERCOT Planning staff and the Dynamics Working Group. |
| Activities | ERCOT: Run time-simulations with the existing models that match measured events in field. Provide results and SCADA-gathered measurements to EPRI for comparison. If the comparisons are not good, return to the authors of the existing models to request revision. |
|  | Market Participants: Unknown, possibly none. |
| Follow-Up | Compare notes with the EPRI project results. Submit results to IEEE for publication. Report to ERCOT Regional Planning Group. Present to UWIG conference. |
| Schedule | Unknown |

| SP-10 DOE Long-Term Planning Study: Text. |  |
| --- | --- |
| Priority | Text. |
| Considerations | Policy: Text. |
|  | Reliability: Text. |
|  | Technical: Text. |
|  | Market Design: Text. |
|  | Performance/Compliance: Text. |
|  | Cost Allocation: Text. |
| Strategy | Text. Recommendation X: Text. |
| Activities | ERCOT (XX): Text. |
|  | Market Participants (MP XX): Text. |
| Follow-Up | Text. |
| Schedule | Text. |
| Status | Text. |

4.2.	System Operations Issues

| SO-01 Inventory of Wind Generation Facilities: As wind-power was added to the ERCOT system it became apparent that there were inconstancies in the communications between WGRs, ERCOT, and Transmission Service Providers. ERCOT launched a number of initiatives to address the communication and interpretation inconsistencies. The Inventory of Wind Generation Facilities was initiated by ERCOT to insure that ERCOT and the WGRs were communicating correctly about voltage control capability, reactive devices, and operating procedures. ERCOT staff engaged in an effort to contact each WGR in writing and by phone to answer specific questions about the WGR’s voltage control equipment and procedures. Written responses from the WGRs were all followed up with site visits and/or phone calls by ERCOT staff to insure there was a common understanding and interpretation of the questions and responses. The inventory process led to many follow up initiatives including changes in data collection forms and procedures (SP-01, SP-02, SP-09), workshops (WT-02, WT-05), and better coordination with Transmission Service Providers (TSPs)(SO-15). The actual inventory has been completed but follow up activities are still ongoing; thus this issue remains open. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: No |
|  | Reliability: Consistent interpretation of requirements and communications is fundamental to reliable operations. The lack of familiarity with ERCOT by the new WGRs and the lack of familiarity with wind-power by ERCOT and TSPs can result in miscommunication. |
|  | Technical: No |
|  | Market: No |
|  | Performance/Compliance: No new compliance considerations, but better understanding and communications will result in a higher standard of compliance. |
|  | Cost Allocation: No |
| Strategy | The basic issue that was identified was the need for more communication and common understanding of ERCOT requirements and WGR characteristics. Recommendation: Develop a common understanding of ERCOT requirements and procedures and WGR equipment characteristics through direct verbal communication between ERCOT and WGRs. |
| Activities | ERCOT (E X): Directly communicate in person or by phone with each WGR to establish a common understanding of the WGRs chacteristics. |
|  | Market Participants (MP X): WGRs proactively communicate with ERCOT to insure information is understood. |
| Follow-Up | SP-01 Verify Wind Turbine Technical Data SP-02 Wind Turbine Computer Models SP-09 Wind Turbine Model Validation WT-02 and WT-05 Wind-power Workshops SO-15 Communications Between Wind Farms and TSPs |
| Schedule | The inventory process is complete. Follow up activity is ongoing (see respective issues) A project to create a common generator data base for use by ERCOT planning, ERCOT operations, ERCOT dispatch software, and TSPs is scheduled to start soon after the Nodal go live date. |

| SP-02 Wind Turbine Computer Models: Computer models used in operations and planning have not always been able to represent all wind-turbine technologies accurately. There are several factors affecting the accuracy of the modeling effort. One is the limitations of software geared to modeling conventional generation technologies. Another is the mutual lack of familiarity and understanding between modelers and WGRs leading to misunderstanding. Yet another factor is the rapid growth in the WGR capacity making an orderly response to the new technologies’ characteristic difficult. Lastly, there is the constant changing of the WGR technology itself making even recent WGR modeling efforts outdated. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This is a key reliability issue. Proper models are needed to accurately perform planning, design, and operational studies. While a variety of approximations are used for all technologies, the degree of approximation for WGRs has seemed excessive. |
|  | Technical: The modeling issue is partly the result of technical deficiencies in the computer software used to perform the needed studies. In addition, those designing the software and running the studies have limited experience with WGRs and require additional education and training. One major technical issue for the whole industry is the need to create non proprietary standard models for the many different WGR turbine types. |
|  | Market: Indirectly, lack of confidence in the models used for studies can result in unneeded conservatism which increases the cost of designs and operations. |
|  | Performance/Compliance: It is incumbent upon the WGRs to provide accurate technical data to Transmission Service Providers and to ERCOT in a timely way. There are existing NERC standards AND ERCOT Protocols that define that responsibility and required time frames. |
|  | Cost Allocation: No |
| Strategy | The focus needs to be on identifying disconnects between equipment on the ground and the representation in studies. There are two main aspects to be addressed; lack of understanding leading to miscommunication, and the technical capability of the software. Recommendation. Increase education of all parties about the technology and the modeling issues. Add resources to ERCOT planning staff to address all study related issues. Lead and participate in industry wide WGR model improvement efforts. |
| Activities | ERCOT (E X): Hold workshops for Market Participants and ERCOT staff to allow WGRs, equipment vendors, Transmission Service Providers, and ERCOT to present their information and issues to each other. Take advantage of study efforts to verify WGR data, to develop more appropriate models, and to initiate software changes. ERCOT and the Transmission Service Providers need to rework all forms and modeling processes to be appropriate for WGRs and use a common database for all studies. |
|  | Market Participants (MP X): WGRs need to work with equipment suppliers to insure that the vendors provide complete, detailed, and accurate technical data for their equipment as needed to support all required studies. WGRs must update those that need their technical data promptly and completely as their plans and actual facilities change. |
| Follow-Up | Insure that the Voltage Ride Through findings relative to WGR modeling needs as well as the modeling data itself is captured and documented. Initiate revisions to procedures and Protocols to establish a common data collection system and data base for all generators with appropriate modifications to insure there is clear documentation of the actual characteristics of each technology’s facilities. |
| Schedule | Wind Workshop One; Title; Date Wind Workshop Two; Title; Date Wind Workshop Three; Title; Date Wind Workshop Four; ERCOT requirements and Vendor solutions; July 2010 Voltage Ride Through Study phase 2; WGR data and model verification; June 2010 Data Repository; modify data collection and establish data base; after nodal go live |

| SO-03 : Wind-powered Generation Response to Down Balancing Instructions When wind-powered generators receive a down balancing instruction, it became apparent that ERCOT did not have a consistent reference point to base their calculation of the effect of their order. This problem is a result of the zonal market design and specific software limitations that do not exist in the nodal market. A process has been completed requiring all WGRs to update their resource plan every hour and to use the best forecast available. As time goes on, it is expected that the AWS TrueWind forecast provided by ERCOT will be the best forecast available. At the present time, some WGRs have forecasting methods with good track records which are better than the ERCOT forecast for their facility. During this transition process, the WGR is allowed to use its own forecast unless the ERCOT forecast is better. Thus the new procedures will improve ERCOT’s ability to calculate the effect of their down balancing instructions in the zonal market without the need for substantial zonal software changes. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: ERCOT operations routinely calculates a balancing offset to account for the differences between what the software thinks WGRs are doing and what they are actually doing. Extreme errors in calculating the effects of down balancing instructions can lead to reliability issues. |
|  | Technical: There is no real technical issue; the solution that has been proposed is the most cost effective way to improve results without spending considerable time and money to change software that is about to be replaced. The nodal software completely resolves this issue. |
|  | Market: No market impacts. |
|  | Performance/Compliance: This new process imposes new requirements on WGRs. The requirements are clear and enforceable. |
|  | Cost Allocation: No cost allocation issues. |
| Strategy | Develop a workable solution and wait for the nodal market for the full resolution of the issue. Recommendation : Require all WGRs to update their resource plan every hour using the best available forecast. |
| Activities | ERCOT (E X): Monitor the accuracy of WGR forecasts as needed. |
|  | Market Participants (MP X): WGRs change procedures to insure hourly updates and to insure that the most accurate forecast is being used. |
| Follow-Up | None |
| Schedule | 9/15/2009 Protocol Revision Request 812 was approved |
| SO-04 – Smart Grid Implications for Renewable Resources – Determine how development of a "smart grid" might benefit and improve integration of renewable resources into the ERCOT grid. Specifically, determine if there are new technical capabilities associated with electronic metering and monitoring systems that would allow higher penetration of renewable resources, particularly at the customer (i.e., distribution) level. |  |
| Priority | Low |
| Considerations | Policy: This issue might involve policy considerations depending on the type and level of “smart grid” deployment. |
|  | Reliability: This issue involves reliability considerations, particularly if it encourages deployment of additional renewable resources at or near a customer’s premises. |
|  | Technical: This issue involves the technical feasibility considerations associated with deployment of a “smart grid” and its associated hardware and software. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does include performance or compliance considerations, particularly if new generation resources are connected at the distribution level. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Examine hardware and software capabilities of electronic metering equipment and other electronically-controlled devices associated with a “smart grid” deployment to determine if they will benefit integration of additional renewable generation resources, particularly at the distribution voltage level. |
| Activities | ERCOT (XX): Assist market participants in the preparation of a whitepaper examining the various technologies associated with deployment of “smart grid” technology in ERCOT. |
|  | Market Participants (MP XX): Prepare a whitepaper examining the various technologies associated with deployment of a “smart grid” and assess the capability of such technologies to improve or enhance integration of additional renewable generation technologies. |
| Follow-Up | If the concepts presented in the final whitepaper gain market acceptance, then market participants should follow-up with appropriate changes in the ERCOT Protocols and/or Operating Guides to facilitate the deployment of “smart grid” technology in the ERCOT market. |
| Schedule | Topics for whitepaper are under discussion at RTWG; a draft whitepaper should be available for review by the end of 2010. |

| SO-05 Operational Studies Related to Wind-powered Generation: This issue is essentially a follow up to the GE Ancillary Services study. ERCOT now has a growing data base of actual wind-power operations at a significant level of penetration. Using that data base, a new study could use actual data rather than assumed data to evaluate the need for new ancillary services, the need for new operating procedures, and the need for wind-power to be certified to provide regulation service. Key areas for further study might include evaluation of actual WGR ramping history, and evaluation of low load high wind-power scenarios. The objective of the study is to further refine operational tools as we increase WGR installed capacity above 15,000 MW. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: As additional wind-power is added to ERCOT, there may be new and unfamiliar operating situations. Anticipating and studying those situations can prepare ERCOT staff to handle the situations reliably. |
|  | Technical: There may be some issues in how WGRs can provide reliability services. |
|  | Market: There could be a large market impact if operational needs are not investigated ahead of time to determine the most effective methods of insuring system reliability. |
|  | Performance/Compliance: There may be new operational requirements or new services that are defined which need follow up to establish Performance/Compliance requirements. |
|  | Cost Allocation: No |
| Strategy | ERCOT has initiated a variety of much needed studies having to do with stability, voltage control, ancillary services, and voltage ride through. It is critical that ERCOT continue to anticipate and study future operational issues in order to avoid entering an unfamiliar operating situation unprepared. Recommendation: Perform an update of the ancillary service study using actual WGR data with an emphasis on fleshing out any operational procedure and resource changes that may be needed. |
| Activities | ERCOT (E X): ERCOT needs to lead the effort to determine the study scope and acquire the study resources. |
|  | Market Participants (MP X): All market participants should assist in determining the study scope. |
| Follow-Up | The results of the study will dictate any follow up that is needed. Possible outcomes include new procedures, mechanisms for WGRs to provide regulation, or changed ancillary services. |
| Schedule | The need for this update is not immediate. Operational data from the Nodal market may be required for a meaningful study. The updated study and some of the follow up should be completed before 2013 at which time it can be anticipated that WGR capacity will exceed 15,000 MW. |

| SO-06 – Testing Reactive Capability of Wind Generation – Determine the appropriate testing methodology to measure the reactive capability of wind generation. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue does not involve policy considerations. |
|  | Reliability: This issue involves reliability considerations, particularly if a wind generator cannot meet the reactive capability requirements. |
|  | Technical: This issue involves the technical feasibility considerations associated field testing reactive capability of wind turbine generation. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does include performance or compliance considerations, particularly if wind generator reactive capability cannot be accurately measured. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Review reactive capability testing methodologies used by other power regions (domestic and foreign) to determine an appropriate testing methodology for use in the ERCOT market. |
| Activities | ERCOT (XX): Review reactive capability testing methodologies used by other power regions (domestic and foreign) as well as ERCOT’s existing methodology and recommend, if necessary, changes to the ERCOT Protocols and/or Operating Guides to accommodate the new validation process. |
|  | Market Participants (MP XX): Provide input and guidance to ERCOT during its review of testing methodologies and implement any subsequent recommendations as necessary in either the ERCOT Protocols or Operating Guides. |
| Follow-Up | None at this time. |
| Schedule | Develop any proposed changes in testing methodology by the end of the second quarter of 2011. |

| SO-07 Wind Generation and High System Frequency: Wind turbines in ERCOT do not provide primary frequency control through Automatic Generation Control (AGC) or governors. Energy production from wind generation can impact system frequency during periods of increasing wind speeds, in particular during periods when frequency exceeds 60 Hertz. This issue seeks to address the types of controls and/or requirements available or necessary for wind turbines to provide the necessary AGC-like response during periods of high system frequency. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue does not involve a Commission, ERCOT or NERC policy at this time. |
|  | Reliability: This issue addresses maintaining adequate system reliability during periods when system frequency is higher than normal. |
|  | Technical: Some types of wind turbines can provide primary frequency response, others cannot. This issue assesses any possible alternative methods available to provide primary frequency response. |
|  | Market: Is primary frequency response better provided by imposing technical requirements on WGRs or by devising a market mechanism to provide the service? |
|  | Performance/Compliance: Performance criteria are to be specified in the PRR / NPRR. Compliance will be done on a spot-check (event-driven) basis. |
|  | Cost Allocation: If primary frequency response capability is required of WGRs, each WGR will bear the cost of such capability. |
| Strategy | Recommendation X: Develop a Protocol Revision Request to require wind generator control systems to be programmed to respond to frequency deviations by controlling WGR real power output in a way that is similar to governor response for conventional steam generators. |
| Activities | ERCOT (E X): None |
|  | Market Participants (MP X): The Wind Operations Task Force of the ERCOT Reliability and Operations Subcommittee (ROS) developed a Protocol Revision Request (PRR) 824 – Primary Frequency Response to add a requirement for wind generator control systems to be programmed to respond to frequency deviations by controlling WGR real power output in a way that is similar to governor response for conventional steam generators. This PRR was approved by the ERCOT Board of Directors in December, 2009 and it applies to new wind generators with Standard Generation Interconnection Agreements signed after January 1, 2010. Another PRR, PRR 833 – Primary Frequency Response from Existing WGRs is currently under review in the ERCOT PRR process. |
| Follow-Up | It is expected that normal and ongoing PDCWG review of system frequency disturbances will reveal if there is still a concern regarding the adequacy of primary frequency response on the ERCOT system. |
| Schedule | PRR 833 is tabled at TAC. |

| SO-08 Impact of Wind Turbines on System Inertia: Determine the potential impact on system interia and develop possible solutions. This is the first of two entries on this topic. The other one is SP-05 which will be done by ERCOT Planning staff after the VRT study is done (June 2010). SO-08 was resolved in October 2008 by a PDCWG (Performance, Disturbance, Compliance Working Group) presentation to ROS. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: No policy considerations |
|  | Reliability: The reliability concern is that wind plants do not automatically respond to frequency deviations in the same way synchronous generators do. As the proportion of synchronous generation decreases, maintaining frequency will require more operator action, either in advance by under-frequency load-shed relay settings, or in real-time reaction by the operators at the Frequency Desk. |
|  | Technical: The technical challenge is how to operate the grid reliably with fewer synchronous generators available to respond automatically to frequency deviations. |
|  | Market Design: The challenge is to ensure the appropriate mix of Resources is available in Real Time to respond to frequency variations. |
|  | Performance/Compliance: ERCOT: NERC CPS1 and DCS criteria and Balancing Authority ACE limit QSEs with synchronous generators: Correct SCE bias settings Wind-only QSEs: None now. |
|  | Cost Allocation: None. |
| Strategy | PDCWG reported by to ROS in October 2008 without making a recommendation. |
| Activities | ERCOT XX: ERCOT Planning staff will study the problem. |
|  | Market Participants: None |
| Follow-Up | This will be a recurring study for ERCOT Planning staff as the wind percentage of all ERCOT generation increases. |
| Schedule | PDCWG reported by to ROS in October 2008. |

| SO-09 SCADA Control of Generator Circuit Breakers: The ERCOT protocols do not specify a number of operating requirements in any detail. Unlike conventional generation resources WGR technology and operating characteristics allow for considerable automation and operation from remote sites. As a result, there is often no staff at the WGR site. Transmission Service Provider (TSP) and ERCOT operators assume people are available on site to perform certain operations. The lack of onsite staff can be accommodated as long as the needed operations can be handled remotely. All WGRs did not have the same level of remote control and/or automation. A task force of TSP, ERCOT, and WGR operators was formed to identify the required operations and the standard for compliance. The task was expanded to include all generators since the newly specified requirements were appropriate for all technologies. This issue has been addressed and is now complete. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Limited impact on reliability but certain local situations could lead to out of tolerance operation if the issue were not addressed. |
|  | Technical: None |
|  | Market: Some increase in cost for WGRs. |
|  | Performance/Compliance: Clearly establishes uniform performance requirements. |
|  | Cost Allocation: None |
| Strategy | Specifying requirements that are generally assumed to be in place provides a clear and uniform compliance regime. Recommendation : Develop clear written specifications for operational needs heretofore simply assumed to be in place. |
| Activities | ERCOT (E X): Participate in establishing the operational requirements. |
|  | Market Participants (MP X): All market participants, but especially generators and TSPs participate with ERCOT to establish the requirements. |
| Follow-Up | None |
| Schedule | Operating Guide Revision Request 226 was approved December 2009 |

| SO-10 Voltage Control Process: This issue has been raised in recognition of the fact that the West Texas / Panhandle will have many different transmission providers serving a large concentration of wind-powered generation. There has long been a need to coordinate voltage in response to large daily swings in load and the accompanying swings in generation. Transmission Service Providers (TSPs) have designed, installed, and operated the needed reactive devices for their systems. Operationally, the typical pattern has been to do ERCOT wide seasonal studies setting voltage profiles and then letting the Transmission Service Providers (TSPs) manage the day to day and hour to hour variations. Coordination of reactive designs between TSPs was needed only for special circumstances. The eight individual TSPs systems involved in the CREZ projects are intertwined with each other. One TSPs voltage control efforts can be expected to have a large impact on anther TSPs facilities. The large concentration of wind-power served by eight different TSPs requires a detailed and coordinated design effort and operating strategy. Thus this issue has both a planning and operations component. |  |
| --- | --- |
| Priority | Medium for the operations component |
| Considerations | Policy: None |
|  | Reliability: Voltage control is a key reliability issue. |
|  | Technical: Currently available technology will provide the needed reactive components. However new operating practices and requiring new coordination strategies may be needed. |
|  | Market: None |
|  | Performance/Compliance: Existing performance and compliance should be adequate unless radically different operating procedures are developed. |
|  | Cost Allocation: No new cost allocation issues are anticipated. |
| Strategy | Recommendation. Include an operational analysis in the reactive design study to evaluate the level of coordination needed to respond to load and generation changes in West Texas / Panhandle. Evaluate the adequacy of current voltage control procedures. |
| Activities | ERCOT (E X): ERCOT assist in developing a study scope and procuring study resources. ERCOT lead the effort to assess the adequacy of standard voltage control procedures when operating the CREZ system. |
|  | Market Participants (MP X): TSPs, generators, and all other market participants actively participate in the evaluation of voltage control procedures for the CREZ system. |
| Follow-Up | The Reliability and Operations Subcommittee needs to review ERCOT and TSP plans for voltage control of the CREZ system. |
| Schedule | The reactive design study is currently underway. June 2010 – reactive operational review portion of the study completed. June 2011 – ERCOT and TSPs establish any needed new procedures. |

| SO-11 Technology-Specific Procedures and Protocols Changes: Text. |  |
| --- | --- |
| Priority | Text. |
| Considerations | Policy: Text. |
|  | Reliability: Text. |
|  | Technical: Text. |
|  | Market Design: Text. |
|  | Performance/Compliance: Text. |
|  | Cost Allocation: Text. |
| Strategy | Text. Recommendation X: Text. |
| Activities | ERCOT (XX): Text. |
|  | Market Participants (MP XX): Text. |
| Follow-Up | Text. |
| Schedule | Text. |
| Status | Text. |

| SO-12 Low Voltage Ride Through (VRT) for Wind Generators: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. WGRs had been given specific exemption from fault tolerance requirements. As more WGRs were added to the ERCOT system, a process to establish fault tolerance standards for new WGRs was initiated. This process has been completed. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Not for new WGRs. A policy issue did develop for existing WGRs (see Sp-03 and SP-08). |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. |
|  | Market: New requirements would cause certain wind-powered turbines to no longer be able to be supplied for WGRs in ERCOT. The provision of fault tolerance for new WGRs from other wind-power turbine suppliers will increase WGR capital costs. There will not typically be any significant change in operating costs for new WGRs. There is little expected change in the competitive landscape for new WGRs that comply with new fault tolerance standards. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: There is no cost allocation issues associated with new WGRs, costs will be borne by the new WGR. |
| Strategy | Establish new requirements for new WGRs that balance WGR capabilities and transmission system design requirements. Recommendation. Adopt an Operating Guide Revision Request establishing new standards for WGR Voltage Ride Through to provide WGR fault tolerance capability. |
| Activities | ERCOT (E X): Participate in the process of establishing new standards. |
|  | Market Participants (MP X): TSPs, generators and all market participants actively participate in the development of new standards for WGRs. |
| Follow-Up | None |
| Schedule | 11/17/2008 Operating Guide Revision Request 208 approved establishing new Voltage Ride Through standards for WGRs (see SO-12). |

| SO-13 Performance Metrics for Wind Generation: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-14 Impact of Transmission Outage Planning on Wind-powered Generation: Transmission outages can affect all generators at one time or another. Transmission Service Providers (TSPs) do an excellent job of keeping planned transmission outages as short as possible. When the TSP suspects that an outage will have a large impact on the market, then they do their best to mitigate the impact. The problem is that the TSPs have no way to estimate the impact of a transmission outage on the market. Since the marginal cost for WGRs is often so dramatically different than the market price, outages can have a huge effect on WGR revenue. This situation is further exacerbated by the common practice of TSPs to schedule outages in the spring and the fall in order to miss high load seasons. WGRs produce much of their power in the windy spring and fall months. Concentrating outages at these times increases the likely market impact on WGRs. Discussions were initiated in the Regional Planning Group to address these two issues. The basic idea is to provide TSPs sufficient information to know when extra ordinary measures to mitigate market impacts are warranted. ERCOT staff did an excellent job of bringing forward possible methods of including market impacts when considering transmission outage scheduling issues. It was noted that the software needed to estimate market impacts was part of the nodal package. These discussions resulted in the identification of additional transmission issues that needed attention (SO-20, SO-29, SO-31, and SO-34). The discussions also focused on CRR study assumption stability. Despite significant discussion, no progress has been made on identifying market impacts that justify mitigation. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: Yes, there are a number of policy issues raised in the discussion that most likely need to be addressed to allow the issue to be resolved. To what extent will TSPs be allowed to recover the cost of extra ordinary mitigation efforts, no matter how well justified? What will be the standard of accuracy required of the market impact estimation process? |
|  | Reliability: This is primarily an efficiency issue and properly done, there are no reliability impacts. There is some fear that once the market cost of transmission outages is known there will be pressure on TSPs to defer maintenance or delay inspections. |
|  | Technical: Market impact estimation processes exist but increasing the accuracy could be a challenge. Mitigation measures do exist but developing better ways to work on energized facilities and doing more predictive maintenance may require new technology. |
|  | Market: This is a major market issue. Transmission outages have always had a huge impact on production costs. Even modest improvements in efficiency could result in large reductions in production cost. |
|  | Performance/Compliance: There could be new performance requirements and compliance measures to implement any change in transmission outage scheduling. |
|  | Cost Allocation: There may be ways to identify generation resources that would benefit from the mitigation and assign the cost of mitigation to them. This would raise many issues since identifying what level of mitigation is “normal” will be subjective. |
| Strategy | Now that TSPs and generators are unbundled it seems appropriate to determine the effects of transmission operations on the market. Recommendation: Start using the transmission outage market impact software to estimate the production cost impact of the outage. Compare the estimated cost with the actual cost based upon actual system conditions at the time of the outage. |
| Activities | ERCOT (E X): ERCOT needs to devote the needed staff to perform market cost estimates and comparisons and communicate results to market participants. |
|  | Market Participants (MP X): TSPs need to identify policy and regulatory roadblocks to their ability to use transmission outage market cost information as a basis for extraordinary mitigation efforts. |
| Follow-Up | This issue needs routine follow up by the Regional Planning Group (RPG) after nodal go live. |
| Schedule | The RPG should discuss preliminary results of market cost calculations in March 2011. |

| SO-15 Communication Between Wind-power Ranches and Transmission Service Providers (TSPs): The newness of the WGR technology and the lack of familiarity with ERCOT and TSP procedures have led to multiple communication issues. A portion of the needed resolution focused on more complete and clear written requirements (see SO-09). In addition, a key component was familiarizing all parties with the procedures and issues of the other parties. A series of management level meetings between TSPs and WGRs developed strategies to increase communication effectiveness. The result was a series of workshops and proactive efforts to become more familiar with WGRs were another way to address the lack of knowledge. As an example one TSP, ONCOR, sent all of their transmission operators to WGR sites with specific learning objectives so that the TSP and WGR operators could improve their working relationship. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: Poor understanding of each other can lead to incorrect results when operating the ERCOT system. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Better understanding and working relationships can result in better performance. |
|  | Cost Allocation: None |
| Strategy | Continue with ERCOTs long history of face to face contact between various operating groups. Recommendation: Recognize that WGRs represent a new technology not familiar to electric system operators. Take proactive steps to remove barriers to effective communication. |
| Activities | ERCOT (E X): Schedule workshops to communicate specific information but to also provide an opportunity for contact between system operators and WGR operators. |
|  | Market Participants (MP X): WGRs proactively seek opportunities to understand TSP and ERCOT procedures and issues. Provide familiarization opportunities at WGR sites. |
| Follow-Up | None |
| Schedule | Immediate action has been taken and completed. |

| SO-16 Wind Generation Ramp Limits: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-17 – Mid-Term and Short-Term Load Forecast Weather Sensitivity – Determine if sensitivity of the ERCOT mid-term and short-term weather forecasts were a major reason for the February 26, 2008 wind event that caused ERCOT to interrupt load due to a drop in system frequency resulting from a rapid reduction in wind generation while customer loads were rapidly increasing. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue does not involve policy considerations. |
|  | Reliability: This issue involves reliability considerations related to operation, voltage control, reactive capability, frequency response, and power production forecasting for wind generation resources. |
|  | Technical: This issue involves the technical capabilities of ERCOT to accurately forecast load and market participants to accurately forecast wind generation output. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does include performance or compliance considerations applicable to all wind generation facilities regarding scheduling and operations. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Analyze the circumstances surrounding the February 26, 2008 wind event to determine if ERCOT’s weather forecast, which impacts both the load forecast and the wind generation output, was a contributing factor. |
| Activities | ERCOT (XX): Provide forecast and operational data related to the February 26, 2008 wind event to market participants. |
|  | Market Participants (MP XX): Analyze data provided by ERCOT related to the weather, load and wind production forecasts for the February 26, 2008 wind event and make any necessary recommendations for changes to prevent a reoccurrence. |
| Follow-Up | None necessary |
| Schedule | ISSUE COMPLETE: The Wind Operations Task Force (WOTF) analyzed data provided by ERCOT related to the February 26, 2008 wind event and determined that weather forecast sensitivity was not a major factor. The WOTF recommended to the ERCOT Reliability and Operations Subcommittee (ROS) that no changes were necessary and ROS concurred. |

| SO-18 Evaluate Transmission Line and Wind Power Production Outage Criteria: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-19 Improve Competitively Sensitive Constraint (CSC) Process: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-20 Dynamic Transmission Line Ratings: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-21 Evaluate Emergency Electric Curtailment Plan (EECP) Steps: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-22 Performance Metrics for Wind Generation: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-23 – Impact of Advanced Meters/ Smart Grid on Integration of Renewable Resources – Determine the impact of the development of a "smart grid" on integration of renewable resources into the ERCOT grid. Specifically, determine if there are new technical capabilities associated with electronic metering and monitoring systems that would allow higher penetration of renewable resources, particularly at the customer (i.e., distribution) level. (Note: This issue is essentially the same as Issue SO-4 - Smart Grid Implications for Renewable Resources and thus, should be deleted and the Issue number re-used) |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: This issue might involve policy considerations depending on the type and level of “smart grid” deployment. |
|  | Reliability: This issue involves reliability considerations, particularly if it encourages deployment of additional renewable resources at or near a customer’s premises. |
|  | Technical: This issue involves the technical feasibility considerations associated with deployment of a “smart grid” and its associated hardware and software. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does include performance or compliance considerations, particularly if new generation resources are connected at the distribution level. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Examine hardware and software capabilities of electronic metering equipment and other electronically-controlled devices associated with a “smart grid” deployment to determine if they will benefit integration of additional renewable generation resources, particularly at the distribution voltage level. |
| Activities | ERCOT (XX): Assist market participants in the preparation of a whitepaper examining the various technologies associated with deployment of “smart grid” technology in ERCOT. |
|  | Market Participants (MP XX): Prepare a whitepaper examining the various technologies associated with deployment of a “smart grid” and assess the capability of such technologies to improve or enhance integration of additional renewable generation technologies. |
| Follow-Up | If the concepts presented in the final whitepaper gain market acceptance, then market participants should follow-up with appropriate changes in the ERCOT Protocols and/or Operating Guides to facilitate the deployment of “smart grid” technology in the ERCOT market. |
| Schedule | Topics for whitepaper are under discussion at RTWG; a draft whitepaper should be available for review by the end of 2010. |

| SO-24 Settlement of Advanced Meters in the Nodal Market: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-25 Generator Governor Response for Wind-powered Generators: When system frequency deviates from the planned frequency of 60 Hz, then conventional, synchronous generators and loads automatically respond. If frequency goes up motors run faster so load goes up. When frequency goes up, all generators tend to speed up so their governors act to slow them down reducing their output. Both of these automatic actions have the effect of reducing the high frequency and getting the system headed back to 60 Hz. The opposite occurs when frequency goes below 60 Hz. These automatic responses to frequency are called primary frequency response. Sufficient primary frequency response is needed to keep the ERCOT system stable, especially when generators or loads trip off suddenly. WGRs are not synchronously connected to the transmission system. There is no automatic response to frequency unless it is created artificially. For some WGR turbine technologies, there is no way to create a response to frequency at all (except tripping them off line). As the installed capacity of WGRs grows above 15,000 MW there will be many hours when a substantial amount of the generation on line will be WGRs. At these times, it will be efficient for WGRs to provide a portion of the needed primary frequency response. If the WGRs do not provide the needed response, then WGRs may have their production curtailed to allow more conventional units to be on line or to increase their output in order to insure the response is available. A process has been completed to require all new WGRs to provide primary frequency response which culminated in the adoption of Protocol Revision Request 824. The newer technology WGRs can modify their control systems to provide what is expected to be excellent primary frequency response. On a going forward basis, the cost and commercial issues are quite manageable and no study is needed to justify the change in requirements. |  |
| --- | --- |
| Priority | High. |
| Considerations | Policy: No policy issue is raised on establishing a new requirement for new WGRs. An issue does arise if a new requirement is placed upon existing WGRs. What is the standard of need that must be demonstrated in order to require existing entities to install new software and/or equipment? |
|  | Reliability: Reliability could be an issue, but it is really an efficiency issue. ERCOT is expected to have sufficient conventional capacity available to allow it to curtail WGRs if needed to provide sufficient primary frequency response capability on the system. Such a process may provide the needed reliability, but at a huge cost to society. |
|  | Technical: For the newest WGR technologies primary frequency response capability can be provided for a very reasonable cost. For existing WGRs the answer ranges from no conversion capability, to impractical conversion capability, to difficult conversion capability, to conversion capability similar to new WGRs. |
|  | Market: A small capital cost increase for new WGRs and a range of possible capital costs for existing WGRs. On a relative basis the actual provision of the service could be much more costly than providing it from conventional generators, and the absolute cost of lost production is expected to be less than 1%. |
|  | Performance/Compliance: New performance standards and compliance metrics will be required. |
|  | Cost Allocation: None, the costs will be borne by the WGRs. |
| Strategy | Maximize WGR production by providing needed system reliability services from WGRs when possible and reasonable. Recommendation: Establish a new requirement for new WGRs to provide primary frequency response similar to conventional generator “governor response”. |
| Activities | ERCOT (E X): Participate in developing the new requirement and performance standards. |
|  | Market Participants (MP X): WGRs and all market participants assist in developing the new requirement and performance standards. Comply with the new standards as they are adopted. |
| Follow-Up | Monitor system performance and WGR performance to frequency deviations. |
| Schedule | December 2009 -Adopted Protocol revision 824 establishing new primary frequency response requirements for new WGRs Operating Guide revisions to establish performance requirements are in the approval process Protocol revision 833 establishing new primary frequency response requirements for existing WGRs is in the approval process. |

| SO-26 – Impact of Solar Generation on System Operations – Determine potential impact of new solar generation on ERCOT system operations and reliability through appropriate studies of solar ramp rate capabilities, forecasting of solar energy production, and voltage and reactive control capabilities of both solar photovoltaic and solar thermal technologies. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue does not involve policy considerations. |
|  | Reliability: This issue does involve reliability considerations because of the potential impact of significant additions of solar PV and solar thermal generating resources on ERCOT system reliability and operations. |
|  | Technical: This issue involves technical considerations of two very different types of solar technology (PV and solar thermal) and their capability to provide necessary reliability services, such as voltage and frequency control, reactive control, ramp rates, etc. |
|  | Market Design: This issue could impact market design considerations since solar generation resources might be able to participate in ERCOT ancillary services markets. |
|  | Performance/Compliance: This issue does include performance or compliance considerations because of the inherent differences between solar PV, solar thermal and conventional generating technologies. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Develop a whitepaper to examine the capabilities and technical issues applicable to solar PV and solar thermal technologies. |
| Activities | ERCOT (XX): Assist market participants in the preparation of a whitepaper examining the various solar technologies and their potential impacts on ERCOT operations and reliability. |
|  | Market Participants (MP XX): Through the work of the RTWG, prepare a whitepaper examining the various solar technologies associated and assess the capability of such technologies to improve or enhance integration of additional renewable generation without compromising operations flexibility and system reliability. |
| Follow-Up | None necessary |
| Schedule | A draft whitepaper should be available for review by the end of 2010. |

| SO-27 Manual Curtailment of Wind Generation to Resolve Local Congestion: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-28 SPS actuation for N-0 Conditions: A SPS is a Special Protection Scheme which is an automatic system designed to trip a generator off line when needed to protect the transmission system. If an SPS is actuated for an N-0 condition that means it is tripping the generator off even though there has been no transmission contingency. This can occur when a new generator is connected to a transmission system that can handle some of its output all of the time and all of its output only some of the time. Since line flows are determined by more than that generator’s output, a SPS is employed to take the generator off line when the total flow, which the generator is not allowed to know, is reaching the transmission lines limit. A problem arose with coordinating ERCOT operations directions to the generator with the generators actions to avoid being tripped. The SPS warning signal, before the trip, was being used by the generator to cut production to avoid the trip. All parties agreed that this was appropriate; however it was unclear whether a complete SPS investigation and report was needed when the warning signal activated but the SPS never tripped the unit. The investigation and reporting was a considerable burden on the Transmission Service Provider (TSP), ERCOT, and the Texas Reliability Entity (TRE). All parties agreed that the investigation and report were needed only if the SPS actually tripped the unit and the Operating Guides were modified to clarify the requirements. This issue affects WGRs almost exclusively since several WGRs have been connected to the transmission system ahead of the needed improvements. While this is normally a temporary situation, the design and construction of CREZ has become part of the solution for many of the WGRS. Other, timelier transmission upgrades are not being pursued since they would become redundant once CREZ construction is complete. This issue has been resolved through procedural changes. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Fundamentally, this issue is associated with compliance procedures. |
|  | Cost Allocation: None |
| Strategy | Recommendation: Insure that there are no reliability issues associated with the N-) SPS operating procedures and modify the Operating Guides to clarify requirements. |
| Activities | ERCOT (E X): Assist in review and resolution of the issue. |
|  | Market Participants (MP X): Generators, TRE, and TSPs assist in review and resolution of the issue. |
| Follow-Up | None needed |
| Schedule | September 2009 Operating Guide Revision Request 224 clarifying SPS reporting requirements was approved |

| SO-29 Transmission Outage Planning for CREZ: This is a specific issue under the broader issue of transmission outage planning (see SO-14). This issue has been raised due to the fact there will be many transmission outages needed to construct the CREZ lines. CREZ construction outages are unique because of number of outages needed and the number of different entities involved in the construction. The issue is further exacerbated by the short time frame to complete all of the construction. No outages will be taken until construction which will be after regulatory approvals and designs are completed. The CREZ build out has a deadline of 2013. The front end time required and the quick build out will concentrate the bulk of the outages into 2011 and 2013. The outages are further concentrated by the practice of scheduling transmission outages only in the spring and fall months. These are the very times when WGRs are able to produce the most power. Originally market participants sought to have ERCOT provide the market impact of outages to the Transmission Service Providers (TSPs) in order to allow them to evaluate the need for extraordinary mitigation. One particular project was selected for such review, but any further market impact evaluation was put on hold pending the resolution of the general issue (SO-14). ERCOT Planning staff has identified the likely outages needed and they are very numerous. The focus now is to coordinate the outages needed by the various parties doing the construction. Normal procedures allow the TSPs to start scheduling their outages no sooner than 90 days after the granting of regulatory approval since the outages will be somewhat dependent on the specifics of the route. There is no practical way to get better information sooner, thus ERCOT must await scheduling information from the TSPs to start any coordination of the schedules. Altering procedures and beginning a coordination process with less than perfect information may be needed to insure that transmission construction is not delayed due to limitations on outages. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: What is the burden of proof to allow extra ordinary mitigation costs to be recovered by the TSPs? |
|  | Reliability: Planned outage cannot be allowed to effect reliability; however the extent of needed outages may increase exposure to unplanned events. |
|  | Technical: There is no real technical issue, but new TSP preliminary engineering processes and a new outage planning process might provide for reasonable longer lead times for the outage scheduling process. |
|  | Market: The construction outages associated with CREZ will have a significant market impact. In fact the impact could be huge due to major curtailments ow wind-power production. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Given the tight schedule and the limitations on available outage information the focus needs to be on coordinating outages in order to avoid construction delays. Extra ordinary mitigation may be needed to simply maintain the construction schedule. There does not seem to be any practical way to “optimize” the outages to reduce market impacts. |
| Activities | ERCOT (E X): Insure that staff and systems are available to coordinate CREZ transmission outages as information from the TSPs becomes available. Explore techniques for anticipating possible outage needs to identify possible conflicts ahead of time. |
|  | Market Participants (MP X): TSPs consider providing a planning estimate of the outages needed. |
| Follow-Up | ERCOT and the TSPs, together with other market participants, need to move forward on developing a mechanism for evaluating market impacts of transmission outages (SO-14) |
| Schedule | This is an ongoing issue until the completion of the CREZ construction. |

| SO-30 Application of Wind Generator Forecasts to PASA: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-31 Tension Monitors on Transmission Lines: The rating of a transmission line, that is to say, the amount of current it can carry is very dependent upon the environmental conditions at the moment. Three major factors affect the current carrying capability: wind, ambient temperature, and sun. Many Transmission Service Providers (TSPs) vary their transmission line ratings used by ERCOT based upon temperature. Wind can have a much larger impact on line ratings than temperature. However, it is much more difficult to estimate line ratings for different wind conditions since the wind varies along the line due to hills and wind direction. One way to consider all the effects on the transmission line is to use real-time measurements on the condition of the line itself to determine how much current it can carry. Several vendors provide a way of measuring the tension on the line which is directly related to the cumulative effects of all environmental conditions along the length of the line and the current loading of the line. The vendor’s equipment then can provide the TSP with the instantaneous rating of the line. Two transmission lines in ERCOT are equipped with such devices. There is particular value for this technology when a WGR’s output is being limited by a nearby line. When the wind is strong enough for the WGR to increase its output it is very likely that the wind will also be cooling the nearby transmission line increasing its ability to handle the WGR’s increased output. The purpose of this initiative is to have ERCOT and the TSPs consider using the tension monitoring technology when economically justified. Current planning processes do not specifically evaluate this solution to curtailment issues. The tension monitor system can be expensive to install and maintain. The equipment is not a standard part of a TSP’s inventory thus requiring special training and procedures. However the potential value in reduced production costs may justify overcoming these obstacles. |  |
| --- | --- |
| Priority | Low unless you are the WGR being curtailed |
| Considerations | Policy: None |
|  | Reliability: The use of sophisticated specialized equipment can introduce additional complexity and uncertainty to system operations. |
|  | Technical: The technical solutions are available but increasing reliability of the devices and simplicity of operation may require additional development. |
|  | Market: This could have significant value to the market, especially the WGRs that are being curtailed due to nearby transmission constraints. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Identify WGRs that are being curtailed due to local transmission constraints and evaluate the possible value of using a tension monitor to increase the transmission line rating. |
| Activities | ERCOT (E X): Develop a screening process to identify possible candidates for use of tension monitors. Evaluate identified candidates. |
|  | Market Participants (MP X): TSPs install economically justified tension monitors. WGRs provide ERCOT with possible candidates for the use of tension monitors. |
| Follow-Up | Each 5-year plan should identify tension monitor candidates and evaluations |
| Schedule | 2010 - Develop and apply the screening process in this year’s 5-year planning process. |

| SO-32 Real Time Wind-powered Generation Capacity: At certain times it will be necessary to estimate the potential output capability of WGRs when they are being curtailed. Experience using an estimation process that possibly includes the effects of wind velocity, direction, losses, and wind-powered turbine production efficiencies could be useful in developing the final estimation process needed. Estimating WGR output from wind measurements is not strait forward. The results are dependent upon many different factors and the experience in the industry is limited and inconsistent. Requiring all WGRs to estimate their output when not curtailed using the same process as would be used when curtailed allows the process to be compared with actual meter readings when curtailed. The comparison process will allow the WGRs to evaluate alternative algorithms and data sources in order to provide the best estimate. The process to require all WGRs to supply real time production potential telemetry has been completed. The data sent to ERCOT has some immediate, limited operational value in the Zonal system but is not needed in the nodal system. This is essentially a process to gain experience with estimating techniques and has little value once the techniques are perfected. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Providing a reasonable estimate of WGR potential capability when the WGR is curtailed is needed to allow ERCOT to reschedule the WGR when it is no longer curtailed. |
|  | Technical: There are many issues about measurement processes, averaging times, and data sources that need to be explored. |
|  | Market: None |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Develop a protocol revision requiring WGRs to telemeter an estimate of production potential to ERCOT using a consistent averaging time for the data. |
| Activities | ERCOT (E X): Develop procedures and systems to capture the new data and analyze as needed. |
|  | Market Participants (MP X): WGRs develop systems needed to telemeter the new estimate of production potential to ERCOT. Compare the estimates with meter readings and experiment with alternative data sources, averaging times and algorithms to develop the best estimate. |
| Follow-Up | Share experience of WGRs in developing reasonable estimation methods. |
| Schedule | January 2010 Protocol revision 811 requiring estimated Real Time Production Potential to be telemetered to ERCOT was adopted. |

| SO-33 Real Time Wind-powered Turbine Availability: WGRs are composed of many, sometimes hundreds, of individual wind-powered turbines. At any given time some of the wind-powered turbines may be out of service on a planned or forced outage basis. The maximum output of the WGR is dependent upon the available wind and the number of wind-powered turbines currently in operation. In addition, the reactive control capability of the WGR is dependent upon the number of wind-powered turbines in service. This initiative is to provide ERCOT with real time information about the actual number of wind-powered turbines available for service, out of service, and whose status is uncertain. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Provides additional detail to improve modeling and thus will have some positive effect on reliability. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: New telemetry requirements will require additional compliance by WGRs with existing telemetry standards |
|  | Cost Allocation: None |
| Strategy | Recommendation: ERCOT develop needed protocol changes defining the new requirement. |
| Activities | ERCOT (E X): ERCOT develop needed protocol changes defining the new requirement. |
|  | Market Participants (MP X): WGRs comply with the new requirements. |
| Follow-Up | None |
| Schedule | November 2009 - Protocol Revision 830 establishing reactive standards and including wind-turbine availability telemetry requirements was adopted |

| SO-34 SCED Line Ratings: The Security Constrained Economic Dispatch (SCED) software determines the allowed output level of all generators in ERCOT respecting transmission line limits. The transmission line limits are provided by the Transmission Service Providers (TSPs) and in many cases are periodically modified based on expected temperatures. The temperatures used must be the highest temperature reasonably possible during the time period and for the region of the estimate. It is possible to provide actual temperatures in local geographic areas on a real-time basis. The use of the higher temperature estimate insures that the rating of the line will be conservative since a high temperature limits the current carrying capability of the line. If the more local real-time temperatures can be used to give SCED updated line ratings then it may be possible to increase the use of the transmission system reliably since a more realistic line rating will be used. Increased use of existing facilities is a benefit to all parties. Implementation in the new nodal software is possible but new procedures, monitoring systems, telemetry, and software will be needed. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: This can have a significant effect on the market allowing production costs to decrease significantly. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Get the most out of existing transmission assets. Recommendation: Establish procedures and systems to allow TSPs to update line ratings near to real time. |
| Activities | ERCOT (E X): After nodal go live, commit resources to evaluate the cost and the schedule to implement real time updating of transmission line ratings. |
|  | Market Participants (MP X): TSPs assist in specifying procedures and systems to allow real-time updating of transmission line ratings and provide ERCOT with the necessary information to implement the system. |
| Follow-Up | None |
| Schedule | After nodal go live and no later than July 2011 have the scope, schedule, and cost of updating line ratings near real time defined. |

4.3.	Market Design Issues

| MD-01 – Ancillary Services Cost Allocations Applicable to Wind: Some Market Participants believe that integration of large amounts of variable wind generation have increased ERCOT’s need for certain Ancillary Services. These parties believe that such increased costs should be allocated to the party responsible for the increased need for Ancillary Services. This issue will evaluate alternative methods of cost allocations for Ancillary Services for possible application to Wind Generation Resources. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue examines the potential change in the existing ERCOT policy of uplifting costs of Ancillary Services to all loads (based on load ratio share) to allocate costs of Ancillary Service costs to various Market Participants. |
|  | Reliability: This issue does not directly impact system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market Design: This issue does not include any market considerations. |
|  | Performance/Compliance: This issue does not involve any performance or compliance considerations. |
|  | Cost Allocation: Primary consideration of this issue. |
| Strategy | Recommendation XX: Develop one or more methodologies with supporting rationales for allocating the cost of Ancillary Services to Intermittent Renewable Resources, specifically, Wind Generation Resources (WGRs). |
| Activities | ERCOT XX: None |
|  | MP XX: The Wind Cost Allocation Task Force (WCATF) of the ERCOT Wholesale Markets Subcommittee (WMS) was created in November 2009 to examine this issue and develop a cost allocation methodology with supporting rationale. The WCATF is meeting monthly in 2010. |
| Follow-Up | Awaiting final report from the WCATF. |
| Schedule | WCATF is to complete their work by _____, 2010. |

| MD-02 – Ancillary Services Procurement Optimization for 2009 – Annually, ERCOT produces its plan for procuring Ancillary Services for the coming calendar year. With the increasing influx of variable wind generation, the amounts and types of Ancillary Services needed to maintain system reliability may change. This issue examines potential impact of wind generation on ERCOT’s plan for Ancillary Service procurements for 2009. |  |
| --- | --- |
| Priority | Complete |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: The amounts and types of Ancillary Services procured by ERCOT do impact system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. |
|  | Performance/Compliance: This issue does not directly involve any performance or compliance considerations. |
|  | Cost Allocation: Whether or not to change Ancillary Cost allocations is a consideration of this issue. |
| Strategy | Recommendation XX: The Wind Operations Task Force (WOTF) of the ERCOT Reliability and Operations Subcommittee (ROS) reviewed ERCOT’s proposed Ancillary Services Procurement Plan for 2009 to ensure that it maintains adequate reliability while ensuring optimum market participation. |
| Activities | ERCOT XX: Prepare 2009 proposed Ancillary Service Procurement Plan |
|  | MP XX: WOTF reviewed ERCOT’s proposed 2009 Ancillary Services Procurement plan and made recommendation to ROS. |
| Follow-Up | None. |
| Schedule | WOTF completed its review of the proposed 2009 Ancillary Services Procurement Plan in December of 2008 and was approved by ROS, TAC and the ERCOT Board of Directors in February, 2009. |

| MD-03 – Non-Spin Requirements: Determine if additional amounts of Non-Spin Service procurements by ERCOT are necessary to reliably accommodate increased amounts of wind generation in ERCOT. Historical events indicate that there is increased risk to reliability due to the variable output of wind generation and the difficulties in predicting when such variations will occur. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by ensuring that adequate amounts of Non-Spin Service are procured by ERCOT to deal with increased risk from variable output wind generation. |
|  | Technical: This issue does involve some technical issues related to revisions of the Non-Spin Service procurement methodology |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does impact performance or compliance. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Examine methods to ensure that adequate Non-Spin capacity is available to ERCOT from the market to deal with increasing amounts of variable wind generation. |
| Activities | ERCOT (XX): Analyze and recommend revisions to the Ancillary Service Procurement methodology, specifically focusing on Non-Spin Service procurements to address concerns about increased amounts of variable wind generation entering the ERCOT market. |
|  | Market Participants (MP XX): Review and provide guidance to ERCOT on its analysis of Ancillary Service procurements. |
| Follow-Up | Periodically review historical Non-Spin Service procurements and deployments to ensure that reliability is maintained at the lowest possible cost to the market. |
| Schedule | ISSUE COMPLETE: In December, 2009, the ERCOT Board approved the proposed 2010 Ancillary Services Procurement methodology which was revised from the previous year’s methodology to specifically increase Non-Spin Service procurements to deal with the increased risk posed by increasing amounts of variable wind generation in the ERCOT market. |

| MD-04 New Ancillary Services Products for Reliability: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| MD-05 – Benefits of Storage Technologies – Storage technologies are either economically competitive or on the verge of being economically competitive. The infusion of funding under the ARRA will increase the range of technologies that can be applied to improving grid stability and reliability at both the transmission and distribution level, and aid in the integration of renewable resources. |  |
| --- | --- |
| Priority |  |
| Considerations | Policy: Optimal utilization of storage technologies may require modifying ancillary services requirements, interconnection rules, and the rules governing the modeling and settlement of energy injections and withdrawals due to special characteristics of storage devices which are inherently different in many respects to conventional generation technologies. |
|  | Reliability: Storage has the potential to increase reliability due to rapid and highly controllable response to dispatch instructions. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. Some storage technologies may raise special issues due to their ability to provide reliability services, increase transmission capacity as well as engage in arbitrage in energy markets. |
|  | Performance/Compliance: The definition and treatment of storage technologies may raise performance considerations. Rules developed for conventional generation implicitly assume certain tradeoffs between energy duration and ramp rates that may not apply to storage. |
|  | Cost Allocation: There may be an issue with UFE, but this should have a de minimus impact on market participants. |
| Strategy | Recommendation X_: Develop nodal protocols, based on experience in other ISOs, to integrate storage devices into ERCOT in a manner that maximizes the value they can provide at a minimum cost. |
| Activities | ERCOT (E X): Storage workshop is the first step in identifying the barriers to integration of storage into the ERCOT market. |
|  | Market Participants (MP X): Storage is a priority item for both TAC and WMS for 2010. |
| Follow-Up |  |
| Schedule |  |
| Status | Complete |

| MD-06 – Ancillary Services Procurement Methodology – Determine impact and possible changes in amounts of ancillary services to be procured by ERCOT on a daily and hourly basis to ensure reliability with increasing amounts of wind generation planned to be installed in the ERCOT market within the next few years. |  |
| --- | --- |
| Priority | Complete |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: The amounts and types of Ancillary Services procured by ERCOT do impact system reliability. The variable and relatively unpredictability of wind generation output will likely require ERCOT to procure additional amounts of Ancillary Services to maintain adequate system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. |
|  | Performance/Compliance: This issue does not directly involve any performance or compliance considerations. |
|  | Cost Allocation: Whether or not to change Ancillary Cost allocations is a consideration of this issue. |
| Strategy | Recommendation XX: The Wind Operations Task Force (WOTF) of the ERCOT Reliability and Operations Subcommittee (ROS) reviewed ERCOT’s proposed Ancillary Services Procurement methodology and made comments to revise the procedure to reflect anticipated growth in the amount of wind generation on the system to ensure that the proper amount of Ancillary Services are procured to ensure adequate reliability with reasonable market participation. |
| Activities | ERCOT XX: Revised Ancillary Service Procurement methodology to incorporate WOTF recommendations approved by ROS. |
|  | MP XX: WOTF reviewed ERCOT’s Ancillary Services Procurement methodology and made recommendations for changes to address increased wind generation penetration in ERCOT. |
| Follow-Up | None. |
| Schedule | WOTF completed its review of the proposed Ancillary Services Procurement methodology in December, 2008 with recommended changes in the ERCOT procurement methodology, which was approved by ROS in January, 2009. |

| MD-07 Wind-powered Generation Resources Providing Ancillary Services: As more WGRs are added to the ERCOT system it may become useful for WGRs to provide certain ancillary services. If WGRs can provide needed services it may relieve ERCOT of the need to schedule conventional generators on line just to provide the needed services. The situation that seems likely to occur is high wind-power production during low load times in the spring. If there is sufficient wind powered production to lower conventional resources output near their Low Sustained Limit (LSL) then the ability of the conventional resources to provide down regulation may be limited. An Ancillary Services study performed by General Electric identified issues that need further study. At this time the additional studies have not been started. The high wind-power output and low load operation may call for wind-generation to be curtailed, then market prices will be very low, even negative (generators pay to produce power). Deployment of ancillary services is less costly to generators operating neat the market price. If market prices go negative (WGRs on the margin) then conventional generators are operating far from the market price and WGRs are operating near the market price. The latest technology WGRs have the technical capability to provide regulation services when there is enough wind. This issue was raised to begin exploring the most efficient way to operate when WGR capacity is above 15,000 MW and load levels are low and WGR output is high. When wind velocity is high modern WGRs are at their best in quickly and accurately controlling their output. There is every expectation that WGRs will be able to respond very effectively to ancillary service deployment orders in these conditions. The following issues need to be explored: - How will conventional generators deal with the risk of prices going negative when offering to supply ancillary services? Negative prices require the generator to pay for each MWH produced. There are three components to the production from a generator. First there is the minimum loading (LSL) required for the generator even to be available to provide ancillary services. In a negative price environment conventional generator minimum running cost can be quite high. Next there is any need to reserve capability to provide the service. For Reg Down, the generator must be above its LSL by the amount it has promised to sell to ERCOT unless ERCOT deploys the service. Producing the extra energy above LSL will be very costly for a conventional generator when market prices are negative. Lastly, there will be energy produced by the generator when reg up is deployed; again costing the conventional generator a lot to produce its power when the market is negative. - What mechanisms exist or need to be added to the current nodal market design to allow WGRs and conventional generators to coordinate their provision of ancillary services? Coordinated operations could reduce the market risk for conventional generators and increase production for WGRs. - To what extent would provision of ancillary services by WGRs reduce the need for ERCOT to commit conventional generators? - What if any changes are needed to the nodal protocols to allow WGRs to provide ancillary services and to maximize the value of WGRs to the ERCOT system? - What if any changes are needed in WGR operating procedures or capabilities to provide ancillary services to ERCOT? |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: Proper procedures need to be put in place to insure that reliability is maintained. |
|  | Technical: None, modern WGRs can provide excellent services if wind conditions are right. |
|  | Market: There could be significant improvement in efficiency if WGRs are integrated into the overall provision of ancillary services. |
|  | Performance/Compliance: There may be new performance measures needed to insure that WGRs are providing the needed service. |
|  | Cost Allocation: None |
| Strategy | Anticipate issues to provide sufficient time to analyze, resolve, and implement as needed. Recommendation: Start a process of reviewing and discussing the mechanisms for WGRs to provide ancillary services. |
| Activities | ERCOT (E X): Develop tools to evaluate the mechanisms to deal with low load and high wind scenarios. Perform studies of alternatives to evaluate the most effective and economical way to reliably operate during low load situations (see SO-05) |
|  | Market Participants (MP X): WGRs assist in evaluating system operations alternatives. Make any needed modifications deemed commercially expedient to participate in providing ancillary services. |
| Follow-Up | May need protocol revisions depending on the results of the analysis |
| Schedule | This is primarily a market issue that will likely be important when more than 15,000 MW of WGR capacity is on the system. Discussion of the issue needs to be started soon and implementation will most likely be beneficial by 2013. |

| MD-08 – Reactive and Voltage Requirements Applicable to Wind: Review current ERCOT Protocols and Operating Guides to ensure reactive and voltage control requirements specified therein are applicable to all generating technologies, including wind generation. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue involves the policy of ensuring that each type of generating technology provides the proper amount of reactive and voltage control capability to ensure adequate reliability of the ERCOT system. |
|  | Reliability: This issue will ensure adequate ERCOT reliability by requiring all types of generating technologies, including wind turbines, to provide the appropriate amount of reactive and voltage control capability. |
|  | Technical: This issue involves some technical issues related to the specific technical capability of a unconventional generation technology (e.g., wind turbine) to provide reactive and voltage control capability similar to that of conventional generation. |
|  | Market Design: This issue may impact market design if it is determined that a unconventional generation technology is allowed to purchase reactive or voltage control capability from a third-party provider through an ERCOT market. |
|  | Performance/Compliance: This issue does impact performance or compliance of any generating technology. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Examine ERCOT Protocols and Operating Guides to determine if reactive and voltage control requirements are clearly applicable to all generating technologies. |
| Activities | ERCOT (XX): Review and comment on any proposed changes in existing ERCOT Protocols or Operating Guides related to reactive and voltage control capability of generation resources. |
|  | Market Participants (MP XX): Review existing ERCOT Protocols and Operating Guides and recommend changes, if necessary, to ensure that all generating technologies are required to provide proper reactive and voltage control capability either directly or via a market solution. |
| Follow-Up | None at this time. |
| Schedule | ISSUE COMPLETE: PRR 830 "Reactive Power Capability Requirement" was approved by the ERCOT Board in November, 2009. However, this PRR has been appealed to the Public Utility Commission of Texas in Docket Nos. 37817, 37818, 37819, 37823, 37824and 37827, so it is not clear if this issue is really complete. |

| MD-09 Wind Generation Dispatch in the Nodal Protocols: The current nodal protocols call for WGRs to follow ERCOT Base Point instructions when the Security Constrained Economic Dispatch (SCED) calculation indicate they must be curtailed below their High Sustained Limit (HSL)to maintain system reliability. The trigger to indicate that the WGR must curtail its output is when the Base Point it receives from SCED is more than 2 MW below the HSL used by SCED. The HSL for a WGR is dependent upon wind conditions and is thus changing routinely. The current nodal protocols call for WGRs to routinely update their HSL by real-time telemetry to ERCOT. It became apparent that it was not possible for the WGR to know which HSL update to use. One solution is to have SCED send out a curtailment flag to signal to the WGR when it must curtail. While this is judged to be the best resolution for the issue it would require software changes and would not be available until after nodal go live. In the interim, a change in the WGR telemetry procedure has been developed to insure that the WGR and SCED are using the same HSL for their trigger. This requires a temporary software change in all of the WGRs control centers. The process requiring all WGRs to modify their software is in progress. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This modified procedure maintains the synchronization between SCED and the WGRs in order to maintain reliable operations. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Clarifies the performance requirement for the WGR. |
|  | Cost Allocation: None |
| Strategy | Recommendation: Develop a nodal protocol revision to temporarily resolve the issue by changing the WGR HSL telemetry procedure. Develop an additional nodal protocol revision, to be implemented after go live, for SCED to send a curtailment flag when needed; coordinate with other WGR related nodal revisions requiring software changes (MD-10, MD-11). |
| Activities | ERCOT (E X): Assist in analyzing and resolving the issue. Implement the needed changes. |
|  | Market Participants (MP X): WGRs implement the temporary fix in their software and procedures. Assist in analyzing and resolving the issue. |
| Follow-Up | None |
| Schedule | Nodal Protocol Revision Request 214 specifying a revised WGR HSL update process is in the approval process. By July 2010 Submit a nodal protocol revision request requiring a change in the nodal software creating a curtailment flag when needed by SCED (coordinate with MD-10 and MD-11) |

| MD-10 – Wind Generation Performance Metrics in the Nodal Protocols – This issue relates to a review of the ERCOT Nodal Protocols to ensure proper treatment of wind generation in regard to performance metrics. Wind turbine generators are different from conventional generation in many ways. Because of these differences, it may be appropriate to develop special performance metrics for wind turbine generators that recognize the technological capability (or lack thereof) inherent to wind turbine generation. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue includes policy considerations on whether or not to impose the same performance standards and metrics on wind turbine technologies which are inherently different in many respects to conventional generation technologies. |
|  | Reliability: Proper operation of wind generation resources can impact system reliability. Measurement of performance of wind generation, like that of conventional generation, is necessary to ensure adequate system reliability. |
|  | Technical: There are some technical considerations related to how wind turbines can or cannot respond to system disturbances. |
|  | Market: This issue does not include any market considerations. |
|  | Performance/Compliance: This issue directly involves performance and compliance considerations. |
|  | Cost Allocation: This issue does not include any cost allocation considerations. |
| Strategy | Recommendation X_: Review the ERCOT Nodal Protocols to determine what performance measures and metrics currently apply to wind turbines and make recommendations for any changes to better measure wind turbine generation operations and responses during reliability events. |
| Activities | ERCOT (E X): Provide operational and performance data for wind turbines for evaluation of various performance metrics applicable to wind turbine generation. |
|  | Market Participants (MP X): This issue was assigned to the ERCOT Wholesale Market Subcommittee (WMS), which in turn, assigned the issue to its QSE Managers Working Group (QMWG), which is currently reviewing the performance metrics applicable to wind generation in the existing ERCOT Nodal Protocols. Upon completion of this review, the QMWG may make recommendations to the WMS for changes in the Nodal Protocols to recognize any inherent technological differences between wind turbine generators and conventional generators in regard to generator performance metrics. |
| Follow-Up | None at this time. |
| Schedule | The QMWG will complete its review of the Nodal Protocols and provide any recommendations to ROS by _______, 2010. |

| MD-11 Wind-powered Generation and Base Point Deviation in the Nodal Protocols: The nodal protocols specify that WGRs shall be held accountable for deviations from their base point when the Security Constrained Economic Dispatch (SCED) calculations must curtail them below the High Sustained Limit (HSL) used by SCED. The need to curtail is signaled by the fact that the base point received by the WGR is 2 MW or more below the HSL sent to ERCOT by the WGR. Insuring that the HSL used by the WGR and that used by SCED is the subject of issue MD-09. This issue has resulted from the fact that the settlement equations use the HSL from the current operating plan and not the HSL used by SCED to trigger base point settlement charge calculations. The settlement trigger needs to be changed to use the HSL used by SCED. Since a software change is required to fix this issue, resolution will have to wait for nodal revisions implemented after go live. The possible effect of this error is inappropriate charges to WGRs that must be resolved by a routine dispute process. Dispute processes for settlement issues may be considered routine, but they do take up market participant and ERCOT staff time. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: Can expose WGRs to higher costs if not resolved. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Prepare a nodal revision request fixing this and other WGR related issues requiring a software change (see MD-09, MD-10) |
| Activities | ERCOT (E X): Assist with analyzing and resolving the issue. Implement needed changes. |
|  | Market Participants (MP X): WGRs assist with analyzing and resolving the issue. |
| Follow-Up | None |
| Schedule | Initiate the nodal revision request by July 2010. |

| MD-12 – Wind Generation Resource LSL as a Percentage of HSL – Determine the appropriate minimum percentage for the Low Sustained Limit (LSL) of the High Sustained Limit (HSL) for a wind generation resource and incorporate those values in the ERCOT Protocols. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not involve policy. |
|  | Reliability: This issue does not directly involve reliability. |
|  | Technical: This issue involves the technical feasibility of a wind generation facility to determine the appropriate minimum and maximum level of generation capability. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does impact performance or compliance of any generating technology to meet its LSL and HSL. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Determine the appropriate levels of LSL and HSL for wind generation facilities. |
| Activities | ERCOT (XX): Review and comment on any proposed changes in existing ERCOT Protocols or Operating Guides related to LSL and HSL for wind generation resources. |
|  | Market Participants (MP XX): Review existing ERCOT Protocols and Operating Guides and recommend the appropriate LSL and HSL standards for wind generation facilities. |
| Follow-Up | None necessary since the performance metric associated with the percentage of LSL to HSL will cease to exist when the ERCOT Nodal Market is implemented in December, 2010. |
| Schedule | ISSUE COMPLETE: PRR 773 "Setting the LSL Requirement for WGRs " was approved by the ERCOT Board in December, 2008. This PRR sets the LSL as a percentage of HSL at 10% for all wind generators installed on or after January 1, 2003. Wind generators installed prior to that date are excluded from the measure. |

| MD-13 – Use of State-of-the-Art Wind Forecast – An accurate wind power generation forecast is essential to the reliable and efficient integration of wind generation into the ERCOT grid. Currently, there are several third-parties who have developed and sold wind power forecasting services. With the large influx of new wind generation resources into the ERCOT grid, it is important for ERCOT to be able to accurately forecast wind energy production on a day-ahead up to an hour-ahead timeframe to reliably and efficiently dispatch its resources to serve load. However, state-of-the-art forecasts require significant amounts of meteorological (site-specific and region-wide) and operating data (i.e., wind turbine availability) in order to accurately forecast energy production from wind generators. Such data is only available from Wind Generation Resource (WGR) owners. |  |
| --- | --- |
| Priority | Complete |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: Proper forecasting of wind generation output can impact system reliability. This new requirement will allow ERCOT to perform its Day Ahead Replacement Reserve Service (RPRS) procurement using a consistent state-of-the-art forecast of the output from WGRs rather than relying on forecasts from varying sources (i.e., individual wind farms) with varying degrees of sophistication and accuracy. |
|  | Technical: There are some technical considerations related to the inputs necessary to populate the data required for a state-of-the art wind power production forecast. |
|  | Market: This issue does not include any market considerations. |
|  | Performance/Compliance: This issue directly involves compliance considerations. |
|  | Cost Allocation: This issue does not include any cost allocation considerations. |
| Strategy | Recommendation: Establish a requirement in the ERCOT Protocols for a Qualified Scheduling Entity (QSE) representing Wind Generation Resources (WGRs) to use a state-of-the-art wind production forecast provided by ERCOT in their daily resource plan submittals. |
| Activities | ERCOT (E X): Develop a state-of-the-art wind power production forecast through collaboration with a recognized forecast provider. File a Protocol Revision Request (PRR) to establish data reporting requirements for QSEs representing WGRs to populate the state-of-the-art wind forecast model. |
|  | Market Participants (MP X): Establish processes to collect and transmit required meteorological data to ERCOT to feed into the state-of-the-art wind power production forecast. |
| Follow-Up | None at this time. |
| Schedule | Protocol Revision Request 763 - Use of WGRPP as Planned Operating Level in Day-Ahead Resource Plan for WGRs was submitted by ERCOT staff in May of 2008 and approved by the ERCOT Board of Directors in July of 2008. |

4.4.	Workshop and/or Training Issues

| WT-01 – Resource Plan and Schedule Update Process: Determine potential improvements to the existing Resource Plan and Resource Schedule update process to improve performance and reliability. Because of the pending implementation of the Nodal market design, this issue should be addressed after the Nodal Market implementation as a topic for a future workshop. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by providing ERCOT with more timely and accurate information regarding the status and operation of wind generation resources. |
|  | Technical: This issue does involve some technical issues related to implementation within the Nodal market design as planned. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does impact performance or compliance. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Solicit input and ideas from Market Participants and ERCOT staff through a workshop. |
| Activities | ERCOT (XX): Host a workshop dealing with potential improvements to the scheduling of both conventional and variable renewable resources that could be implemented into the Nodal market design after initial Go-Live (i.e., after December, 2010) |
|  | Market Participants (MP XX): Provide speakers and/or suggested improvements for discussion at the workshop. |
| Follow-Up | None at this time. |
| Schedule | Hold workshop after Nodal Go-Live (2011 or beyond). |

| WT-02 – Wind Workshop III (Summer 2009): Develop list of topics and speakers for the ERCOT Wind Workshop III to be held in the summer of 2009. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by providing ERCOT with better tools to address issues being experienced as the penetration of variable wind generation on the ERCOT system continues to increase. |
|  | Technical: This issue does involve some technical issues related to various types of wind turbine designs. |
|  | Market Design: This issue could result in development of new market-based tools to help ERCOT deal with increased penetration of variable wind generation. |
|  | Performance/Compliance: Any tools developed as a result of this issue could impact performance or compliance. |
|  | Cost Allocation: This issue could impact cost allocation if certain costs are incurred due to increased penetration of variable wind generation |
| Strategy | Make the market participants aware of issues that ERCOT has experienced as variable wind generation penetration has increased to stimulate new ideas and methods of reliably integrating such resources into the ERCOT system. |
| Activities | ERCOT (XX): Host a workshop for interested parties to discuss methods of improving system operations and reliability in an environment of ever-increasing use of variable wind generation resources. |
|  | Market Participants (MP XX): Provide speakers and/or suggested improvements for discussion at the workshop. |
| Follow-Up | None at this time. |
| Schedule | ISSUE COMPLETE: The workshop was held on June 29, 2009 and was well-attended. |

| WT-03 Wind Turbine Operator Training: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-04 Wind in the Nodal Market: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-05 Wind Workshop IV: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-06 Storage Workshop I: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-07 Energy Storage Workshop I: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

5.	2010-2011 RTWG Work Plan

The RTWG Work Plan for 2010-2011 is guided by its charter and goals as approved by TAC.  The work plan describes the activities and work product planned for the period through the first year of nodal market operations.

5.1.	RTWG Charter

The RTWG Charter was approved by TAC on Nov. 6, 2008.

The ERCOT Technical Advisory Committee creates the Renewable Technologies Work Group to coordinate and track stakeholder efforts to capture the benefits and address the challenges associated with the introduction of renewable energy generating technologies interconnected to the ERCOT grid.

Created as a Work Group, rather than a Subcommittee, the RTWG does not have a formal voting structure, but rather strives to achieve consensus on the issues raised during the conduct of its duties.  Where applicable, the RTWG will report the consensus, majority, and / or minority views of participants on each issue.

The Chair and Vice Chair of the RTWG will be appointed by the TAC Chair and confirmed by the TAC.  The RTWG shall meet not less than quarterly and shall continue in the conduct of its duties until such time as TAC decides to dissolve the work group.

The RTWG is charged with the following duties:

- Identify issues related to renewable energy generation on the ERCOT system – either benefits not realized or challenges which need to be addressed.  This activity does not preclude WMS or ROS from identifying and resolving wind integration issues within their traditional purview.

- Define, frame, and prioritize the identified issues for resolution

- Refer issues to the appropriate TAC subcommittees for further development and resolution

- Gather input as provided from TAC subcommittees and RTWG activities and develop recommendations and / or frame issues for resolution by TAC

- Provide monthly status reports to TAC

- Maintain an issues tracking system

- Organize and host technical workshops as needed to ensure ERCOT Staff and market participants stay abreast of new technologies deployed on the ERCOT system, emerging technologies offering solutions to renewable generation technology challenges, and industry best practices

- Organize training seminars as needed to ensure ERCOT Staff and affected market participants effectively coordinate practices and procedures adopted to reliably integrate renewable generation technologies into the ERCOT grid

- Draft quarterly reports to TAC to support the ERCOT process to provide quarterly reports to the PUCT regarding reliability and grid integration issues related to renewable resources

5.2.	RTWG Goals

Text.

Goals.

5.3.	RTWG Activities

Regular Meetings

Workshops

Liaisons

Reports

Phase One Activities

Completed Phase One Activities

Summary Table of Major Phase One Activities

-PRRs

-NPRRs

-OGRRs

-NOGRRs

-Process/Procedure Changes

-Issues Not To Be Addressed

-Open Phase One Activities

--PRR 833

--Wind Workshop IV

Phase Two Activities

Solar Workshop I

Storage Workshop I

Wind Workshop V

Storage White Paper

Wind Ramp Event Simulation Tool

Phase Three Activities

No Phase Three Activities are yet defined or scheduled.

5.4.	RTWG Work Product

Text.

Regular Meetings, Workshops, Issues Communication, Issues Tracking, Work Product

Issues Communication

To ensure transparency and broad communication of all renewable technologies integration issues with market participants and policymakers, the following activities are performed on a regular basis:

- Designated RTWG member reports relevant RTWG activities to the WMS and ROS monthly;

- Designated RTWG member reports relevant WMS and ROS activities to the RTWG monthly;

- The RTWG Chair (or designate) reports RTWG activities to TAC monthly;

- The TAC Chair (or designate) reports on the TRIP to the ERCOT Board of Directors and to the PUCT quarterly; and

- The current version of the RTWG issues list is available in the public  area of the ERCOT web site.

The RTWG in coordination with ERCOT staff, will facilitate periodic workshops and training seminars on renewable technology issues for industry stakeholders and interested parties.

6.	Summary Tables

6.1.	Summary Table of TRIP Goals

| Goal 01 | Identify and communicate issues of interest related to the integration of renewable resources to market participants and industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| --- | --- | --- |
| Goal 02 | Develop strategies to resolve identified issues. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 03 | Communicate the long-term plan for ERCOT activities related to renewable technologies integration to market participants and industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 04 | Communicate progress on renewable technologies integration and raise issues for resolution to Texas policy makers and ERCOT ISO decision makers. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 05 | Document the renewable technologies integration activities within the ERCOT Region as a resource for electric power industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 06 | Document “lessons learned” through the ERCOT renewable technologies integration effort to preserve institutional memory and better inform ongoing integration activities. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 07 | Remain informed of federal policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 20 |
| Goal 08 | Guide and track stakeholder efforts to facilitate implementation of and adaptation to the PUCT’s CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 09 | Ensure the ERCOT planning function addresses the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 10 | Ensure the ERCOT operations function is prepared for the operating conditions resulting from the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 11 | Remain informed of state policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 23 |
| Goal 12 | Identify and capture the economic benefits and reliability enhancements offered by renewable generation technologies and related applications and practices while maintaining ERCOT system reliability. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 24 |
| Goal 13 | Improve the quality of data and accuracy of models used to support the ERCOT system planning function. Supported by Recommendations 02, XX, XX, XX, and XX. | p. 25 |
| Goal 14 | Assess ERCOT system planning capabilities in light of activities required to effectively plan for further integration of renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 26 |
| Goal 15 | Ensure particular attention is paid to ramping events, including taking steps to mitigate ramp event impacts, improve ramp event forecasting and pre-event system posturing, and devising more effective and/or efficient use of market and operational tools during ramp events. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 28 |
| Goal 16 | Identify and address current and anticipated challenges to the maintenance of system frequency control. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 28 |
| Goal 17 | Develop a near-term process by which the range of issues associated with the kinds of ancillary services available to the ERCOT market and the procurement methodologies for those services are evaluated and, if necessary, adjusted to facilitate the integration of renewable generation technologies. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 29 |
| Goal 18 | Assess voltage control requirements, capabilities, and areas of possible clarification or improvement in current procedures and technical standards. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 30 |
| Goal 19 | Evaluate renewable generation forecasting practices and outcomes. Identify areas of possible improvement and develop solutions. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 31 |
| Goal 20 | Assess ERCOT operations capabilities in light of activities required to effectively integrate renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Where operational capabilities are improved, ensure adequate training is performed to maximize benefits. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 31 |
| Goal 21 | Improve and maintain stakeholder technical understanding of the capabilities and limitations of relevant emerging and evolving grid-connected technologies; their potential benefits and challenges for the system planning and operations functions; and facilitate collaborative stakeholder communications to solve technical integration issues. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 32 |
| Goal 22 | Strike an appropriate balance which maintains an open access paradigm allowing and encouraging introduction and integration of benficial technological advances while maintaining interconnection, registration, planning, and operating criteria which protect system security. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 23 | As renewable generation and related technologies mature and enhanced capabilities become available, ensure technical standards are periodically evaluated to ensure best available technologies and practices are utilized where necessary and cost-effective. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 24 | Contribute to ERCOT’s development of longer-term system planning studies which include reasonable assumptions regarding the installation and capabilities of emerging renewable generation and related technologies. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 25 | Focus on near-term refinement and development of tools providing enhanced operational capabilities for ERCOT management of wind-related issues. In the longer term, evaluate potential tools needed to integrate other renewable technologies as operational issues are identified. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 34 |
| Goal 26 | Identify renewable technologies integration market design questions and impacts on market outcomes. Facilitate issues framing for resolution, if desired, by the appropriate stakeholder or policy making body. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 36 |
| Goal 27 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 28 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 29 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 30 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |

6.2.	Summary Table of TRIP Recommendations

| Recommendation 01 | For system planning purposes and operational readiness activities, ERCOT should assume full implementation of the PUCT CREZ Plan by Dec. 31, 2013. Studies and preparations should assume at least 19,000 MW of installed wind generation capacity. Supports Goals Nos. 08, 09, 10. | p. 23 |
| --- | --- | --- |
| Recommendation 02 | As integration issues are examined, data and model quality should be considered and, where possible, improved. ERCOT and stakeholders should collaborate in specific activities to improve ERCOT’s access to quality technical data related to renewable generation technologies. Supports Goals Nos. 13, XX, XX, and XX. | p. 25 |
| Recommendation 03 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system planning resources to keep pace with rapidly evolving grid-connected technologies. Supports Goals Nos. 14, XX, XX, and XX. | p. 27 |
| Recommendation 04 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system operations resources, including operator training opportunities, to keep pace with rapidly evolving grid-connected emerging technologies. Supports Goals Nos. XX, XX, XX, and XX. | p. 31 |
| Recommendation 05 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 06 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 07 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 08 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 09 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 10 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 11 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 12 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 13 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 14 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 15 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 16 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 17 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 18 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 19 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 20 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 21 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 22 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 23 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 24 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 25 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 26 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 27 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 28 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 29 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 30 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 31 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |

6.3.	Summary Table of Recommended ERCOT TRIP Activities

| ERCOT 01 | Activity description. Schedule. | p. XX |
| --- | --- | --- |
| ERCOT 02 | Activity description. Schedule. | p. XX |
| ERCOT 03 | Activity description. Schedule. | p. XX |
| ERCOT 04 | Activity description. Schedule. | p. XX |
| ERCOT 05 | Activity description. Schedule. | p. XX |
| ERCOT 06 | Activity description. Schedule. | p. XX |
| ERCOT 07 | Activity description. Schedule. | p. XX |
| ERCOT 08 | Activity description. Schedule. | p. XX |
| ERCOT 09 | Activity description. Schedule. | p. XX |
| ERCOT 10 | Activity description. Schedule. | p. XX |

6.4.	Summary Table of Recommended Market Participant TRIP Activities

| MP 01 | Activity description. Schedule. | p. XX |
| --- | --- | --- |
| MP 02 | Activity description. Schedule. | p. XX |
| MP 03 | Activity description. Schedule. | p. XX |
| MP 04 | Activity description. Schedule. | p. XX |
| MP 05 | Activity description. Schedule. | p. XX |
| MP 06 | Activity description. Schedule. | p. XX |
| MP 07 | Activity description. Schedule. | p. XX |
| MP 08 | Activity description. Schedule. | p. XX |
| MP 09 | Activity description. Schedule. | p. XX |
| MP 10 | Activity description. Schedule. | p. XX |

6.5.	Summary Schedule of Major TRIP Activities 2010-2012

| Date | Wind Workshop IV | reference |
| --- | --- | --- |
| Date | Solar Workshop I | reference |
| Date | Storage Workshop I | reference |
| Date | ERCOT Operations Training | reference |
| Date | Wind Workshop V | reference |
| Date | Activity | reference |
| Date | Activity | reference |

6.5.	Summary TRIP Schedule

7.	 Appendices

7.1.	March 2010 RTWG Issues List

7.2.	2009 RTWG White Papers

7.3.	2008-2009 Wind Workshop Presentations

7.4	2009 Presentations Made to the RTWG

8.	References

The presentations made at WInd Workshop I are located in Section 7.2.1.

cite 33672 final order paragraph No. XX

cite PUCT project where quarterly reports are filed

cite

cite

cite ERCOT CO2 study May 2009

cite SB7, 75R

cite SB20, 78 first or second called

cite 33672

cite

cite

PURA 39.XXX, etc.

brief recitation of criteria and cite NERC standards.

defined ancillary services in the zonal market may be found in Protocols Sec. X.X-X.XX and link to doc. defined ancillary services in the nodal market may be found in Nodal Protocols Sec. X.X-X.XX and link to doc.

cite GE study and point to ancillary services discussion, impacts, recommendations.

brief summary of 2008 and 2009 methodology changes and links to methodology documents

cite url