| SP-03 Wind Turbine Fault Tolerance: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. WGRs had been given specific exemption from fault tolerance requirements. As more WGRs were added to the ERCOT system, it became necessary to evaluate existing WGR fault tolerance capabilities as well as to establish fault tolerance standards for new WGRs. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Yes; the policy issue that became evident was to determine the standard of need that must be demonstrated in order to require existing WGRs to meet any new requirements that could be very expensive. |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. However, existing WGRs may not be easily modified to meet new fault tolerance requirements and there may be a significant technical challenge to determining their actual requirement and then meeting it. In most cases, new WGRs can meet fault tolerance requirement by buying certain options in the wind-powered turbines. In most cases, those options cannot be retrofit onto existing wind-powered turbines; thus, the actual ability to meet new requirements may provide a significant technical challenge. |
|  | Market: New requirements would cause certain wind-powered turbines to no longer be able to be supplied for WGRs in ERCOT. The provision of fault tolerance for new WGRs from other wind-power turbine suppliers will increase WGR capital costs. There will not typically be any significant change in operating costs for new WGRs. There is little expected change in the competitive landscape for new WGRs that comply with new fault tolerance standards. For existing WGRs the possible expense of retrofitting existing equipment could be significant. Compliance may require the addition of very expensive dynamic reactive devices in the WGR substation. The expenses could cause some WGRs to be retired rather than be upgraded. For all WGRs there is likely to be both increased capital cost and operating cost as a result of complying with new standards. There are also commercial issues with inability to control single source prices and with warranty terms and conditions as well as warranty cost. These technical, cost, and commercial issues raise compliance with new standards by existing generators to a policy level. See SP-08 for additional details pertaining to existing WGRs. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: There is no cost allocation issues associated with new WGRs, costs will be borne by the new WGR. For existing WGRs see the discussion for SP-08. |
| Strategy | Establish new requirements for new WGRs that balance WGR capabilities and transmission system design requirements. For existing WGRs, evaluate need. Recommendation. Adopt an Operating Guide Revision Request establishing new standards for WGR Voltage Ride Through to provide WGR fault tolerance capability. Perform detailed studies using well groomed data to evaluate exiting WGRs capability to ride through system faults. |
| Activities | ERCOT (E X): Participate in the process of establishing new standards. Specify scope and contract for studies to evaluate the need for system design changes related to faults affecting existing WGRs. |
|  | Market Participants (MP X): TSPs, generators and all market participants actively participate in the development of new standards for WGRs. |
| Follow-Up | Codify new standards in protocols (see SO-12). Require needed studies for existing WGRs to be completed by a specific date (see SP-08). |
| Schedule | 11/17/2008 Operating Guide Revision Request 208 approved establishing new Voltage Ride Through standards for WGRs (see SO-12). Studies for existing WGRs are underway with results required by June 2010 (see SP-08). |