ERCOT Operations Report

April 2010 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 4/3/2010 6:24 | 59.723 | 104 | Unit trip with 817 MW |
| 4/4/2010 10:44 | 59.868 | 7 | Unit trip with 417 MW |
| 4/7/2010 0:33 | 59.789 | 160 | Unit trip with 809 MW and 232 MW |
| 4/7/2010 1:31 | 60.104 | 4 | SCE +628 MW in 15 min. Out of Down Regulation. Wind generation increased 2000 MW in 60 min. |
| 4/7/2010 2:06 | 60.152 | 411 | SCE +1105 MW in 15 min. Out of Down Regulation. Wind generation increased 2000 MW in 60 min. |
| 4/8/2010 12:26 | 59.890 | 6 | Unit trip with 345 MW |
| 4/9/2010 21:32 | 59.885 | 3 | Unit trip with 373 MW |
| 4/12/2010 0:35 | 59.844 | 68 | Unit trip with 479 MW |
| 4/12/2010 11:42 | 59.854 | 55 | Unit trip with 455 MW |
| 4/14/2010 7:35 | 59.844 | 32 | Unit trip with 554 MW |
| 4/23/2010 23:59 | 60.104 | 4 | SCE +630 MW in 15 min. Out of Down Regulation. Generation schedules changing after offset calculation. |
| 4/24/2010 0:04 | 60.160 | 612 | SCE +630 MW in 15 min. Out of Down Regulation. Generation schedules changing after offset calculation. |
| 4/28/2010 2:08 | 60.103 | 4 | SCE +330 MW in 15 min. Out of Down Regulation. Load dropped by 225 MW in 15 min. |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 4/2/10 6:17:53 | 4/2/10 6:26:54 | 0:09:01 | 341.52 | Unit Trip |
| 4/3/10 6:24:03 | 4/3/10 6:56:54 | 0:32:51 | 1151.00 |  |
| 4/4/10 10:44:39 | 4/4/10 10:58:54 | 0:14:15 | 544.28 |  |
| 4/4/10 21:03:41 | 4/4/10 21:22:40 | 0:18:59 | 357.52 | Incorrect offset calculation |
| 4/5/10 3:19:59 | 4/5/10 3:35:38 | 0:15:39 | 362.85 | DC Tie Trip |
| 4/5/10 13:21:47 | 4/5/10 13:29:12 | 0:07:25 | 325.50 | Unit Trip |
| 4/7/10 0:33:47 | 4/7/10 1:04:06 | 0:26:13 | 965.81 |  |
| 4/7/10 7:16:02 | 4/7/10 7:21:06 | 0:05:04 | 330.83 | Unit Trip |
| 4/7/10 8:20:37 | 4/7/10 8:30:32 | 0:09:55 | 368.19 | Incorrect offset calculation |
| 4/8/10 12:26:47 | 4/8/10 12:42:32 | 0:15:45 | 426.89 |  |
| 4/9/10 21:32:03 | 4/9/10 21:40:18 | 0:08:15 | 453.58 |  |
| 4/11/10 21:18:37 | 4/11/10 21:25:40 | 0:07:03 | 336.17 | Unit Trip |
| 4/12/10 0:35:03 | 4/12/10 0:53:01 | 0:17:58 | 672.33 |  |
| 4/12/10 11:42:23 | 4/12/10 11:56:30 | 0:14:07 | 618.98 |  |
| 4/14/10 7:35:51 | 4/14/10 7:51:56 | 0:16:05 | 672.33 |  |
| 4/14/10 23:48:49 | 4/15/10 0:09:04 | 0:11:11 | 341.52 | Slow unit response |
| 4/17/10 20:49:03 | 4/17/10 20:54:32 | 0:05:29 | 352.19 | Unit Trip |
| 4/23/10 11:08:37 | 4/23/10 11:33:21 | 0:24:44 | 325.5 | Out of up regulation. |
| 4/24/10 21:10:27 | 4/24/10 21:16:48 | 0:06:21 | 325.5 | Unit Trip |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| DFW | 112 | 0 | 0 | 0 | 0 | 112 |
| Western | 0 | 3 | 0 | 3 | 2 | 5 |
| North | 2 | 0 | 0 | 0 | 0 | 2 |
| Houston | 0 | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| Austin | 0 | 0 | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 0 | 0 | 0 | 0 |
| E RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| South | 0 | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 | 0 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 | 0 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Northeast | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 114 | 3 | 0 | 3 | 2 | 119 |

| Historical Totals | Apr-10 | Apr-09 | Mar-10 |
| --- | --- | --- | --- |
| Austin | 0 | 28 | 7 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 0 | 8 | 0 |
| DFW | 112 | 11 | 61 |
| E RIO | 0 | 4 | 0 |
| Houston | 0 | 9 | 1 |
| Laredo | 0 | 12 | 0 |
| North | 2 | 12 | 3 |
| Northeast | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 1 |
| South | 0 | 2 | 0 |
| W RIO | 0 | 99 | 10 |
| Western | 5 | 5 | 8 |
| Total | 119 | 190 | 91 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Hamilton Road - Sonora 138KV | Sonora - Friess Ranch 69KV | 20 |
| Base Case | Matador - Paducah 69KV | 19 |
| Fort Mason - Gillespie and Yellow Jacket 138KV | Yellow Jacket - Hext 69KV | 8 |
| Graham SES - Long Creek Switching Station & Cook Field Road Switching Station 345KV | Putnam - Cisco 69KV | 8 |
| Midkiff Switch - Sprayberry 138KV | Midkiff Switch - Reagan Shell Tap 69 KV | 8 |
| Aspermont - Spur 138KV | Spur 138/69 KV AT | 7 |
| Graham SES - Parker Switch 345KV | Barton Switch - Oran TU 138KV | 7 |
| Jack County - Hill Top 138KV | Rhome TU - Decatur Tap 138KV | 6 |
| Graham - Parker 345KV | Flat Creek - Leon Switch 138KV | 6 |
| Pawnee - Lon Hill 345KV | Rincon - Airco CSW 138KV | 6 |
| Abilene Mulberry Creek - Bitter Creek & Long Creek Switching Station - Sweetwater Generating Plant 345KV | Trent - Merkel 69KV | 4 |
| Base Case | ENA Snyder - WKN_Breaker 69KV | 4 |
| Graham SES - Long Creek Switching Station & Cook Field Road Switching Station 345KV | Comanche Switch - Comanche Tap 138KV | 4 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Airport TMPP 138KV | 3 |
| Base Case | Eskota Switch 138/69KV AT | 3 |
| DuPont Switch - Ingleside Switch 138KV | Ingleside Cogen Switch - Ingelside DuPont 2 138KV | 3 |
| Odessa EHV - Morgan Creek - Quail Switch 345KV | Big Spring Switch - Big Spring West 138KV | 3 |
| Pearsall - San Miguel 138KV | Pearsall 138/69 KV AT | 3 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Pockrus 138KV | 3 |
| Santa Anna - Ballinger 138KV | Ballinger - Humble Ballinger 69KV | 3 |
| Abilene Mulberry Creek - Bitter Creek and Long Creek - Sweetwater Cogen 345KV | Sterling County - Sterling City 69KV | 2 |
| Batesville - Pearsall 138KV | Uvalde - Downie1 138KV | 2 |
| Paris Switch - Valley and Parker Switch - Valley South 345KV | Paris Switch 345/138KV AT | 2 |
| Farmersville - Monticello 345kV | Allen Switch - Monticello 345KV | 2 |
| Base Case | Stanton Switch - Big Springs 138KV | 2 |
| Hamilton Road - Sonora 138KV | San Angelo Power Station -Santiago 138KV | 2 |
| Midland East - Odessa 345KV | Odessa EHV 345/138KV autotransformer 1 | 2 |
| Morgan Creek SES - Bitter Creek & Sweetwater Generating Plant 345KV | Trent - Scott Rea Tap 69KV | 2 |
| Morgan SES - Quail Switch & Longshore 345KV | Big Spring West - Stanton Switch 138KV | 2 |
| PH Robinson 345/138KV AT2 | PH Robinson 345/138KV AT1 | 2 |
| Asherton - West Batesville 138KV | Batesville 138/69KV AT | 1 |
| Aspermont - Spur 138KV | Spur - Girard Tap 69KV | 1 |
| Austrop - Sandow Switch 345KV | Elgin Switch - Butler 138KV | 1 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Teasley 138KV | 1 |
| Victoria - Victoria DuPont Switch 138KV | Weaver Road - Green Lake 69KV | 1 |
| Big Brown SES - Venus Switch 345KV | Richland Chambers - Trinidad SES 345K | 1 |
| Dilley Switch - San Miguel Switch 138KV | Derby - Pearsall 69KV | 1 |
| Graham SES - Long Creek Switching Station & Cook Field Road Switching Station 345KV | Putnam - Leon Switch 138KV | 1 |
| Lon Hill - Weil Tract 138KV | Citgo West - Weil Tract 138KV | 1 |
| Lon Hill - Weil Tract 138KV | Westside - McKenzie 138KV | 1 |
| Long Creek - Sweetwater - Abilene Mulberry 345KV | Shiloh BEC - Hasse BEC POD 138KV | 1 |
| Lytton Springs - Zorn and Austrop Zorn 345KV | McCarty Lane - Ranch Road 12 138KV | 1 |
| Nelson Sharpe - Ajo 345KV | North Edinburg - Rachal 138KV | 1 |
| Orange Grove - Lon Hill 138KV | Lon Hill - Smith 69KV | 1 |
| Pawnee - Lon Hill 345KV | Sinton - Skidmore 69KV | 1 |
| Sweetwater Generating Plant - Long Creek Switching Station & Morgan Creek SES - Champion Creek Switching Station 345KV | Abilene Mulberry Creek - Long Creek Switching Station 345KV | 1 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Lake Creek SES 345KV | Goldthwaite - San Saba Switch 69KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West – North | 17 |
| North – Houston | 2 |
| North – South | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

4/28  Gillespie LCRA – Fort Mason – Yellow Jacket 138 kV (This RAP was proposed by AEP)

New Procedures/Forms/Operations Bulletins

None

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

4/01  10:54	Held IE 1100 Balancing Energy deployments for IE 1115 due to a Market Management System problem.  Resumed with the IE 1130 deployments.

4/22  23:30	Held IE 2330  Balancing Energy deployments for IE 2345 due to a Market Management System problem.  Resumed with the IE 2400 deployments.

Communication

None

## ERCOT peak (Unofficial)

04/23 17:00 40,174 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2007 | 2008 | 2009 | 2010 |
| January | 4.55 | 3.30 | 4.11 | 3.78 |
| February | 3.75 | 3.59 | 3.49 | 3.79 |
| March | 2.70 | 3.29 | 3.24 | 2.24 |
| April | 3.00 | 2.45 | 2.66 | 2.47 |
| May | 3.22 | 3.01 | 2.90 | NA |
| June | 4.46 | 2.81 | 2.89 | NA |
| July | 4.29 | 2.55 | 2.83 | NA |
| August | 3.11 | 3.66 | 3.07 | NA |
| September | 3.78 | 4.99 | 3.68 | NA |
| October | 3.08 | 2.79 | 2.92 | NA |
| November | 2.95 | 2.60 | 1.93 | NA |
| December | 3.74 | 4.54 | 3.70 | NA |
| Annual Average | 3.55 | 3.29 | 3.11 | 3.07 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 4/2/10 | 9:16 | 10:45 | Advisory for ARRS below 3000 MW. |
| 4/4/10 | 11:00 | 20:50 | OCN issued for projected reserve capacity shortage for HE 19 - 23. |
| 4/12/10 | 11:45 | 16:00 | Advisory issued due to ARRS below 3000 MW. |
| 4/23/10 | 7:12 | 10:30 | Advisory issued for ARRS below 3000 MW. |
| 4/23/10 | 12:54 | 19:17 | Advisory issued for ARRS below 3000 MW. |

Transmission Watch

4/1 – 4/30  00:15	Transmission Watch issued due to forced outage at Gail substation.  Implemented Block Load Transfer up to 2 MW from ERCOT (Gail substation) to SPP (Draw substation).

Emergency Notice

None

Texas RE Event Analysis

4/07 00:33	Loss of two units in a total of 1041 MW of generation.

4/17 20:48	Sandow Switch 40 SPS activated.

4/18 11:17	QSE loss network connectivity.

4/28 04:42	Eskota Switch SPS activated.

Others

4/27  21:36	Held IE 21:45 Balancing Energy deployments for IE 22:00 due to an offset calculation error.  Resumed with the IE 22:15 deployments.