| OGRR Number | 240 | OGRR Title | CREZ Facility Protection and Control Requirements |
| --- | --- | --- | --- |

| Date | March 4, 2010 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Rafael Garcia |
| E-mail Address | Rafael.Garcia@oncor.com |
| Company | Oncor Electric Delivery Company LLC |
| Phone Number | 817-215-5126 |
| Cell Number | 817-228-3541 |
| Market Segment | Investor Owned Utilities (IOU) |

Comments

As an ERCOT Market Participant, Oncor has worked hard to keep Operating Guides away from specifying technological solutions, regardless of what area of the market it affects.  We advocate identifying the performance requirements for protective systems, but not the specific technology to achieve the desired outcome.  Although the CREZ initiative presents new and immediate challenges to all TSPs, it represents the beginning and not the end of injection of new renewable energy technology in ERCOT.  For this reason, any change to the Operating Guides should not single out CREZ, but address the overall needs of a changing system topology.  The ERCOT Transmission Owners that have existing transmission circuits in service have a successful long history of correctly clearing transmission system disturbances, which serves as a clear indication of the utilization of good utility practices in implementing protective systems.  No protective relaying scheme is perfect and no one scheme is applicable for all situations without introducing other significant issues and additional cost.

The current differential protection scheme solution that is being mandated in this OGRR as the only appropriate scheme for all circuits requires the use of fiber optic cable for communication between terminals.  If the communication path is lost or the packets of information received at both ends do not match, the relay disables its high-speed protection scheme.  Because this scheme is so highly dependant on the availability of the communication channel, a fiber loop is being proposed as a backup route to ensure the availability of the circuit.  What is not mentioned in the OGRR is that in order to obtain an alternate path, in some cases the fiber signal must travel though multiple repeaters, numerous splices located between cable segments and at transpositions, and through multiple facilities owned and maintained by different transmission owners.  All of these connections are potential points of failure and can complicate restoration once an event occurs.  To say that the use of current differential protection represents the most reliable solution is all cases are highly questionable.  To our knowledge, nothing like this has ever been attempted between so many parties and this principle clearly violates the standard protection philosophy of keep it simple and straight forward.  CIP issues also do not appear to be addressed in the OGRR.

The SONET technology mandated by this OGRR typically allows anyone possessing the appropriate credentials and having access to any multiplexer in the loop to reconfigure any or all multiplexers in the loop remotely. Thus the establishment of a fiber loop or network owned by multiple parties also introduces concerns over NERC cyber security access/CIP standards compliance.

In addition this OGRR mentions a total cost of $20 million for the installation of fiber it does not include the total cost of establishing the SONET loop they require.  Oncor’s cost estimate to complete the loop and install the multiplexers is $50 million, which includes an additional 200 miles of fiber that would either have to be purchased from private networks or be installed.

The following represents Oncor’s comments addressing comments submitted by AEP in support of OGRR240.

The operational issues identified by AEP in their comments have been known for over 50 years. Modern relays and protection engineers have successfully implemented these schemes throughout the country with remarkable success.  Where high-speed protection is a must, DCB schemes have been used with great success.  Current differential relays have experienced their own issues. Communications errors or a loss of the channel can result in high-speed tripping being blocked by the relay when it is most needed. Communications errors and hardware failures have also been known to cause tripping of current differential line relaying during non-fault conditions. Although quite good, the use of current differential line relaying does not assure a misoperation-free protection system.

1. Mutual Coupling, 2. Current Reversal, 3. Power Swing

Mutual coupling, current reversal, and power swings are not new to our industry (have been around for at least the last 60 to 70 years) and all of these presently exist or occur on the ERCOT system. Protective relay manufacturers and protection engineers have worked together to develop better algorithms and improved setting criteria to appropriately deal with these phenomenon. We are seeing relay performance improvements in ERCOT as relay systems are replaced with more modern protective relays utilizing the same types of schemes.

4. Voltage Transients

Low capacitance CCVTs are well known to create voltage signal distortion that can result in inaccurate voltage signal replication and are therefore not well suited for relaying applications that require accurate voltage signals for high speed protection and are therefore not in line with using good utility practices. This problem is easily corrected by using better quality high-capacitance CCVTs.

5. Carrier

Different schemes are used for different reasons and DCB using power line carrier is biased toward reliability and is used where high speed tripping is a must.  If the carrier communications is lost, the relaying will still operate with high speed to ensure the fault is cleared quickly (minimizing potential damage) and allow the system to be restored to normal as quickly as possible.  It is true that the required relay settings will overreach remote terminals but the reach is controlled by settings minimizing exposure.  As previously stated, a current differential scheme on the other hand will not operate if the communication is lost; it is more secure but not as reliable as a DCB scheme.

Issues with series-compensated EHV line protection

We agree that series compensated lines, especially those with weak sources behind them, introduce new challenges that must be closely studied when applying protective relaying.

- 6. Voltage and Current Inversion

We agree that series compensated lines, especially those with weak sources behind them, may be better protected using current differential schemes.

- 7. Sub-synchronous Resonance

The sub-synchronous resonance issue is being studied and will be appropriately dealt with using mitigation techniques.

- 4. Distance Relay Settings

An assumption being made is that the voltage transformers are located on the bus side of the series compensation, but an alternative is to locate them on the line side, eliminating this concern.

- Recommendations on CREZ line protection schemes

5. Use Fiber-based Line Differential Scheme as Primary Protection, 2. Redundancy

Highly communication channel dependent.  Current differential schemes may not require coordination for external faults but are highly dependent on coordination with the remote terminal and may not operate correctly unless the equipment at both ends is properly matched and appropriate verification testing is performed.

There is no doubt that fiber optic cable has many uses, Oncor does not agree that current differential schemes are a replacement for all other line protection schemes.  Keep in mind that if both primary and back-up protection must be high speed, the alternate fiber path must be as highly reliable as the primary scheme with dual differential protection, which is questionable with so many different parties involved where one must deal with the following issues/ possible points of failure:

  - The number of splices along with quality of the splices

  - Number of transpositions where additional stresses are placed on the static

  - Number of repeaters

  - Security concerns wherever they are located (NERC/CIP compliance)

  - Secure AC and DC power sources must be provided to each of these devices

  - Transient/surge protection at each of these locations

  - Compatibility between equipment used by many different companies

  - Number of parties involved and who will monitor and respond to network issues

  - Long alternate paths of fiber in the order of several hundred miles in some cases to monitor and determine failure points

  - The ongoing need for IT support and required quick response time

  - If two high-speed systems are indeed needed, you cannot operate the affected circuit(s) with one communication channel unavailable.  Sharing one very long loop will affect the reliability of multiple circuits.

Oncor proposes the following language changes:

- Deletion of paragraph (17) of Section 7.2.2, Design and Operating Requirements for ERCOT System Facilities.  Oncor believes the “CREZ” label, in and of itself, is not an appropriate basis for engineering design decisions. The “CREZ” lines, other than the fact that some will have series-compensation, are not fundamentally different than the rest of the ERCOT System. “CREZ” will not function in isolation from the rest of the ERCOT System and should not have a different set of standards arbitrarily applied.  Drawing an artificial dividing line through the system map and applying two different sets of engineering standards and performance criteria seems arbitrary, unfair, and difficult to justify from a regulatory compliance or engineering viewpoint.  This list and wording should be deleted.

- Revising paragraph (1) of Section 7.2.4, Maintenance and Testing Requirements for ERCOT System Facilities.  Oncor believes that this is too prescriptive and Oncor favors the wording in the SPWG OGRR242.  While end-to-end testing is appropriate and necessary for some types of protection schemes, each facility owner should be allowed to determine what is necessary to fully verify any given protection system. This type of testing is also performed outside of the “CREZ” projects on an “as needed” basis.

- Revising paragraph (7) under “Dependability and Security” of Section 7.2.5.1, General Protection Criteria.  Oncor believes this wording is unclear, unnecessary, highly subjective, and should be revised.  The “best technologies available” for any given application is an engineering judgment decision and may not always be the newest or most complex technology.  Oncor favors the SPWG OGRR242 language that bases design upon performance needs.

- Revising paragraph (1) under Testing and Maintenance” of Section 7.2.5.1, General Protection Criteria.  Oncor believes this requirement is unnecessary and arbitrary applied to “CREZ.”   AEP wording should be deleted.  The periodic testing and maintenance procedures and needs of “CREZ” facilities are expected to be similar to the rest of the ERCOT System. Given the overall system design of the CREZ project, this may be needed even less than in other parts of the ERCOT System.

- Revising language under “Current Transformers” in Section 7.2.5.2, Equipment and Design Considerations.  Oncor believes that this requirement should not be different for “CREZ” than it is for other Facilities.  This design practice is appropriate for all new facilities.  Oncor favors the alternative language used in the SPWG OGRR242.

- Revising language under “Voltage Transformers and Potential Devices”.  Oncor believes that this requirement should not be different for “CREZ” than it is for other facilities. This design practice is appropriate for all new facilities. Oncor favors the alternative language used in the SPWG OGRR242.

- Revising language under “Batteries and Direct Current (DC) Supply.  Oncor believes that this requirement should not be different for “CREZ” than it is for other Facilities. This design practice is appropriate for all new transmission Facilities. Oncor believes the spare charger recommendation is too prescriptive and each Facility owner should determine what is right for his business practices.  Oncor favors the alternative language proposed in the SPWG OGRR242.

- Deletion of the AEP proposed language under “Circuit Breakers” in Section 7.2.5.2.  Oncor believes that this is an acceptable practice, but this language is too prescriptive.  The need for this specific control circuit function and the implementation method is determined by the control system design practices of each Facility owner.  This should not be “CREZ” specific.

- Deletion of the AEP proposed language under “Communications Channels” in Section 7.2.5.2.  Oncor recommends deleting this language.  This language is highly prescriptive and requires a very specific technology solution applied in a specific manner that may not be the best or most practical choice for every installation. The use of other viable technologies is excluded.  This is also applied arbitrarily to “CREZ” Facilities without defining any performance criteria or need.

- Revising paragraph (2) under “Control Cables and Wiring” in Section 7.2.5.2.  The requirement for shielded cable should be based upon need and the requirement should not be based upon a Facility being “CREZ”.  The use of shielded cable is frequently not necessary and introduces new design problems with respect to protecting the cable shield from damaging ground current flows.  Oncor favors using the language proposed in the SPWG OGRR242 and deleting this CREZ specific language.

- Revising language under “Transmission Line Protection” in Section 7.2.5.3, Specific Application Considerations.

  - This requirement is overly prescriptive and not based upon need.  Oncor favors using the SPWG OGRR242 language that is need-based and less technology specific.

  - The communication system cited in this requirement may not be practical for all installations.

  - The SPWG membership, AEP, and the DWG have all indicated that the type and quantity of studies necessary to accomplish this are unknown.  It is also unclear what “pre-determined slip speed” should be used, or how to determine it.  Oncor favors the SPWG OGRR242 language in place of this.

- Revising language under “Transmission Station Protection” in Section 7.2.5.3.  This requirement is extremely prescriptive and presumes certain control circuit design practices that may not be applicable to each Facility owner.  This requirement should not be CREZ specific.  The use of separate auxiliary relays for cross-tripping is a practice held over from the days of electro-mechanical relaying and its applicability is highly dependent upon other control circuit design practices.  Oncor recommends that this language be deleted.  The availability and applicability of these specific technologies is dependent upon the transformer design and manufacturer practices. Sudden pressure relays are often intentionally blocked from operation during high-current through faults, as they are prone to incorrect operation in some circumstances. Oncor favors the language proposed in the SPWG OGRR242.

- Revising language under “Breaker Failure Protection” in Section 7.2.5.3.  This is a highly prescriptive and unnecessary requirement.  There are multiple algorithms used by various relay manufacturers to successfully accomplish modern breaker-failure protection schemes.  Oncor favors the non-CREZ-specific changes proposed in the SPWG OGRR242.

Revised Proposed Guide Language

### 7.2.2	Design and Operating Requirements for ERCOT System Facilities

- Protective relay system shall be designed to provide reliability, a combination of dependability and security, so that protective relay system will perform correctly to remove faulted equipment from the ERCOT System.

- For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one (1) location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in other sections of the Operating Guides.

- Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

- The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

- Applicable IEEE/ANSI guides shall be considered when applying the protective relay system on the ERCOT System.

- The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

- All Facility owners shall give sufficient advance notice to ERCOT of any changes to their Facilities that could require changes in the protective relay system of neighboring Facility owners.

- Facility owners’ operations personnel shall be familiar with the purposes and limitations of the protective relay system.

- The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused Direct Current (DC) control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within thirty (30) days.  This documentation shall be reviewed by ERCOT for verification of implementation.

- Upon ERCOT’s request, within thirty (30) days, Power Generation Companies (PGCs) shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

- Upon ERCOT’s request, within thirty (30) days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

- Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by Generation Entities, to ERCOT upon their request within thirty (30) days.

- Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include under-frequency or under-voltage Load shedding.  A “Type 1 SPS” is any SPS that has wide-area impact and specifically includes any SPS that a) is designed to alter generation output or otherwise constrain generation or imports over DC Ties, or b) is designed to open 345 kV transmission lines or other lines that interconnect Transmission and/or Distribution Service Providers (TDSPs) and impact transfer limits.  Any SPS that has only local-area impact and involves only the Facilities of the owner-TDSP is a “Type 2 SPS.”  The determination of whether an SPS is Type 1 or Type 2 will be made by ERCOT upon receipt of a description of the SPS from the SPS owner.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of NERC Standards relating to SPSs, and shall additionally meet the following ERCOT requirements:

- The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources and HVDC ties.

- The SPS shall be automatically armed when appropriate.

- The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one (1) or more of the SPS’s monitored Facilities exceeds ninety-percent (90%) of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be allocated as agreed by the SPS owner and the Generation Resource owner.

- The status indication of any automatic or manual arming of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility(ies) controlled by the SPS.

- When a Transmission Operator (TO) removes an SPS from service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market.  When an SPS is returned to service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

- The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS every five years, or sooner as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and posted on the ERCOT website.

- For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Service Request to ERCOT.

- For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a Service Request.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one (1) review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, and approval of ERCOT before completion of the required ERCOT review.

- The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of any Facility(ies) controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

- An ERCOT SPS review shall verify that the SPS complies with ERCOT and NERC criteria, guides, and Reliability Standards.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within thirty (30) days.

- As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the appropriate Reliability and Operations Subcommittee (ROS) working groups such as the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

- ERCOT shall develop a methodology to include the SPS in the Commercially Significant Constraint (CSC) limit calculations, if appropriate.

- ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

- SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 6.1.2, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

- ERCOT shall report all SPS operations and misoperations to the Texas Regional Entity (TRE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to TRE.  An operation and misoperation of an SPS with respect to reporting requirements to TRE occurs when changes to the Transmission System occur, including but not limited to circuit breaker operation.  Owners of SPS’s will provide a monthly report to ERCOT describing each instance an SPS armed/activated and reset.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to TRE.

- If an SPS which reduces and/or removes generation from service operates more than two (2) times within a six (6) month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

- For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the ERCOT Market Information System (MIS).  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a Service Request, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the SPS.

7.2.4	Maintenance and Testing Requirements for ERCOT System Facilities

- The Facility Owner shall perform sufficient testing to verify the proper operation of each new or modified protective relay system prior to placing the equipment in its zone(s) of protection in service.

- Facility Owners shall have documented protective relay system maintenance and testing programs in place.  Documentation shall include identification of protective relay system, a summary of testing procedures including requirements for frequency of tests, and the date last tested.

- The Facility Owner shall periodically test and inspect all components of the protective relay system to assure continued reliability.  Identified deficiencies shall be corrected.  Documentation demonstrating compliance with the Facility Owner’s maintenance and testing programs shall be supplied to ERCOT or NERC upon their request within thirty (30) days.

#### 7.2.5.1	General Protection Criteria

Dependability

- Except as noted in Sections 4 and 5 below, all elements of the ERCOT System operated at 100 kV and above (i.e., lines, buses, transformers, generators, breakers, capacitor banks, etc.) shall be protected by two (2) protective relay systems.  Each protective relay system shall be independently capable of detecting and isolating all faults thereon.

- The protective relay system design should avoid the use of components common to the two (2) protective relay systems.  Areas of common exposure should be kept to a minimum to reduce the possibility of both protective relay systems being disabled by a single contingency.

- The use of two (2) identical protective relay systems is not generally recommended, due to the risk of simultaneous failure of both protective relay systems because of design deficiencies or equipment problems.

- Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.  This protection need not be duplicated.

- On installations where freestanding or column-type Current Transformers (CTs) are provided on one (1) side of the breaker only, the protective relay system should be provided to detect a fault on the primaries of such CTs.  This protection need not be duplicated.  Application of freestanding CTs requires extra care to ensure that the relaying is proper and that the schemes overlap.

Security

The protective relay system should be designed to isolate only the faulted element, except in those circumstances where additional elements should be tripped intentionally to preserve system integrity.  For faults external to the protected zone, each protective relay system should be designed to either not operate, or to operate selectively with other systems, including breaker failure.  (In this context, the limits of the protected zone are defined by the circuit breakers.)

Dependability and Security

- The protective relay system should be no more complex than required for any given application.

- To the maximum degree practicable, the components used in the protective relay system should be of proven quality, as demonstrated either by actual experience or by stringent tests under simulated operating conditions, to ensure that the reliability of the protective relay system is not degraded by the components.

- The protective relay system shall be designed to minimize the possibility of component failure or malfunction due to electrical transients and electromagnetic interference or external effects such as vibration, shock and temperature.

- Critical features associated with protective relay system and circuit breaker operation shall be annunciated or monitored.

- The protective relay system circuitry and physical arrangements shall be carefully designed so as to minimize the possibility of incorrect operations due to personnel error.

- Computerized fault studies shall be used during the planning or design stages to analyze the effects of an addition or modification to the ERCOT System and to determine proper protective relay system coordination.

- To the extent dynamic or transient analysis shows that a protection system, designed within the guidelines contained in these Operating Guides, is unable to operate in a manner that maintains continuity of service and/or system stability in accordance with NERC Reliability Standards and the Operating Guides, additional measures shall be considered for improvement to the operation of the protection system.  Additional measures may include redundant CTs, Voltage Transformer (VT), power supplies and communication paths.

Operating Time

The objective of the protective relay system is to take corrective action in the shortest practical time with due regard to selectivity, dependability and security. In cases where clearing times are deliberately extended, consideration should be given to the following:

- Effect on ERCOT System stability or reduction of stability margins.

- Possibility of causing or increasing damage to equipment and subsequent extended repair and/or outage time.

- Effect of disturbances on service to customers and neighboring Facility Owners.

Testing and Maintenance

- The design of the protective relay system both in terms of circuitry and physical arrangement shall facilitate periodic testing and maintenance.  Test devices or switches should be provided to eliminate the necessity for removing or disconnecting wires during periodic testing.

- Commissioning of new equipment should consist of the following steps:

- Relay installation wiring diagrams cross-checked against schematics

- After completion of construction, physical check of wiring and relay installation

- Check and testing before energizing of all equipment in the zone of protection, including relay testing.  It is desirable to test the relays at the setting the relay will have in service

- Check of supporting paperwork, such as relay test reports

- Check that the relay settings when received from the manufacturer concur with the intended manufacturer’s specifications

- Calibrate and check that proper utility’s settings have been made

- Maintain a record of trip check and energizing procedure performance

- Maintain a record of in-service measurement of voltage, current magnitudes, phase angles, and a comparison to expected values and to other instrumentation

- Release to Facility owner for service

Analysis of System Performance and Associated Protection Systems

- Relay operation and settings shall be reviewed periodically and whenever significant changes in generating sources, transmission facilities, or operating conditions are anticipated.

- Naturally occurring faults and other system disturbances should be analyzed as a source of information as to the health of relay schemes in the system.  Sources of information usually available are:

- Short circuit study for the exact conditions of the fault

- Fault recorder traces

- Sequence of events data recording the opening and closing of contacts in the protective relay scheme and associated communication equipment

- Fault locator data

- SCADA logger output of breaker operation and alarms

- Interviews with operating personnel and/or other witnesses

- Field report of relay flags and breaker counter changes

- Field report of the fault location, if found

- Records of relay setting, relay testing, trip check and energize procedures as carried out, in-service measurements, relay wiring diagrams and schematics, manufacturers' information

- Other coworkers and SPWG members

- Manufacturers’ application and design engineers

- Steps one can follow in analyzing a disturbance are:

- Gather data

- Create a time line consisting of events and periods between events

- Compare actual and calculated values of current and voltage during the periods between events

- Compare actual and expected breaker operations and flags

- Choose the least complicated explanation for contradictory information and to fill in missing information

- Gather additional information as indicated to prove or disprove explanations

- Iterate

- Document by issuing a report of all findings, changes, and recommendations

- After a reasonable time, check back to see if the recommendations have been carried out

#### 7.2.5.2	Equipment and Design Considerations

Current Transformers

- CTs associated with the protective relay system shall have adequate steady state and transient characteristics for their intended function.

- The output of each CT shall remain within acceptable limits for the connected burdens under all anticipated fault currents to ensure correct operation of the protective relay system.

- CTs or their secondary windings shall be located so that adjacent protection zones overlap.

- CT secondary wiring shall be grounded at only one (1) point. When multiple CTs are interconnected, the combination shall have only one (1) ground.

- For all transmission equipment with CTs installed or upgraded and subsequently energized after January 1, 2012, the two (2) protective relay systems protecting a zone shall utilize isolated and separate CTs, or isolated and separate secondary windings in the case of free-standing CTs.

- Other considerations:

- Internal bushing CTs are preferred over external slip-over CTs

- 10L800 (C800) class CTs are preferred for relaying

- Breakers and free-standing CTs with four or more sets of CTs are preferred

- Over-the-bushing external CTs can sometimes solve problems when there aren't enough CTs.  Note that there may be an unprotected region between the external CT and the bushing CT.

- Shorting type terminal blocks should be provided for all CTs

Voltage Transformers and Potential Devices

- Voltage Transformers (VTs) and potential devices associated with the protective relay system shall have adequate steady state and transient characteristics for their intended functions.

- VTs and potential devices shall have adequate volt-ampere capacity to supply the connected burden while maintaining their relay accuracy over their specified primary voltage range.

- Usually one (1) set of VTs (with two separate secondary windings per VT) per bus (i.e. single bus substation configuration) or per power system element (i.e. ring bus and breaker-and-a-half substation configurations) is sufficient.

- The two protective relay systems protecting ERCOT System Facilities may use separate secondary windings of the VTs or one (1) of the secondary windings may be dedicated to supplying the polarizing potential and the other winding used to supply other protection and monitoring functions.  For all VTs installed or upgraded and subsequently energized after January 1 2012, the two (2) protective relay systems protecting a zone shall utilize isolated and separate VT secondary windings.

- VT and potential device secondary wiring shall be grounded at only one (1) point.  (ANSI/IEEE C57 recommends grounding at the panel.)

- VT installations shall be designed with due regard to ferroresonance due to capacitance across the interrupter at 138kV and above.

- Other considerations

- Special attention should be given to the physical properties of secondary circuit fuses

- Capacitor coupled VTs are suitable for relaying and SCADA telemetry

- Report loss of VT voltage (VT fuse failure) over SCADA

Batteries and Direct Current (DC) Supply

- DC batteries associated with the protective relay system shall have a high degree of reliability.

- Two (2) batteries each with its own charger should be provided at each location.  An acceptable alternative is one (1) battery with two (2) separately protected branches.  The two protective relay systems protecting a zone shall be supplied from the separate sources or branches. For a new Facility at 100kV and above, two (2) batteries shall be required in locations that remote backup clearing of lines and substation faults is not achieved.  For new or expanded transmission Facilities at 200 kV and above built or upgraded and subsequently energized after January 1, 2012 with two or more transmission voltage circuit breakers, two batteries each with its own charger, are required.

- Each battery shall have sufficient capacity to permit operation of the station, in the event of a loss of its battery charger or the AC supply source, for the period of time necessary to transfer the load to the other battery or to re-establish the supply source. Each battery and its associated charger shall have sufficient capacity to supply its share of the DC Load of the station.

- A fault at the battery terminals can only be interrupted by a mid-bank protective device.  If a mid-bank protective device is not used, then the connections between the battery terminals and the main protective devices shall possess the highest possible degree of reliability.

- Battery chargers and all associated circuits shall be protected against short circuits.  All protective devices shall be coordinated to minimize the number of DC circuits interrupted.

- The regulation of DC voltage shall be designed such that, under all possible loading conditions, voltage within acceptable limits will be supplied to all devices.

- DC systems shall be monitored to detect abnormal voltage levels, both high and low, DC grounds, and loss of AC to the battery chargers.  Loss of DC to relay schemes shall be alarmed.  Also, where possible the loss of AC to the battery chargers and loss of DC should be provided as SCADA alarm inputs.

- DC systems shall be designed to minimize AC ripple and voltage transients.

- The DC circuit protective devices used shall have published DC interrupting ratings suitable for the required circuit duty.

AC Auxiliary Power

- There should be two (2) sources of station service AC supply, each capable of carrying all the critical loads associated with the protective relay system.

- Failure of station service AC supply should be alarmed over SCADA.

Circuit Breakers

- Two (2) trip coils, one (1) associated with each protection system, shall be provided for each operating mechanism.  The failure of one (1) coil shall not damage or impair the operation of the other coil.

- The design shall be such that the breaker will operate if either both trip coils are energized simultaneously, or either trip coil alone, and verified by tests.

- Circuit breaker auxiliary switches used in protection systems should be highly reliable with a positive make-break action and good contact wipe.  Multiplier contacts simulating breaker auxiliary switches should be used with caution in protection systems.

- A three-phase and line-to-ground interrupting study to validate or indicate breaker interrupting rating shall be performed.

Communications Channels

- Where communication channels are required for the protective relay system purposes, the communication facilities shall have a degree of reliability no less than that of the other protective relay system components.  For extra security, the output contacts from two (2) independent channels may be wired in series.

- Where communication channels are required in each of the two (2) protective relay systems, the channels shall be separated physically and designed to minimize the risk of both channels being disabled simultaneously by a single contingency.

- Communication channels shall be provided with means to verify signal performance.

- Other considerations

- Report loss of channel over SCADA

- Automatic testing of power line carrier (PLC) is desirable to reduce false trips from failure to block

- Split up PLC Loads between DC sources so that loss of one (1) fuse does not disable all the carrier sets.  If all the carrier sets were to be disabled, then multiple false trips during a fault could result.

- Control cables and wiring

Control Cables and Wiring

- Control cables, wiring and auxiliary control devices should be such as to assure high reliability with due consideration to published codes and standards, fire hazards, current-carrying capacity, voltage drop, insulation level, mechanical strength, routing, shielding, grounding and environment.

- Other considerations

- AC or DC go-and-return functions should be implemented in the same cable to avoid induction loops

- Individual wires in cables should have colored jackets, not black jackets with a "color" printed on the jacket

- Standardization of the relationship between wire colors and functions is desirable

- No splice in any wire or cable

- All cables terminated on terminal blocks

- Shielded cable should be installed in locations where electric fields, magnetic fields, or electromagnetic interference is sufficient enough to disrupt the reliable operation of the control cable and it cannot be mitigated by other means

Environment

- Means shall be employed to maintain environmental conditions that are favorable to the correct performance of the protective relay system.  Particular attention should be given to solid-state equipment installations.

- Other environmental hazards to look out for:

| - Fire ants | - Rats |
| --- | --- |
| - Snakes | - Dust, dirt, grime |
| - Trash and leftover hardware | - Water |
| - Gunfire | - Theft of substation and transmission grounds |
| - Hand-held radio keyed near solid-state relays | - Batteries located in same room as relays (battery fires) |
| - Severe cold weather conditions can impact operation of circuit breakers, DC battery, and carrier signals. |  |

#### 7.2.5.3	Specific Application Considerations

Transmission Line Protection

- 1.	Each of the two (2) independent protective relay systems shall detect and initiate action to clear any line fault without undue system disturbance.  The protective relay system shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme, a widespread disturbance will not result.  A protective relay system, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other protective relay system, including breaker failure.

- 2.	New transmission line protection Facilities shall include:

- Fuses shall not be used in the 3Vo polarizing supply for ground relays.

- Loss-of-potential function shall be used for schemes dependent on voltage for correct operations.   SCADA alarms shall be provided for Loss-of-potential conditions.

- Dual primary protection over dual communications channels shall be used where dynamic and/or voltage stability studies indicate non-pilot protection operating times are inadequate.

- 2.	Transmission line protection should include:

- Primary phase and ground protection over a communications channel.

- Backup relaying with at least two (2) zones of phase protection.

- Backup relaying with at least two (2) zones of ground protection, or backup relaying with ground directional overcurrent relaying (time delay and instantaneous).

- “Ground chain protection” or switch-to-on-fault to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs and protection elements dependent on distance measurement.

- Recognition and trip for open conductor is desirable but not required.

- Overload protection is provided by SCADA analog alarms and dispatcher discretion.

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure.

- Short lines may require special attention, such as dual primary schemes, etc.

- For transmission Facilities with series compensation, dual primary protection should be considered.  One (1) of the two (2) protective relay systems should be differential type.

- Fuses shall not be used in the 3Vo polarizing supply for ground relays.

- Settings for synchronization check relays should be set based on a study if deemed necessary.

- Transmission Station Protection

- 1.	Each zone in a station shall be protected by two (2) independent protective relay systems.  For zones not protected by line protection, at least one (1) of the two (2) protective relay systems shall be a differential type.

- 2.	The protective relay system shall be designed to operate for station faults so that, if ultimate clearing is accomplished by a breaker failure scheme, a widespread disturbance will not result.  The protective relay system shall be designed to operate properly for the anticipated range of currents.

- 3.	Station protection should consist of:

- Bus differential or bus overcurrent protection of all buses

- All transformers protected by transformer differential, transformer overcurrent, or fuses (for small transformers).  Note that ferroresonance is possible for fused transformers above 69kV.

- Sudden pressure relay protection for transformer main tanks and transformer tap changer compartments

- For transformers with conservator tanks, Buchholz relay protection for the transformer main tanks and transformer tap changer compartments are preferred in addition to sudden pressure relay protection.

Breaker Failure Protection

- 1.	Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.

- 2.	The breaker failure protection should be initiated by each of the protection systems that trip that breaker.  It is not necessary to duplicate the breaker failure protection itself.

- 3.	Induction cup, solid state, or microprocessor based current detectors shall be used to determine if a breaker has failed to interrupt.

- 4.	Plunger or clapper type overcurrent relays are not recommended as breaker failure fault detectors.

Generator Protection

- 1.	Generator faults shall be detected by more than one (1) protective relay system.  These may include faults in the generator or generator leads, unit transformer, and unit-connected station service transformer.

- 2.	Generators shall be protected to keep damage to the equipment and subsequent outage time to a minimum.  In view of the special consideration of generator unit protection, the following are some of the conditions that should be detected by the protection systems:

- Unbalanced phase currents

- Loss of excitation

- Over-excitation

- Field ground

- Inadvertent energization (reverse power)

- Uncleared system faults

- Off-frequency

It is recognized that the overall protection of a generator will also involve non-electrical considerations.  These have not been included as part of this criteria.

- 3.	The apparatus shall be protected when the generator is starting up or shutting down as well as running at normal speed; this may require additional relays, as the normal relays may not function satisfactorily at low frequencies.

- 4.	A generator shall not be tripped for a system swing condition except when that particular generator is out of step with the remainder of the system.  This does not apply to protective relay system designed to trip the generator as part of an overall plan to maintain stability of the ERCOT System.

- 5.	The loss of excitation relay shall be set with due regard to the performance of the excitation system.

Automatic Under-Frequency Load Shedding Protection Systems

- Automatic under-frequency Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, Maintenance and Testing Requirements for ERCOT System Facilities, apply to under-frequency Load shedding protection systems as well.

- 1.	Automatic under-frequency Load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the system during major emergencies.

- 2.	The criteria for the operation of these protection systems are detailed in Section 2.9, Requirements for Under-Frequency Relaying.

- 3.	Automatic under-frequency Load shedding protection systems need not be duplicated.

- 4.	Generator and turbine under-frequency protection systems shall be coordinated with Section 2.9.

- 5.	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency Load shedding program.

- 6.	Automatic Load restoration for an under-frequency Load shedding operation is not currently utilized in ERCOT.

Automatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage Load shedding systems are classified as protective relay systems. The maintenance requirements, discussed in Section 7.2.4 apply to under-voltage Load shedding protection systems as well.

- 1.	The requirement for under-voltage relaying shall be determined by system studies performed/administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

- Amount of Load to be shed to restore voltage to minimum acceptable level or higher,

- The minimum and maximum time delay allowed before automatically shedding Load,

- The voltage level(s) at which to initiate automatic relay operation, and

- The location(s) for effectively applying under-voltage Load shedding protection systems.

- 2.	Automatic under-voltage Load shedding protection systems need not be duplicated.

- 3.	Analyses shall be performed on under-voltage Load shedding schemes by working groups and/or equipment owners as assigned by ERCOT to demonstrate that they are expected to act before generators trip Off-line due to the protective relay requirements described in Section 3.1.4.6, Protective Relaying and Voltage Ride-Through (VRT) Requirement.  A specific exemption from this analysis requirement may be provided by the ROS.

- 4.	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

- 5.	Automatic Load restoration for an under-voltage Load shedding operation is not currently utilized in ERCOT.

- 6.	The scheme shall be designed to ensure reliable operation and to prevent false tripping.