Draft Planning Guides Outline

- Introduction (Rev 2)

- Process For Planning Guide Revisions (From Section 1 of Operating Guides - Rev 1)

- Regional Planning Process Rev 0 (RPG Charter)

  - Move TPIT to  Section 5.6 Data (Rev 1)

  - Move ALDR to Data (Rev 1)

  - Move Economic Criteria to Criteria section (Rev 1)

- Generation Interconnection Process (From Generation Interconnection or Change Request Procedure - Rev 0)

- Planning Criteria

  - Reliability criteria (Section 5 of the current operating guides – Rev 0)

  - Evaluate if section 7 (or parts thereof) of Operating Guides dealing with System Protection should be moved to the Planning Guides. (Rev 1 or 2)

  - Economic Criteria(from RPG Charter Rev 1)

  - Requirement for posting TSP Specific Planning Criteria (Rev 1 or 2)

- Data/Modeling

  - Transmission Planning Steady State models base case development (SSWG Procedures- Rev 1)(revised Nodal version Rev 2)

  - Dynamic Model development (DWG procedures Rev 1)

  - SPWG Procedures Model development (DWG procedures Rev 1)

  - TPIT Report Procedures (Rev 1 or 2)

  - ALDR  Procedures (Rev 1 or 2)

  - Economic Assumptions development Procedures (Rev 2)

  - Data Dictionary Explanation and Procedures (move from SSWG procedures-Rev 1)

  - Generator Data Procedures  for use in Transmission Planning (Rev 2)

  - Contingency List (Multiple Circuits) Submission and Procedures (move from SSWG procedures-Rev 1)

  - Connectivity node group development procedures with NMMS (Rev 1 or 2)

- Should the Planning Guides include PASA/SOO documentation? (PUC Sub Rule 25.505)

- Should the Planning Guides include CDR procedures? (Generation Adequacy TF/LOLP)

Notes:

- Rev 0 indicates inserting document without change.

- Rev 1  indicates inserting document with moves and deletions

- Rev 2 indicates inserting new or significantly revised document

- Introduction (Rev 2)

- Process For Planning Guide Revisions (From Section 1 of Operating Guides - Rev 1)

- Regional Planning Process Rev 0 (RPG Charter) – note that the content page is left here for now.  All sections in the document are now preceded with a “3” to indicate that this is the 3rd section of the Planning Guide.

CONTENTS Page

1 INTRODUCTION ........................................................................................................................... 4

1.2 REGIONAL PLANNING GROUP .......................................................................................... 4

1.3 OVERVIEW OF MAJOR TRANSMISSION PLANNING ACTIVITIES .............................. 5

1.3.1 Long Term System Assessment (LTSA) ......................................................................... 5

1.3.2 Five-Year Transmission Plan........................................................................................... 5

1.3.3 RPG Project Reviews....................................................................................................... 6

1.3.4 Generation Interconnection Process................................................................................. 6

2 RPG PROJECT REVIEW PROCESS ............................................................................................. 7

2.1 CATEGORIZATION OF PROPOSED TRANSMISSION PROJECTS.................................. 7

2.1.2 Tier 3............................................................................................................................... 7

2.1.3 Tier 2............................................................................................................................... 7

2.1.4 Tier 1............................................................................................................................... 7

2.1.5 Flowchart for Tiers........................................................................................................... 7

2.2 PROJECT SUBMISSION......................................................................................................... 8

2.2.1 All Projects....................................................................................................................... 8

2.2.2 Projects that are Not Included in the Current Five-Year Plan.......................................... 9

2.2.3 Other Information ............................................................................................................ 9

2.3 RPG PROJECT REVIEW PROCEDURE AND TIMELINE................................................. 10

2.3.1 All Tiers ......................................................................................................................... 10

2.3.2 Tier 3.............................................................................................................................. 10

2.3.3 Tiers 1 and 2 Only.......................................................................................................... 11

2.3.4 Determine Designated Providers of Transmission Additions ........................................ 11

2.3.5 RPG Acceptance and ERCOT Endorsement ................................................................. 11

2.3.6 Notify PUCT of Recommended Transmission Projects................................................. 12

2.3.7 Modifications to ERCOT Endorsed Projects ................................................................. 12

2.4 TRANSMISSION PROJECT IMPLEMENTATION TRACKING ....................................... 12

3 Project Evaluation......................................................................................................................... 13

3.1 DEFINITIONS OF RELIABILITY-DRIVEN AND ECONOMIC-DRIVEN PROJECTS.... 13

3.2 RELIABILITY-DRIVEN PROJECT EVALUATION........................................................... 13

3.3 ECONOMIC-DRIVEN PROJECT EVALUATION .............................................................. 14

4 Five-Year Plan Development Process............................................................................................ 15

4.1 DEVELOPMENT OF FIVE-YEAR PLAN............................................................................ 15

4.2 USE OF FIVE-YEAR PLAN.................................................................................................. 16

5 Requests For New or Modified Generation Interconnection ......................................................... 17

6 PLANNING RESPONSIBILITIES ............................................................................................... 18

6.1 ERCOT RESPONSIBILITIES................................................................................................ 18

6.2 TDSP RESPONSIBILITIES................................................................................................... 20

6.3 STAKEHOLDER/MARKET PARTICIPANT RESPONSIBILITIES................................... 21

3.1 INTRODUCTION

ERCOT, as the independent organization (IO) under the Public Utility Regulatory Act (PURA), is charged with nondiscriminatory coordination of market transactions, system-wide transmission planning, network reliability and ensuring the reliability and adequacy of the regional electric network in accordance with ERCOT and NERC reliability criteria. In addition, the IO ensures access to the transmission and distribution systems for all buyers and sellers of electricity on nondiscriminatory terms.

The ERCOT Staff will supervise and exercise comprehensive independent authority of the overall planning of transmission projects of the ERCOT transmission grid (transmission system) as outlined in PURA and Public Utility Commission of Texas (PUCT) Substantive Rules. ERCOT’s authority with respect to transmission projects that are local in nature is limited to supervising and coordinating the planning activities of Transmission/Distribution Service Providers. The PUCT Substantive Rules further indicate that the IO “shall evaluate and make a recommendation to the commission as to the need for any transmission facility over which it has comprehensive transmission planning authority.” In performing its evaluation of different transmission projects, ERCOT takes into consideration the need for and cost-effectiveness of proposed transmission projects in meeting the ERCOT and NERC planning criteria.

Transmission planning (60-kV and above) is a complex undertaking that requires significant work by, and coordination among, the IO and the Transmission/Distribution Service Providers (TDSPs), and other market participants. The IO works directly with the TDSPs, with stakeholders/market participants, and through the Regional Planning Group. Each of these entities has responsibilities to ensure the appropriate planning and construction occurs.

This document describes the practices and procedures through which the ERCOT meets its requirements related to system planning under Texas statute, North American Reliability Corporation (NERC) standards, Public Utility Commission of Texas (PUCT) rules, and the ERCOT Protocols and Operating Guides. This document becomes effective upon approval by the ERCOT Board of Directors.

3.1.2 REGIONAL PLANNING GROUP

Transmission planning affects many stakeholders and benefits from input of different ideas and perspectives. The Regional Planning Group (RPG) is the primary mechanism through which stakeholder communication related to planning activities in the ERCOT Region is accomplished.

The RPG is a non-voting, consensus-based organization focused on identifying needs, identifying potential solutions, communicating varying viewpoints and reviewing analyses related to the transmission system in the planning horizon. While participation in the RPG is required of all Transmission Service Providers (TSPs), membership is open to all stakeholders. Representatives of transmission and distribution owners (existing and potential), generators, marketers, consumer groups, environmental groups, landowners, governmental officials, Commission Staff and other entities typically participate in RPG meetings. The RPG is led and facilitated by ERCOT Staff. Meetings are held on an “as-needed” basis and are open to all RPG participants.

Communication with and among RPG members is accomplished via these open meetings, as well as email and web postings. All stakeholders who are interested in RPG activities and information should register for the RPG email distribution list. ERCOT maintains a controlled access area on the ERCOT website listing all projects and system planning related data that is not considered protected or proprietary. Access to such information is controlled because some of this information may be considered protected Critical Energy Infrastructure Information (CEII).

The goals of the RPG are:

- Coordinating transmission planning and construction to ensure that the ERCOT and NERC planning standards are met and that proposed projects are the most reasonable means of addressing planning requirements;

- Preventing inefficient solutions to regional problems through a coordinated effort and resolving the needs of the interconnected transmission systems while ensuring a reliable and adequate network;

- Planning the bulk transmission system with sufficient lead time, and considering longer-term needs and impacts, to avoid the unnecessary upgrades to the underlying transmission systems taking into account the transfer capacity needs between load and generation pockets to avoid unreasonable congestion costs;

- Allowing for stakeholder/market participant and consumer review of major proposed transmission project additions;

- Helping to develop coordinated SPSs and RAPs for new problems that occur, and for problems that appear likely to occur based upon the transmission planning simulations;

- Improving communication and understanding between neighboring TSPs on operating procedures, SPSs and RAPs that respond to contingencies, voltage deviations, and facility overloads;

- Allowing for REPs to understand the scope and magnitude of all proposed, planned, and approved transmission projects within ERCOT, so that each can appropriately reflect expected wires cost increases into their retail pricing; and,

- Integrating renewable technologies under PUCT Substantive Rules and Legislative mandates.

3.1.3 OVERVIEW OF MAJOR TRANSMISSION PLANNING ACTIVITIES

The process of planning a reliable and efficient transmission system for the ERCOT Region is composed of several types of activities and studies.

3.1.3.1 Long-Term System Assessment (LTSA) – The LTSA is performed by ERCOT in coordination with the RPG on a biennial basis (in even-numbered years) and reviewed annually.

The study uses scenario analysis techniques to assess the potential needs of the ERCOT system up to 20 years into the future. The role of the LTSA is not to recommend the construction of specific system upgrades, due to the high degree of uncertainty associated with the amount and location of loads and resources in this timeframe. Instead, the role of the LTSA is to evaluate the system upgrades that are indicated under each of a wide variety of scenarios in order to identify upgrades that are robust across a range of scenarios or might be more economic than the upgrades that would be determined considering only near-term needs in the Five-Year Transmission Plan development.

3.1.3.2 Five-Year Transmission Plan – The Five-Year Transmission Plan is developed annually by ERCOT, in coordination with the RPG, and by the TSPs. The Plan addresses region-wide reliability and economic transmission needs and the planned improvements to meet those needs for the upcoming five years. These planned improvements include projects previously approved by the ERCOT Board of Directors, projects previously reviewed by the RPG, new projects that will be refined at the appropriate time by TSPs in order to complete RPG review, and the local projects currently planned by TSPs. Combined, these projects represent ERCOT’s plan addressing the reliability and efficiency of the system to meet national and regional planning standards, criteria, and protocols. Projects that are included in the Five-Year Transmission Plan are not considered to have been endorsed by ERCOT until they have undergone the appropriate level of RPG Project Review, if required.

3.1.3.3 RPG Project Reviews – Except for minor transmission projects that have only localized impacts and projects that are directly associated with the interconnection of new generation, all transmission projects in the ERCOT region undergo a formal review by the RPG. In addition, ERCOT Staff performs an independent analysis of the need for major transmission projects that are submitted for RPG Project Review. The affirmative result of this review is formal endorsement of the project by ERCOT. This ERCOT Project Endorsement is intended to support, to the extent applicable, a finding by the PUCT that a project is necessary for the service, accommodation, convenience, or safety of the public within the meaning of PURA §37.056 and PUCT Substantive Rule § 25.101.

3.1.3.4 Generation Interconnection Process – This process facilitates the interconnection of new generation units in the ERCOT region by assessing the transmission upgrades necessary for new generating units to operate reliably. The process to study interconnecting new generation or modifying an existing generation interconnection to the ERCOT grid is covered in a separate procedure. The generation interconnection study process primarily covers the direct connection of generation facilities to the ERCOT grid and directly-related projects. Projects that are identified through this process and are regional in nature may be reviewed through the RPG Project Review Process upon recommendation by the TSP or ERCOT, subject to the confidentiality provisions of the generation interconnection procedure. ERCOT staff will perform an independent economic analysis of the transmission projects that are identified through this process which are expected to cost more than $25 million. This economic analysis is performed only for informational purposes; as such, no ERCOT endorsement will be provided. The results of the economic analysis will be included in the interconnection study posting. Additional upgrades to the transmission system that might be cost-effective as a result of new or modified generation may be initiated by any stakeholder through the RPG Project Review procedure described herein at the appropriate time, subject to the confidentiality provisions of the generation interconnection procedure.

3.2 RPG PROJECT REVIEW PROCESS

3.2.1 CATEGORIZATION OF PROPOSED TRANSMISSION PROJECTS

ERCOT classifies all transmission projects into one of four categories (or Tiers). Each Tier is defined so that projects with a similar cost and impact on reliability and the ERCOT market are grouped into the same Tier. The criteria used to classify a specific project into the appropriate Tier are given below, in increasing order of the level of review to which the projects within the Tier are subjected.

ERCOT Staff may use its reasonable judgment to increase the level of review of a proposed project (e.g. from Tier 3 to Tier 2) from that which would be strictly indicated by these criteria, based on stakeholder comments, ERCOT analysis or the system impacts of the project.

Any project that would be built by an entity that is exempt (e.g. a municipal utility) from getting a CCN for transmission projects but would require a CCN if it were to be built by a regulated entity will be treated as if the project would require a CCN for the purpose of defining the Tier of the project.

3.2.1.1 Tier 4 - This category consists of: small system upgrades whose estimated capital cost is less than or equal to $15 million and that do not require a CCN, as well as certain “neutral” projects. Neutral Projects are: the addition of or upgrades to radial transmission lines; the addition of equipment that does not affect the transfer capability of a line; repair and replacement-in-kind projects; projects that are directly associated with the interconnection of new generation; and the addition of static reactive devices. A project, irrespective of estimated capital cost, to serve a new load is considered to be a Neutral Project even if a CCN is required, unless such project would create a new transmission line connection between two stations (other than looping an existing line into the new load serving station).

3.2.1.2 Tier 3 - This category consists of projects with estimated capital costs between $15 million and $50 million not requiring a CCN.

3.2.1.3 Tier 2 - This category consists of projects with estimated capital costs less than $50 million requiring a CCN.

3.2.1.4 Tier 1 - This category is for all projects whose estimated capital cost is $50 million or greater.

3.2.1.5 Flowchart for Tiers - The flowchart below illustrates the general process, described in this subsection, used to classify projects into the four Tiers.

3.2.2 PROJECT SUBMISSION

Any stakeholder may initiate a RPG Project Review through the submission of a document describing the scope of the proposed project, as described in the Project Scope section below, to the RPG (rpg@ercot.com) mailbox. Projects should be submitted with sufficient lead-time to allow the Project Review to be completed prior to the date on which the project must be initiated by the designated TSP. Stakeholders may submit projects for RPG Project Review within any project Tier. All transmission projects in Tiers 1, 2 and 3 should be submitted. TSPs are not required to submit

Tier 4 projects for RPG review, but should endeavor to see that any Tier 4 projects that are known in advance are included in the cases used for development of the Five-Year Transmission Plan.

All system improvements that are necessary for the project to achieve the system performance improvement, or to correct the system performance deficiency, for which the project is intended should be bundled into a single project submission.

3.2.2.1 All Projects

The submittal of each transmission project (60-kV and above) for RPG Project Review should include the following elements:

- The proposed project description including expected cost, feasible alternative(s) considered, transmission topology and transmission facility modeling parameter data, and all study cases used to generate results supporting the need for the project in electronic format (powerflow data should be in PTI PSS/E RAWD format). Also, the submission should include accurate maps and one line diagrams showing locations of the proposed project and feasible alternatives (AutoCad-compatible format preferred);

- Identification of the SSWG or Five-Year Transmission Plan powerflow cases used as a basis for the study and associated PSS/E IDEVs or PowerWorld Auxiliary files that describe the proposed project.

- Description and data for all changes made to the SSWG or Five-Year Transmission Plan cases used to identify the need for the project, such as generating unit unavailability and area peak load forecast.

- A description of the reliability and/or economic problem that is being solved;

- Desired/needed in-service date for the project, and feasible in-service date, if different;

- The phone number and email address of the single point of contact person who can respond to ERCOT Staff and RPG participant questions or requests for additional information necessary for stakeholder review.

3.2.2.2 Projects that are Not Included in the Current Five-Year Transmission Plan

In addition, for projects that are not included in the current Five-Year Transmission Plan, the following elements should be included in the submission. While it is not necessary, if any of these additional elements are available for projects that are included in the Five-Year Transmission Plan, they should be included in the submittal of these projects as well.

- Analysis of rejected alternatives, including cost estimates, effect upon transfer capability, and other factors considered in the comparison of alternatives with the proposed project;

- Assumptions modeled in performance studies such that credible performance deficiencies can be identified through study;

- Results of performance analyses that are consistent with system operating practices and procedures;

- Documentation of the process used to identify specific performance deficiencies (reliability and economic);

Both transmission and non-transmission solutions to performance deficiencies may be considered where applicable.

3.2.2.3 Other Information

If there is any other information, not included above, that the submitter believes is relevant to consideration of the need for any submitted project, they should include that information in the project submission.

3.2.3 RPG PROJECT REVIEW PROCEDURE AND TIMELINE

The RPG Project Review Procedure is designed to review projects in a manner commensurate with the cost and impact to the market and to system reliability of the project, based on the Tier into which the project is grouped.

3.2.3.1 All Tiers

The RPG Project Review procedure for submitted projects in all Tiers consists of the following steps:

- ERCOT will provide electronic copies of RPG Project Review submittals to the RPG within seven days of receipt and solicit comments or questions from the RPG.

- All concerns/questions or objections about the submitted project by any stakeholder or ERCOT Staff should be submitted to the RPG within 21 days after ERCOT’s transmittal to the RPG.

- Stakeholders should each provide a “single” complete comment from their company about each project by the end of the 21-day review period rather than sending multiple comments at various times or from various individuals. A single comment will help

- ERCOT and the project submitter keep track of the comments and develop an appropriate response.

- Any questions related to data deficiency should be submitted to ERCOT and the submitter immediately.

- If concerns or objections about a project are received, the project will be put into “study mode” until all concerns are resolved or until ERCOT assesses that a reasonable effort has been made to resolve all concerns, generally no more than an additional 28 days.

- Project submitters should answer all questions and respond to all concerns in a timely manner.

- Comments should be based on good utility practice and sound engineering judgment. Suggestions should be able to be implemented by the TSP constructing and operating the project.

- ERCOT will post all project submissions, the comments received, and other information and databases associated with submitted transmission projects on its website.

3.2.3.2 Tier 3

- ERCOT will assume acceptance of a Tier 3 project by the RPG if no concerns/questions or objections are provided within 21 days of ERCOT’s transmittal to the RPG.

- If reasonable ERCOT or stakeholder concerns about a Tier 3 project cannot be resolved within the 28-day study mode, the project may be processed as a Tier 2 project, unless ERCOT assesses that reasonable progress is being made toward resolving these concerns.

- Projects that are required to meet an individual TDSP’s Planning Criteria and that are not covered by the NERC Reliability Standards or ERCOT Planning Criteria will also be processed in this Tier, and will be reclassified as a Tier 4 “neutral” project if comments are resolved.

3.2.3.3 Tiers 1 and 2 Only

For Tier 1 and 2 projects, ERCOT Staff will conduct an Independent Review of the submitted project:

- The ERCOT Independent Review will consist of studies and analyses necessary for ERCOT Staff to make its assessment of whether the proposed project is needed and whether the proposed project is the preferred solution to the identified system performance deficiency that the project is intended to resolve.

- ERCOT will consider all constructive comments received during the 21-day RPG comment period and factor these comments into the Independent Review of the project.

- ERCOT will attempt to complete the Independent Review for a project in 90 days or less.

- If ERCOT Staff is unable to complete their Independent Review based on RPG input within 90 days, ERCOT will provide the submitter a reason for the delay and expected completion time.

- ERCOT may, at its discretion, discuss submitted transmission projects at meetings of the RPG in order to obtain additional input into the Independent Review.

- ERCOT will prepare a written report documenting the results of its Review recommendation on the project and will distribute this report to the RPG.

- Tier 1 projects will require ERCOT Board of Directors endorsement.

3.2.3.4 Determine Designated Providers of Transmission Additions

Upon completion of the RPG Project Review, ERCOT Staff will determine designated providers for the recommended transmission projects. The default TSPs will be those TSPs that own the end points of the new projects. Those TSPs can agree to provide or delegate the new facilities. If different TSPs own the two ends of the recommended project, ERCOT will designate them as co-providers of the recommended project, and they can decide between themselves what parts of the recommended project they will each provide. If they cannot agree, ERCOT will determine their responsibility following a meeting with the parties. If a designated TSP agrees to provide a project and that designated TSP does not diligently pursue the project (during the time frame before a CCN is filed, if required) in a manner that will meet the required in-service date, then upon concurrence of the ERCOT Board of Directors, ERCOT will solicit interest from TSPs through the RPG and will designate an alternate TSP.

3.2.3.5 RPG Acceptance and ERCOT Endorsement

For Tier 3 Projects, successful resolution of all comments received from ERCOT Staff and stakeholders during the 21-day RPG comment period will result in RPG Acceptance of the proposed project. An RPG Acceptance letter will be sent to the designated TSP for the project, the project submitter (if different from the designated TSP), and copied to the RPG. For Tier 2 projects, ERCOT Staff recommendation as a result of the ERCOT Independent Review of the proposed project will constitute ERCOT Endorsement of the project. For Tier 1 projects, ERCOT Endorsement is obtained upon affirmative vote of the ERCOT Board of Directors. An ERCOT Endorsement letter will be sent to the designated TSP for the project, the project submitter (if different from the designated TSP), the Public Utility Commission of Texas (PUCT) and copied to the RPG upon receipt of ERCOT Endorsement for Tier 1 and Tier 2 projects.

Following the completion of the ERCOT Independent Review, ERCOT will present all Tier 1 projects to the ERCOT Board of Directors with its recommendation as to whether or not the project should be endorsed by the Board. Prior to presenting the project to the Board, ERCOT will present the project to the ERCOT Technical Advisory Committee (TAC) for review and comment. Comments from TAC will be included in the presentation to the Board for the Board’s consideration. ERCOT will make a reasonable effort to make these presentations to TAC and the Board at the next regularly scheduled meetings of these groups following completion of the ERCOT Independent Review of the project.

3.2.3.6 Notify PUCT of Recommended Transmission Projects

ERCOT will inform the PUCT of the disposition of all ERCOT Tier 1 or 2 transmission projects and of the designated TSPs for those projects. ERCOT will then support ERCOT Endorsed projects in future CCN proceedings required for those projects through the use of filed supporting documents and testimony if necessary.

3.2.3.7 Modifications to ERCOT Endorsed Projects

If the designated TSP for an ERCOT Endorsed project determines a need to make a significant change to the facilities included in the project (such as the line endpoint(s), number of circuits, voltage level, decrease in rating or similar major aspect of the project) prior to filing a CCN application(if required) for the project (or prior to beginning the final design of the project, if no CCN is required), the TSP should notify ERCOT via email (RPG @ercot.com) in a timely manner of the details of that change. If ERCOT concurs that the proposed change is significant, the change will be processed as a Tier 3 project.

3.2.4 TRANSMISSION PROJECT IMPLEMENTATION TRACKING

ERCOT will track the status of public transmission projects that change the characteristics of the grid that are modeled in powerflow cases as they are implemented, and communicate that status to stakeholders via the Transmission Project Information and Tracking database (TPIT). TPIT provides information on transmission projects that are included in current TSP plans or included in the Five-Year Transmission Plan, including a description of the project, the status of the project including currently-expected in-service dates, contact information for the designated TSP for the project, etc. The assigned Tier of each project and the review status of the project will also be included.

TPIT will be updated by the TSPs on a quarterly basis and posted on the ERCOT website on or around March 8, June 8, September 8 and December 8 of each year. Changes to the status of each project, if any, will be documented each quarter along with a brief description of the reason for the change. Individual project costs are not included, but a summary of the total costs of projects will be provided.

3.3 PROJECT EVALUATION

Proposed transmission projects will be evaluated using a variety of tools and techniques to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner. For most proposed projects, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet. The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area (as identified in the LTSA), and consideration of the relative operational impacts of the alternatives. In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place. Consideration of the merits of this alternative relative to the proposed transmission project is more complex. To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in the following subsections.

3.3.1 DEFINITIONS OF RELIABILITY-DRIVEN AND ECONOMIC-DRIVEN PROJECTS

Proposed transmission projects are categorized for evaluation purposes into two types: reliability-driven projects and economic-driven projects. The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment and dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve. If it is not possible to forecast a dispatch of the generating units such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a Reliability-Driven Project. If it is possible to simulate a dispatch of the generating units in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an Economic-Driven Project.

3.3.2 RELIABILITY-DRIVEN PROJECT EVALUATION

For reliability-driven projects, the comparison of project costs generally includes only the relative capital costs of the alternatives. In the case of Tier 1 and 2 projects, any differences in expected ERCOT system production costs between the alternatives may be included in the consideration of the relative costs of the alternatives, due to larger potential impacts on losses and congestion of these projects.

3.3.3 ECONOMIC-DRIVEN PROJECT EVALUATION

For economic-driven projects, the net economic benefit of a proposed project (or set of projects) will first be assessed over the project’s life based on the net societal benefit that is reasonably expected to accrue from the project. The project will be recommended if it is reasonably expected to result in positive net societal benefits. If the proposed project is not expected to provide positive net societal benefits, then the net consumer benefit of the project will be assessed, and the project will be recommended if the net consumer benefits are reasonably expected to be positive.

To determine the societal benefit of a proposed project, the revenue requirement of the capital cost of the project is compared to the expected savings in system production costs resulting from the project over the expected life of the project. Indirect benefits and costs associated with the project should be considered as well, where appropriate. The current set of financial assumptions upon which the revenue requirement calculations is based will be posted on the ERCOT Planning website. The expected production costs are based on a chronological simulation of the security-constrained unit commitment and economic dispatch of the generators connected to the ERCOT grid to serve the expected ERCOT system load over the planning horizon. This market simulation is intended to provide a reasonable representation of how the ERCOT system is expected to be operated over the simulated time period. From a practical standpoint, it is not feasible to perform this production cost simulation for the entire 30-40 year expected life of the project. Therefore, the production costs are projected over the period for which a simulation is feasible and a qualitative assessment is made of whether the factors driving the production cost savings due to the project can reasonably be expected to continue. If so, the levelized annual production cost savings over the period for which the simulation is feasible is calculated and compared to the first year annual revenue requirement of the transmission project. If this production cost savings exceeds this annual revenue requirement for the project, the project is economic from a societal perspective and will be recommended.

For projects that do not provide sufficient societal benefit to be recommended, the net consumer benefit of the proposed project will be calculated. Outputs from the same market simulation described above will be used to provide an estimate of the expected reduction in total system generator revenues due to the project, which is a reasonable indication in the ERCOT market of the impact on consumer costs due to the project. Expected above-market generator revenues not included in the simulation, such as RMR payments, may need to be included in this evaluation. If the levelized generator revenue reduction exceeds the first year annual revenue requirement for the project, the project is economic from the consumer benefit perspective and will be recommended.

Other indicators based on analyses of ERCOT system operations may be considered as appropriate in the determination of consumer benefits, including:

- out-of-merit payments for unit operations;

- visible ERCOT market indicators such as clearing prices of Transmission Congestion Rights or Congestion Revenue Rights;

- actual Market Clearing Prices or Location Marginal Prices and observed congestion.

In order for such an alternate indicator to be considered, the costs must be reasonably expected to be on-going and be adequately quantifiable and unavoidable given the physical limitation of the transmission system.

3.4 FIVE-YEAR TRANSMISSION PLAN DEVELOPMENT PROCESS

The purpose of the Five-Year Transmission Plan is to provide a coordinated plan for the ERCOT system, in which all planned improvements to the system are documented, and which includes projects that have achieved a level of review that is commensurate with the impact of the projects. The Five-Year Transmission Plan is updated on an annual basis. While unanticipated changes in load and generation may require additional projects to be needed that were not included in the current Five-Year Transmission Plan, or require additional evaluation of projects included in the current Five-Year Transmission Plan when they are submitted for RPG Project Review, the Plan provides a reasonable and supportable basis for analyses of the planned ERCOT grid.

3.4.1 DEVELOPMENT OF FIVE-YEAR TRANSMISSION PLAN

The starting case for the Five-Year Transmission Plan development is created by removing all Tier 1, 2 and 3 projects that have not undergone RPG review from the most recent Steady-State Working Group summer peak base cases for each year of the planning horizon. The planning process begins with computer modeling studies of the generation and transmission facilities and substation loads under normal conditions in the ERCOT system. Contingency conditions along with changes in load and generation that might be expected to occur in operation of the transmission grid are also modeled. To maintain adequate service and minimize interruptions during facility outages, model simulations are used to identify adverse results based upon the planning criteria and to examine the effectiveness of various problem-solving alternatives.

The effectiveness of each grid configuration and facility change will be evaluated under a variety of possible operating environments because loads and operating conditions cannot be predicted with certainty. As a result, repeated simulations under different conditions are often required. In addition, options considered for future installation may affect other alternatives so that several different combinations must be evaluated, thereby multiplying the number of simulations required.

Once feasible alternatives have been identified, the process is continued with a comparison of those alternatives. To determine the most favorable, the short-range and long-range benefits of each must be considered including operating flexibility and compatibility with future plans.

3.4.2 USE OF FIVE-YEAR TRANSMISSION PLAN

The Five-Year Transmission Plan will generally serve as the basis for all subsequent RPG Project Reviews, both of projects included within the Five-Year Transmission Plan and of other proposed projects. Stakeholders are encouraged to submit, at the start of the Five-Year Transmission Plan development process, any known transmission projects that are not in the current SSWG base cases and are likely to be submitted within the next year, as work on RPG Project Reviews will be limited while the Five-Year Transmission Plan is being developed and documented. Projects submitted for RPG Review after the Five-Year Transmission Plan development has begun and which need ERCOT Independent Review may be delayed. Inputs to the Five-Year Transmission Plan, such as new generating units and updated local transmission projects, may be updated at the time these subsequent studies are performed if ERCOT Staff or stakeholders identify such updates as being needed to appropriately consider the need for the specific project under review. If the project under review is included in the Five-Year Transmission Plan, and no changes are identified which would affect the need for the proposed project through the 21-Day Comment Period, then the Five-Year Transmission Plan will serve as the ERCOT Independent Review of the proposed project, if required.

Tier 1, 2, and 3 projects that are included in the Five-Year Transmission Plan should be submitted for RPG Project Review at an appropriate lead time. Generally, this lead time should be sufficient to allow the Review to be completed before the TSP reaches the decision point at which it must initiate the engineering and procurement in order to meet the required in-service date, but not farther in advance than is necessary. In general, these lead times will be 3-4 months for Tier 3 projects and 6-7 months for Tier 1 and 2 projects.

Tier 1, 2 and 3 projects that are included in the Five-Year Transmission Plan but do not reach this decision point before the development of the next year’s Five-Year Transmission Plan begins will be removed from the case used to develop the Five-Year Transmission Plan and will be re-evaluated as a part of the development of this subsequent Five-Year Transmission Plan.

3.5 REQUESTS FOR NEW OR MODIFIED GENERATION INTERCONNECTION

As required under PUCT Substantive Rules, ERCOT will receive and process all new generation interconnection and change requests in accordance with the procedure entitled “GENERATION INTERCONNECTION AND CHANGE REQUEST PROCEDURES” (GI Procedures). As a part of that process ERCOT will perform a steady-state security screening study to determine site feasibility for interconnection and at what level the generator can expect to operate with other generation in the area in operation before significant transmission additions are necessary. ERCOT will also make a very rough estimate of the transmission system additions needed to integrate the new generation. This information in the form of a report will be presented to the generating entity requesting interconnection, and the generating entity can then decide if it wants to continue to request interconnection at that site or withdraw the application. At that time, ERCOT will inform the generating entity if it considers the proposed site to be inappropriate to the point that ERCOT will not support the addition of transmission needed to integrate the project into the transmission system.

If the generating entity decides to go forward at the designated site, ERCOT will then initiate a full interconnection study and designate the TDSP whose system is most likely to be the point of direct interconnection for the new generator as the lead TDSP for the study. The full interconnection study is primarily intended to analyze and develop the direct interconnection and directly-related facilities that would be needed to reliably connect the interconnecting generator to the ERCOT grid.

The provisions of the GI Procedures with respect to confidentiality of generation interconnection requests will govern the treatment of that information. Once a generation interconnection becomes non-confidential under the GI Procedures, it may be included in scenario analysis in the Five-Year Transmission Plan or RPG Project Reviews. Once ERCOT receives an executed interconnection agreement or public, financially-binding agreement between the generator and TSP under which generation interconnection facilities would be constructed or a commitment letter from a municipal electric provider or an electric cooperative building a generation project, the project will be included in the base cases beyond its expected in-service year in the development of the Five-Year Transmission Plan and RPG Project Reviews. Tier 1, 2 or 3 transmission projects associated with generation interconnections may be submitted for RPG Project Review as soon as the confidentiality provisions of the GI Procedures allow. However, projects that are dependent on generation interconnections may not receive final RPG Acceptance or ERCOT Endorsement of the projects associated with the new generation until the execution of a generation interconnection agreement or other public, financially-binding agreement between the generator and TSP under which generation interconnection facilities would be constructed or ERCOT’s receipt of a commitment letter from a municipal electric provider or an electric cooperative building a generation project.

3.6 PLANNING RESPONSIBILITIES

ERCOT, the TDSPs and other stakeholders have important responsibilities in the planning process, both individually and as part of the RPG.

3.6.1 ERCOT RESPONSIBILITIES

ERCOT Staff will:

- Study and monitor the transmission system for current and future transmission constraints;

- Review generation additions and determine adequacy of generation reserve levels;

- Support development and validation efforts for appropriate and accurate modeling of generation, load and transmission equipment needed to support operations/planning studies and simulations.

- Gather load data via the Annual Load Data Request (ALDR) process and independently develop its own monthly, annual, and long-term forecasts;

- Gather generation data via the Generation Interconnection and Change Request Procedures and keep track of existing generation and new generation additions to the ERCOT system;

- Prepare information, studies and reports for various governmental agencies (FERC, PUCT, etc.) and national organizations (NERC, etc.);

- Perform simulations in order to determine the impact of various transmission line contingencies, load and generation levels on the reliability of the ERCOT transmission system;

- Execute independent simulation and testing of the transmission system to help investigate possible impacts to reliability and system security;

- Review, assess possible impacts and approve remedial action plans (RAPs) and special protection systems (SPSs);

- Supervise the processing of all requests for interconnection to the transmission system from owners of proposed new or expanded generating facilities, including performing or coordinating any applicable system security studies;

- Lead and supervise the RPG in the consideration and review of proposed projects to address transmission constraints and other system needs;

- Conduct an open process of public review and comment on major proposed transmission facility additions;

- Consider new transmission proposals submitted by all interested parties;

- Generate alternatives analysis, including estimated cost comparisons, and recommend beneficial projects/solutions;

- Recommend transmission facility additions that are the cost-effective means to meet the ERCOT and NERC planning criteria or are required for interconnection of new generating facilities into the ERCOT system;

- Submit certain transmission facility additions, as specified in this Charter, to the ERCOT Board of Directors for review and concurrence;

- Determine the providers of transmission additions;

- Notify the PUCT of all Board-supported transmission facility additions and their designated providers;

- Support, to the extent applicable, a finding by the PUCT that a project is necessary for the service, accommodation, convenience, or safety of the public within the meaning of PURA §37.056 and PUCT Substantive Rule §25.101;

- Coordinate with the ERCOT Technical Advisory Committee Reliability and Operations Subcommittee (ROS) in the performance of steady-state and dynamic simulation testing of the bulk power system to determine the impact on the planned system of occurrences of the types of contingencies listed in the North American Electric Reliability Corporation (NERC) Planning Standards;

- Work with the Steady-State Working Group (SSWG), Dynamic Working Group (DWG) and System Protection Working Group (SPWG) to model equipment, create databases, perform tests with the TSPs to evaluate compliance of their transmission facilities with the ERCOT Operating Guides, and recommend further studies if needed;

- Perform Reliability Must-Run (RMR) studies when generation owners notify ERCOT of their intent to mothball, not run or retire existing generating units to determine if RMR status for such generation is required to maintain area reliability consistent with the ERCOT Transmission Planning Criteria. Additionally, ERCOT Staff will coordinate with affected TSP(s) and other interested market participants to develop RMR exit strategies to ensure that an overall cost effective plan is developed, reviewed, approved, and implemented in an expeditious manner;

- Facilitate the quarterly communication of changes to project status via the ERCOT Transmission Project & Information Tracking (TPIT). The quarterly updates will be posted on the ERCOT website on March 8, June 8, September 8, and December 8 of each year;

- Facilitate the quarterly update and posting of the SSWG Dataset A and B cases to reflect changes to project status communicated in TPIT. The quarterly updates will be posted on the ERCOT website on or around March 1, June 1, September 1, and December 1 of each year;

- Post error correction files submitted by TSP(s) as soon as reasonably possible;

- Use a planning process and associated analysis tools that are flexible enough to accommodate the different internal planning, engineering, material procurement, capital budgeting schedules and financial structures of TSPs;

- Post electronic versions of the annual Federal Energy Regulatory Commission (FERC) 715 Reports, annual FERC Form 1 reports and all annual reports of all planned transmission projects provided by the TSPs.

- Maintain appropriate and cost effective computer hardware and software to perform all of the above responsibilities in a timely manner to meet stakeholder and ERCOT management objectives.

3.6.2 TDSP RESPONSIBILITIES

TDSPs shall:

- Ensure review and compliance with PURA and PUCT Substantive Rules obligations to plan, build and operate the transmission system for the benefit of all users;

- Perform appropriate tests to ensure the reliability of its own transmission facilities, recommend studies, and propose appropriate solutions;

- Utilize the RPG process as the forum for ERCOT Staff, PUCT Staff, consumers and stakeholder/market participant review of all proposed transmission projects;

- Provide accurate and appropriate load data via the ALDR process;

- Provide data necessary to allow RPG members to replicate studies of project proposals and feasible alternatives. This includes identifying the previously posted PTI PSS/E case to be used as the reference case, supplying PTI PSS/E IDEV or PowerWorld Auxiliary files to modify the case as necessary to develop the study case and supplying a written description of the project proposal, alternatives considered, and any other case changes that were necessary to replicate the study;

- Actively participate in and support the RPG efforts and ROS working groups by providing timely input, study comments and responses to comments submitted;

- Recommend coordinated studies to the RPG as needed of those conditions of importance to multiple ERCOT TSPs or the entire ERCOT power system;

- Propose appropriate solutions for issues identified by ERCOT including RAPs and SPSs;

- Support analysis and reports needed for the ERCOT Board of Directors to make the final decisions on the projects necessary to fulfill PURA and PUCT Substantive Rules obligations;

- Be responsible for obtaining the Certificate of Convenience and Necessity (CCN) and all other required regulatory approvals;

- Identify and provide the information necessary to remove Tier 1, 2, and 3 projects from the current SSWG cases in order to produce the cases that will be used for the Five-Year Transmission Plan development.

- Provide input, feedback and analysis necessary to develop the Five-Year Transmission Plan as a consensus plan of the transmission needs of the ERCOT system at the time the Plan is developed;

- Submit projects included in the Five-Year Transmission Plan for RPG Project Review at an appropriate lead time to meet the required in-service date;

- Make a firm commitment to construct with sufficient lead time to meet required in-service dates for most transmission line projects recognizing that some projects could take five to eight years to accommodate the time for routing studies, CCN approval, right-of-way acquisition and construction.

- Make every effort to adhere to the project schedule to meet the needs as determined through the RPG Project Review;

- Provide quarterly updates to ERCOT of transmission project status changes, recognizing that transmission planning is a continuous process;

  - Provide quarterly updates to reflect the current status of its transmission projects, and keep up to date all information/documentation relating to its transmission projects (previous, new, and future) in TPIT. These quarterly updates will be due one month prior to the dates that ERCOT Staff will post the updates (i.e., February 1, May 1, August 1, and November 1);

  - Provide quarterly PTI PSS/E IDEV updates (or PowerWorld Simulator Auxiliary Files) to the SSWG Dataset A and B cases that reflect the timing and scope change of projects using the most accurate information available to reflect current plans, actual conditions, and ongoing construction activities. These quarterly updates will be due one month prior to the dates that ERCOT Staff will post the updates;

  - Use the most accurate information available to annually assist in building accurate base cases (steady-state, stability and system protection) reflecting actual conditions, ongoing construction activities and future additions;

  - Submit error corrections to ERCOT as they are identified, with a description and associated PTI PSS/E IDEV file (or PowerWorld Simulator Auxiliary Files);

- Provide to ERCOT electronic copies of their planning criteria (or any basis document or philosophy used to justify transmission additions) and notify ERCOT of any changes within 30 days;

- Provide electronic copies of all generation interconnection requirements and notify ERCOT of any changes within 30 days;

- Provide to ERCOT their annual report of all planned transmission projects;

- Provide to ERCOT complete paper and electronic copies of their annual FERC Form 1, FERC 714 and FERC 715 filings;

- Provide to ERCOT a copy of all signed interconnection agreements or other agreements under which generation interconnection facilities would be constructed within ten business days following the signing of the agreement;

- Provide to ERCOT and other interested market participants upon request, annually updated paper and electronic copies of complete system oneline diagrams. It is recognized that the TSP may require market participants to enter into a confidentiality agreement before providing complete system oneline diagrams in order to ensure the protection of this Critical Energy Infrastructure Information and may charge a reasonable fee to cover the cost of producing the requested documents.

3.6.3 STAKEHOLDER/MARKET PARTICIPANT RESPONSIBILITIES

With the implementation of retail competition in the ERCOT market and the associated changes in market design and operations, more market participants and stakeholders have a financial stake in the development of a reliable and cost-efficient transmission system. The Retail Electric Providers (REPs) and load-serving Qualified Scheduling Entities (QSEs) pay for transmission wires services. Wholesale energy costs and prices are significantly affected by transmission system constraints, providing a strong financial incentive for market participants and other stakeholders to become actively involved in the ERCOT transmission planning process to encourage efficient, long-term transmission system development. By working in a collaborative fashion, stakeholders will ensure that reliable and cost-effective long-term planning is pursued.

Stakeholders/Market Participants shall:

- Actively participate in the ERCOT transmission planning process to encourage efficient, reliable, and cost-effective long-term transmission system development;

- Provide accurate, appropriate and timely data including performance characteristics and limitations upon request by ERCOT and TDSPs for their simulations and analysis;

- Support and assist in operations and planning model development and validation efforts;

- Review proposed projects and provide timely comments about projects submitted to the RPG for their review that address reliability and/or economic deficiencies of the transmission system;

- Provide data necessary to allow RPG members to replicate studies of project proposals. This includes identifying the previously posted PTI PSS/E case to be used as the reference case, supplying PTI PSS/E IDEV file (or PowerWorld Simulator Auxiliary Files) to modify the case as necessary to develop the study case and supply a written description of the project proposal, alternatives considered, and any other case changes that were necessary to replicate the study;

- Develop and submit accurate/appropriate proposed projects for review;

- Operate facilities and provide updated information per the requirements of the ERCOT Protocols, Operating Guides, Generation Interconnection or Change Request Procedures and applicable Standards of the North American Electric Reliability Corporation. These obligations include real and reactive power, frequency control and governor action, and coordination of protection systems, controls and machine or load characteristics;

- Maintain the confidentiality of Critical Energy Infrastructure Information.

All market participants may develop and submit proposed projects to the Regional Planning Group (RPG), as well as review projects developed and proposed by the RPG. Broad participation in the process results in a thorough development of projects. However, confidentiality provisions prevent participation of non-TDSPs in the studies leading to interconnection agreements with generators until they become public.

Section 3 – items outside of Rev 0

  - Move TPIT to  Section 5.6 Data (Rev 1)

  - Move ALDR to Data (Rev 1)

  - Move Economic Criteria to Criteria section (Rev 1)

- Generation Interconnection Process (From Generation Interconnection or Change Request Procedure - Rev 0)

GENERATION INTERCONNECTION OR

CHANGE REQUEST PROCEDURE

January 18, 2010

Version 2.02

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 1/5/2009 | 2.0 | Modified Procedures Document developed through RPG – corrected version ; endorsed by TAC, Approved by ERCOT CEO | ERCOT/RPG |
| 1/25/2010 | 2.01 | Effective date change | ERCOT |
| 1/26/2010 | 2.02 | Appendix B link to SS-FIS RARF Data Submission Guide | ERCOT |

Table of Contents

1	INTRODUCTION	1-1

Purpose	1-1

Applicability	1-1

Effective Date	1-2

Modification and Approval Process	1-2

2	INTERCONNECTION PROCESS AND PROCEDURES	2-2

Generation Interconnection or Change Request (GINR) Application	2-2

2.1.1	Submitting Generation Interconnection or Change Request to ERCOT	2-2

2.1.2	Generation Interconnection or Change Request Screening Study Fees	2-3

2.1.3	Where to Submit Data and Fees	2-3

2.1.4	Unique Project Identification	2-3

Full Interconnection Study Request	2-4

2.1.5	Submitting FIS Request to ERCOT	2-4

2.1.6	FIS Request Application Fees	2-5

2.1.7	Where to Submit Data	2-5

2.1.8	Use of the Resource Asset Registration Form	2-5

Modifications to Request	2-5

3	STUDY PROCESSES AND PROCEDURES	3-6

Security Screening Study	3-6

Full Interconnection Study	3-7

3.1.1	TSP Communication	3-8

3.1.2	Full Interconnection Study Process Overview	3-8

3.1.3	Full Interconnection Study Elements	3-9

3.1.4	Economic Study	3-11

3.1.5	FIS Study Report and Follow-up	3-11

3.1.6	Proof of Site Control	3-12

3.1.7	Confidentiality	3-12

Interconnection Agreement	3-13

3.1.8	Standard Generation Interconnection Agreement	3-13

3.1.9	Other Arrangements for Transmission Service	3-13

3.1.10	Provisions for Municipals and Cooperatives	3-14

4	INTERCONNECTION DATA, FEES, AND TIMETABLES	4-14

Generation Plant Data Requirements	4-14

4.1.1	Application and Security Screening Study	4-14

4.1.2	Full Interconnection Study	4-14

4.1.3	Prior to Start of Construction	4-15

4.1.4	Prior to Commercial Service	4-15

4.1.5	During Continuing Operations	4-15

Interconnection Study Fees	4-16

4.1.6	Security Screening Study Fee	4-16

4.1.7	Stability Modeling Fee	4-16

4.1.8	Full Interconnection Study Fee/Cost	4-17

Interconnection Process Timetables	4-17

GENERAL AND TECHNICAL STANDARDS	4-18

4.1.9	Transformer Tap Position	4-18

APPENDIX A	4-19

GENERATION ENTITY INFORMATION SHEET	4-20

APPENDIX B	4-21

GENERATOR INTERCONNECTION REQUEST SCREENING STUDY DATA SHEET	4-21

# 4.1INTRODUCTION

## Purpose

The primary purpose of the ERCOT Generation Interconnection or Change Request Procedure (Procedure) is to define the requirements and processes used to facilitate new or modified generation interconnections with the transmission system of the Electric Reliability Council of Texas (ERCOT).  The activities outlined in this Procedure are expected to:

- Determine the facilities required to directly interconnect new or modified generation to the ERCOT System;

- Ensure that the interconnection of the new or modified generation is accomplished in a manner that maintains the reliability of the ERCOT System and compliance with the North American Electric Reliability Corporation (NERC) Reliability Standards, ERCOT Protocols and Operating Guides;

- Increase the quality of communications between the generating entity (GE), transmission service provider (TSP), and ERCOT;

- Provide for the best available information on future capacity additions for use in identifying, forecasting, and analyzing both short- and long-range ERCOT capabilities, demands, and reserves; and,

- Provide accurate initial data about the generation facility to ERCOT to ensure that ERCOT and stakeholders have the information necessary for planning purposes.

The requirements and procedures in this Procedure conform to all applicable rules, standards, protocols, and guides of the Public Utility Commission of Texas (PUCT), NERC, and ERCOT.  In the event of a conflict between this Procedure and those applicable rules, standards, protocols, and guides of the PUCT, NERC and ERCOT, then such rules, standards, protocols and guides will take precedence over the Procedure.

## Applicability

The requirements in this Procedure are applicable, in general, to the following:

- New generating Resources including storage devices, with an aggregate power output (gross Resource output minus auxiliary Load directly related to the Resource) of 10 MW or greater, planning to interconnect to transmission in the ERCOT System.

- Existing generating Resources interconnected in the ERCOT System that are seeking to:

  - upgrade the rated capacity of the Resource by 10 MW or greater within a single year,

  - re-power the Resource, or

  - change the physical or electrical interconnection of the Resource.

Interconnection requirements for on-site distributed generation are not subject to this Procedure but are addressed in PUCT Substantive Rules §25.211 (Interconnection of On-Site Distributed Generation) and §25.212 (Technical Requirements for Interconnection and Parallel Operation of On-Site Distributed Generation).

## Effective Date

This Procedure and modifications thereto will become effective upon approval and will apply to all future and current interconnection requests that have not yet signed an Interconnection Agreement (IA) by the date of this approval.

## Modification and Approval Process

Modifications to this Procedure will be proposed by ERCOT, presented to the Regional Planning Group (RPG) and Technical Advisory Committee (TAC) for comment prior to approval, and approved by the ERCOT CEO.

# INTERCONNECTION PROCESS AND PROCEDURES

The ERCOT interconnection process is designed in accordance with PUCT Substantive Rule §25.198 (Initiating Transmission Service) which delegates to ERCOT the responsibility for implementing the transmission interconnection process.

## Generation Interconnection or Change Request (GINR) Application

Any generating entity (GE) seeking an interconnection to the ERCOT System or increase in Resource capability, as applicable in Section 1, Applicability, must submit the following to ERCOT:

- a generation entity information sheet (Appendix A),

- a completed GINR screening study data form (Appendix B), and

- the appropriate fee (as detailed in Section 4.2.1).

### Submitting Generation Interconnection or Change Request to ERCOT

All GINR Applications and supporting data submittals shall be delivered to ERCOT by standard mail, facsimile (fax), or Internet email. Applications and supporting data shall be sent as discrete file attachments.  The application with signature may be in PDF form if desired but the supporting data shall be sent as a Microsoft Excel file attachment so that data may be easily extracted to reduce transcription errors.

In order to clearly identify GINR Applications, it is important that GENERATION INTERCONNECTION OR CHANGE REQUEST is the first line of the address field or is in the subject field of an email request.

The GE shall include in the GINR Application all information necessary to allow for timely development, design, and implementation of any electric system improvements or enhancements required by ERCOT and the TSP to reliably meet the interconnection requirements of the proposed generation.  This information shall be of sufficient detail for use in establishing transfer capabilities, operating limits (including stability), and planning margins to provide both reliability and operating efficiency as well as facilitating coordinated planning for future transmission system additions.

ERCOT Staff will notify the GE within 7 business days through telephone call or email if the GINR Application fails to include the applicable fees or the information that is necessary to perform the initial screening interconnection studies.  If the applicant fails to respond to ERCOT’s inquiries within 10 business days, the GINR will be deemed incomplete and rejected. ERCOT shall notify the applicant if such condition occurs.

Once the application has been deemed materially complete, ERCOT Staff will date-stamp the application, add the interconnection request to the ERCOT interconnection list, and notify the GE of receipt of the completed application within 10 business days.  The GE should note that the date stamp is not a reservation of transmission capacity, either planned or unplanned.

An ERCOT Staff engineer will be assigned to oversee the interconnection study process and answer questions concerning the interconnection screening study and process.   Once assigned, this engineer will contact the GE and will be the primary ERCOT contact for interconnection studies.  If during the course of the studies, additional information is needed by ERCOT from the GE, ERCOT will immediately notify the GE and the GE will have 10 business days to answer the request for additional information without impacting the study timeline.

Prior to the initial contact from this engineer, GEs should direct questions concerning this Procedure to GINR@ercot.com.  The GE should contact their ERCOT Wholesale Services client representative for all queries that are not related to the interconnection studies.

If a generation facility that uses the same physical transmission interconnection is to be built in stages with in-service dates more than one year apart, the stages should be treated as separate interconnection requests but may be included in the same study.

### Generation Interconnection or Change Request Screening Study Fees

In order to consider the GINR, a security screening study fee   must be remitted to ERCOT along with the GINR Application as explained in detail in Section 4.2.1.    The security screening study fee is non-refundable.  The GE may choose to wire money to ERCOT to comply with the fee requirements.

For instructions on how to wire the funds to ERCOT, send an email to GINR@ercot.com requesting the account and wiring information.  For security purposes, this information has not been included in this Procedure nor is it posted on an ERCOT website.

If submitting the payment via standard mail, please make the check payable to Electric Reliability Council of Texas, Inc.  Please contact GINR@ercot.com to alert ERCOT to this method of submission for the application.

### Where to Submit Data and Fees

All standard mail submissions for the application, data, or fees shall be sent to the following address:

GENERATION INTERCONNECTION REQUEST

ATTN: Manager, Regional Planning

ERCOT, INC.

2705 WEST LAKE DRIVE

TAYLOR, TEXAS 76574-2136

Submission of the application and data via email shall be addressed to GINR@ercot.com. All data for studies shall be submitted electronically.

### Unique Project Identification

ERCOT Staff will assign a unique name to all GINRs according to the following convention:

yrINRxxxxp

where:

yr is the calendar year the generation is anticipated to be online (08, 09, 10)

INR indicates interconnection request

xxxx is a sequence number beginning with 0001 (reset for each year)

p is an optional, sequential alphabetical identifier beginning with ‘a’ to be used for phased projects

It is vital that all correspondence relating to a specific GINR, security screening or full interconnection study reference this unique project identification number once it has been assigned by ERCOT.

## Full Interconnection Study Request

Any GE seeking a Full Interconnection Study (FIS) for interconnection to the ERCOT System, as applicable in Section 1, Applicability, must submit the following to ERCOT:

- a notice to proceed with the FIS,

- the Resource Asset Registration Form (RARF) excel spreadsheet with applicable information required for interconnection studies as described in the RARF instructions (the RARF is located in the Resource Asset Registration Forms zip file located at http://www.ercot.com/gridinfo/generation/index).

- a stability modeling fee (as detailed in Section 4.2.2), and

- proof of site control (see Section 3.2.6)

In addition, there will be a FIS fee/cost paid directly to the TSP(s) (see Section 4.2.3).

### Submitting FIS Request to ERCOT

All FIS requests and supporting data submittals shall be delivered to ERCOT by Internet email. The supporting data shall be sent as discrete file attachments.

In order to clearly identify the GINR, it is important that the associated project INR number is referenced in the subject field of all communications.

The GE shall include in the FIS request all information necessary to allow for timely development, design, and implementation of any electric system improvements or enhancements required by ERCOT and the TSP to reliably meet the interconnection requirements of the proposed generation.  This information shall be of sufficient detail for use in establishing transfer capabilities, operating limits (including stability), and planning margins to provide both reliability and operating efficiency as well as facilitating coordinated planning for future transmission system additions.

Upon receipt of the FIS request, the assigned ERCOT Staff engineer will continue to be the primary ERCOT contact for the GE, ensuring RARF data is communicated to the TSP. The engineer will initiate a meeting between the TSP(s) and the GE. If during the course of the studies, additional information is needed from the GE, ERCOT will immediately notify the GE and the GE will have 10 business days to answer the request for additional information without impacting the study timeline.

### FIS Request Application Fees

When a FIS is requested, a stability modeling fee must be remitted to ERCOT as explained in detail in Section 4.2.2.  The stability modeling fee is non-refundable.  The GE may choose to wire money to ERCOT to comply with the fee requirements.

For instructions on how to wire the funds to ERCOT, send an email to GINR@ercot.com requesting the account and wiring information.  For security purposes, this information has not been included in this document nor is it posted on an ERCOT website.

If submitting the payment via standard mail, please make the check payable to Electric Reliability Council of Texas, Inc.  Please contact GINR@ercot.com to alert ERCOT to this method of submission for the application.

### Where to Submit Data

Submission of the data via email shall be addressed to GINR@ercot.com. All design data shall be submitted electronically.

### Use of the Resource Asset Registration Form

The GE shall use the RARF in order to facilitate data submittal for the planning studies and to reduce duplication/redundancy of forms. Key portions of the workbook include, but are not limited to, the following tabs:

- Site Information

- Unit Information

- Reactive Capability

- Planning

- Protection

- Subsynchronous Resonance

The RARF and all updates shall be submitted by the GE and sent to the assigned ERCOT Staff engineer and to GINR@ercot.com. While the TSP may request information necessary to perform the FIS from the GE directly, and the GE must provide this information to the TSP in order to facilitate the completion of the FIS in a timely manner, the GE must also contemporaneously submit to ERCOT an update to the RARF containing the information.  ERCOT will forward this information along with a change report to the TSP(s) for use with the FIS.  The planning submittals of the RARF are considered planning data and should accurately reflect the design of the facility. Please note this process does not meet the RARF submittal requirements contained in the ERCOT Protocols, but the use of this format is intended to facilitate the preparation of the data required for that process and the continuity of data between the interconnection study process and the data submitted for Resource registration.

## Modifications to Request

The GE shall maintain communication with ERCOT Staff and the TSP at all stages of the generation interconnection process.  The GE must also notify both ERCOT and the TSP of any changes that would affect the technical attributes and/or timeline of the project, including, but not limited to, capacity, in-service date, changes in location, changes in generator type, interconnection agreement execution, air permit acquisition, etc. as soon as these changes are known.   The GE shall maintain the RARF with the most up-to-date design information and shall submit the updated information to ERCOT and the TSP.   All changes of ownership must be communicated to ERCOT and the TSP when the ownership transfer occurs during the interconnection process and should include evidence of the ownership change such as a purchase/sale agreement.

If, after receipt of the updated RARF, ERCOT or the TSP determines that changes to the project (submitted after the application was deemed complete) are sufficiently substantive to warrant new studies, then ERCOT may require updated studies to be performed before the generator is allowed to interconnect to the ERCOT System.  The GE and TSP(s) will work out an appropriate agreement for the TSP(s) to perform the revised FIS and the TSP will provide the revised FIS to ERCOT and the other TSPs through the confidential email list.  If the requested capacity increases by more than 20% from the amount that was included in the screening study, ERCOT shall require the GE to submit a new GINR for the additional capacity or to submit a new GINR for the entire project.  ERCOT may, at its discretion, require the GE to submit a new GINR for significant capacity decreases or capacity increases of less than 20%, particularly if other changes to the request are also made, such as changes to the in-service date.  ERCOT’s determination of whether new studies are needed in no way affects the ongoing obligations of the GE and TSP to comply with NERC Standards, and ERCOT Protocols and Operating Guides.

The obligation to maintain the RARF with the most up-to-date design information and to notify ERCOT and the TSP of such changes continues even after an interconnection agreement is signed.  If ERCOT reasonably believes that the changes might affect the reliable operation of the ERCOT System, then the Resource may not be allowed to connect to the ERCOT System until studies can be completed to evaluate the effect of the changes.  If these additional studies show a negative impact on the ERCOT System, the Resource may not be allowed to connect until these negative impacts are rectified.

In addition, the GE shall notify ERCOT of the status of all applicable air permits with the initial interconnection application. The GE shall provide status updates to ERCOT and the TSP when a permit for the project has been issued by the Texas Commission on Environmental Quality (TCEQ). The GE shall also notify ERCOT if permits delay the FIS as well as when it has given the TSP the notice to proceed with the FIS.  The GE has an on-going obligation to provide timely updates to ERCOT and the TSP regarding changes to any information submitted as part of the generator interconnection or change process.

# STUDY PROCESSES AND PROCEDURES

## Security Screening Study

For each proposed generation interconnection or change project, ERCOT Staff will conduct a steady-state security screening study (including power flow and transfer studies) based on the expected in-service year to identify potential generation dispatch limitations based on the site proposed by the GE.  The security screening study is a high level review of the project and generally includes a number of initial assumptions from both ERCOT and the GE.  In accordance with PUCT Substantive Rule §25.198 (Initiating Transmission Service), ERCOT will establish the scope of the security screening study, not the GE.

The results of this study will provide an indication of the level at which the generator can expect to operate simultaneously with other known generation in the area before significant transmission additions or enhancements may be required.  During the course of this study, ERCOT Staff may consult with the affected TSP(s), if needed, to ensure the most efficient means of assuring the feasibility of transmission service is identified and examined.

During the security screening study phase of the interconnection or change process, and in accordance with the ERCOT Protocols, all data, documents, and other information required by ERCOT from a GE related to a request for generation interconnection or change are considered “protected information” to the extent that such information is not otherwise publicly available.  As a result, ERCOT Staff shall not publicly release any of the “protected” data, documents, or other information during the screening study phase except to TSPs.  Information about generation interconnections or changes in the security screening study phase will only be released publicly in aggregated amounts.

Upon completion of the security screening study, ERCOT Staff will present the GE with a preliminary report indicating future transmission additions or enhancements that may be required to obtain the full transfer of the proposed new or modified generation at the specified in-service year.  ERCOT will also inform the GE about any additional transmission system improvements estimated to be required for the continued security and reliability of the ERCOT system.  This report does not imply any commitment by ERCOT or any TSP to recommend or construct these transmission additions or enhancements.

Following the presentation of the security screening study results, the GE must determine whether it wants to continue the interconnection or change process by formally requesting a full interconnection study or to withdraw its GINR.  Should the GE decide to go forward with the project represented by this unique project number, the GE must notify ERCOT in writing within 180 calendar days of its desire to pursue a Full Interconnection Study.  ERCOT Staff will notify the TSP(s) and will begin initiation and coordination of the full interconnection study only after receiving this notification from the GE.

Unless ERCOT receives notice from the GE of its decision to go forward with the proposed project, ERCOT will not initiate a full interconnection study.  Such notice must be received in writing by ERCOT within 180 calendar days following completion of the security screening study.

Should the GE decline to notify ERCOT of its intent to initiate a full interconnection study within the 180 calendar days, ERCOT will consider the interconnection or change request cancelled and no longer valid.  Subsequently, should the GE wish to proceed after the initial 180-day period,  ERCOT will consider the original security screening study invalid and the process will begin again starting with a new GINR for a security screening study and payment of the appropriate fee.  The GE will also be required to provide to ERCOT any updates or changes in the project’s data.

## Full Interconnection Study

A Full Interconnection Study (FIS) consists of the set of steady-state, dynamic, short-circuit, and facility studies that are necessary to determine any facilities that are required to reliably interconnect new or modified generation to the ERCOT System.  The FIS is not intended to determine the deliverability of power from the plant to market or the facilities required to ensure that the plant does not experience any congestion-related curtailment.  To initiate the FIS, the GE must notify ERCOT in writing of its desire to pursue a FIS within 180 calendar days of the completion of its Security Screening Study.  The GE must also provide the appropriate stability modeling fee and proof of site control.

The GE can decide to request a FIS at any time after the initial GINR Application is deemed complete by ERCOT and before the completion of the Security Screening Study.  Requesting both studies at the same time may shorten the overall time to complete the generation interconnection process due to overlap of work on both studies.

### TSP Communication

A confidential email list, known as the Transmission Owner Generation Interconnection email list, will be set up to facilitate communication of confidential generation interconnection-related information among TSP(s) and ERCOT Staff.  Membership to this email list will be limited to ERCOT Staff and appropriate TSP personnel.

### Full Interconnection Study Process Overview

Within five (5) business days of receiving notice to proceed with a FIS, proof of site control and correct fee(s) from the GE, ERCOT will designate a TSP to lead the FIS and contact that TSP to schedule a FIS scope meeting.   ERCOT will select the lead TSP based upon its preliminary analysis with respect to the most likely point of interconnection.   For GEs that have previously developed generation projects in ERCOT with a particular TSP, the FIS scope meeting may be skipped if the GE, ERCOT, and the TSP(s) agree to do so.  In these cases the timeline for the GE and TSP to reach agreement on the FIS scope will start on the date the TSP(s) was notified of the GEs decision to proceed with a FIS.

At the same time ERCOT will send notification of the project FIS to all other TSP(s) via the confidential Transmission Owner Generation Interconnection email list.  It is the responsibility of each TSP to determine if the proposed project would have a material impact on their transmission facilities and to what extent they should participate in the FIS.  Each TSP desiring to participate in the FIS should notify the lead TSP.  The lead TSP will have the responsibility to involve all other TSP(s) that have expressed an interest in the FIS as appropriate for their expressed level of involvement to the extent that such involvement is reasonable.

At the FIS scope meeting the GE will present the proposed interconnection or change request and ERCOT will review the results of the security screening study.  The lead TSP will facilitate a general discussion of the preliminary study scope of work for the FIS.

The GE and the TSP(s) must reach agreement on the FIS scope within sixty (60) calendar days of the FIS scope meeting.  The assistance of more than one TSP may be required in areas where transmission facilities are provided by multiple TSPs.  In these cases it may be necessary for the GE to execute study agreements with multiple TSPs

The FIS scope agreement must include all assumptions, timetables, study cost estimates and payment schedules, and the determination of all requirements for interconnection.  The GE and the TSP(s) have flexibility in reaching agreement on the scope of the FIS, as long as the scope includes at least all studies needed to meet the requirements of this Procedure.  The GE and the TSP(s) shall consider the ERCOT security screening study and other preliminary studies and documents provided by the GE when developing the FIS scope.  The FIS can be divided into several distinct study phases such that notice to proceed from the GE is required before starting each phase.

The TSP(s) shall send the FIS scope to the confidential Transmission Owner Generation Interconnection email list for review and comment by ERCOT and other TSP(s).  Comments must be made within ten (10) business days.

If the GE can not agree to the FIS study scope within the 60-day period, ERCOT will attempt to mediate an agreement but if unsuccessful will consider whether the GE’s interconnection or change request should be terminated.  If the request is terminated, and if the GE subsequently determines to move forward with the interconnection, ERCOT shall require the GE to begin the interconnection process again, including a new security screening study and payment of the appropriate fee(s).

### Full Interconnection Study Elements

The FIS consists of a series of distinct study elements.  Some of the elements may or may not be necessary for the TSP(s) to undertake and complete depending upon the provisions of the interconnection study scope agreement.  The primary purpose of the FIS is to determine the most effective and efficient manner in which to satisfy the desire of the GE’s interconnection or change request while continuing to maintain the reliability of the ERCOT System by meeting all NERC Reliability Standards, ERCOT Protocols and Operating Guides that would be affected by the interconnection and operation of the proposed generation.  The scenarios and base cases being used for these studies to determine potential transmission limitations will be documented in the FIS study scope.

Each generation resource that requires a separate physical transmission interconnection will be treated as an individual study to be analyzed separately from all other such requests unless otherwise agreed to by the GE in the interconnection study scope agreement

The FIS process includes developing and analyzing various computer model simulations of the existing and proposed ERCOT generation/transmission system.  The results from these simulations will be utilized by the TSP(s) to determine the impact of the proposed interconnection.

The TSP(s) will also examine normal transmission operations as well as potentially adverse, or contingency, conditions in order to identify and analyze the reliability and effectiveness of various interconnection design alternatives in alleviating or mitigating any undesirable performance of the interconnection under a variety of operating conditions.

In comparing interconnection alternatives, the TSP(s) will consider such information as interconnection cost and construction schedule, impact to short- and long-range reliability, operational flexibility, and compatibility with future transmission plans for each alternative.  The TSP(s) are not bound to only study interconnection alternatives suggested by the GE  The study should include analysis demonstrating the adequate reliability of any temporary interconnection configurations.

The TSP(s) may reserve the right to update the final FIS report in the event that changes occur to the ERCOT grid (i.e. new generation additions not originally considered execute interconnect agreements) after the report is completed and before the interconnect agreement is executed.

All studies undertaken will be performed in compliance with all applicable PUCT Substantive Rules, ERCOT Protocols and Operating Guides, NERC Reliability Standards, good utility practice, and the guidelines below unless otherwise directed by ERCOT Staff.

Steady-State Analysis.   The steady-state interconnection study base case shall be created from the most recently approved ERCOT Steady-State Working Group (SSWG) base case.  TSP(s) or ERCOT Staff may, at their discretion, remove any future (currently non-existing) transmission facility from the steady-state interconnection study base case that may significantly affect the interconnection study results and has not already undergone appropriate RPG review.  In addition, ERCOT Staff, and TSP(s) may request that generation resources proposed in other prior GINRs that have already been made public be included in the steady-state interconnection study base case if deemed appropriate.  ERCOT Staff may request a list of the interconnection requests included in the FIS by the TSP(s).

Using the SSWG study base case, the TSP(s) shall perform contingency analyses as required by the NERC Reliability Standards, ERCOT Protocols and Operating Guides and identify any additional transmission facilities that may be necessary to ensure that expected system performance conforms to these standards.  All facilities necessary to reliably interconnect the proposed generation will be determined and clearly identified in the report for this part of the FIS.  Any other facility that cannot be constructed or otherwise completed in time to accommodate the initial commercial operations date of the generation will be identified and communicated to the GE along with any likely limitations of generation output that may result.

Loss-of-generation analyses shall assume that the lost generation will be replaced from all remaining ERCOT units in proportion to their nominal capacity (i.e., inertial response) and respecting generation limits.

The lead TSP is responsible for completing an analysis of any contingency events or outages anticipated to result in a violation of the NERC Reliability Standards, ERCOT Protocols and Operating Guides, regardless of which TSP owns the facilities involved.  The results of this analysis will be shared with those TSP(s) that have facilities involved in planning criteria violations and they will be responsible for attempting to verify the validity of the anticipated violations.

System Protection (Short-Circuit) Analysis.  The FIS scope agreement will specify locations where available short-circuit fault duty will be identified, calculated, and documented.  If any of the required generator interconnect-associated transmission system improvements result in transmission facility (ies) violating the TSP’s short-circuit criteria, the TSP shall plan to provide facilities to address such violations.  The TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and later for protective relay setting purposes.

Dynamic and Transient Stability (Unit Stability, Voltage, Subsynchronous Resonance) Analysis.  At the discretion of the TSP(s) or ERCOT Staff, transient stability studies will be performed  if necessary to meet NERC Reliability Standards, ERCOT Protocols and Operating Guides applicable for the generator and for the ERCOT System. If the TSP(s) in charge of these stability studies decides not to conduct the studies, the TSP(s)  must provide a written justification in lieu of the study report.  When performing such studies, all existing or publicly committed generation in the area of study will normally be represented at full net output or better model (some combined cycle units or coal plants might be modeled at full gross output together with its auxiliary load).  Any resulting increase in generation will be balanced as addressed in the FIS scope agreement.

Stability study base cases shall be formed from the latest available approved ERCOT SSWG base cases consistent with the most recently approved ERCOT Dynamics Working Group (DWG) stability data base. The initial transmission configuration in the area of study included in a stability study base case shall be identical to that used in the steady-state studies of the same period.  Any previously identified transmission improvements that will not be in service prior to the in-service date of the generation under study shall not be included in the stability study base case.

Transient stability studies will analyze the performance of the proposed generation interconnection and the ERCOT System in terms of angular stability, voltage stability and excessive frequency excursions.  Additional studies may include small signal stability, subsynchronous resonance or critical clearing time analyses where the number of cycles for which a transmission line can sustain a fault without causing loss of synchronism of any of the generators is compared to the response of the protection systems.  Such studies should incorporate reasonable conservative assumptions regarding plant operating conditions.  Proposed analyses shall be identified and defined in the full interconnection study scope agreement.

All stability studies shall be performed in accordance with ERCOT’s Planning Criteria, and the results shall identify any additional transmission facility(ies) or other action(s) necessary to ensure conformance to that standard.

Facility Study.  At a minimum, the facility study provides complete details and estimated cost of the facility requirements for the direct interconnection of the proposed generation project to the TSP.

Results of the facility study will provide conceptual design descriptions, construction milestones, and detailed cost estimates for all direct interconnection-related transmission and substation facilities proposed to be installed in accordance with the findings and recommendations of the FIS.

### Economic Study

ERCOT Staff is required to perform an independent economic analysis of the transmission projects that are identified through this process as being needed for the direct connection of the proposed generation facility and which are expected to cost more than $25 million. This economic analysis is performed only for informational purposes; as such, no ERCOT endorsement will be provided.

At the point in the FIS that the lead TSP determines that it will recommend direct interconnection facilities for the proposed generation project which have an estimated cost expected to exceed $25 million, the lead TSP will communicate this finding, within 10 business days of such determination, to ERCOT Staff and other TSP(s) via the confidential Transmission Owner Generation Interconnection email list.  This communication will include all available information upon which that finding is based, including but not limited to: a description of the direct interconnection facilities; information necessary to modify a powerflow case to include those facilities (idev or similar format); any information obtained from the generation project that would be helpful in modeling the generator for the study; and, the estimated cost of the facilities.  ERCOT will request, and the GE will provide, information necessary to represent the characteristics of the proposed generation facility needed for the economic study.

ERCOT will generally complete this economic study within 90 calendar days, and will inform the TSP(s) and GE if additional time is required.  ERCOT will provide the results of the economic study to the TSP(s)  via the confidential Transmission Owner Generation Interconnection email list and the GE when it is complete.

### FIS Study Report and Follow-up

The TSP(s) will present a preliminary report of their findings and recommendations for each of the study elements to ERCOT Staff and other TSP(s) via the confidential Transmission Owner Generation Interconnection email list and to the GE.  Any questions, comments, proposed revisions, or clarifications by any party shall be made in writing to the TSP(s) within ten (10) business days after the issuance of each study report, which may cover one or more study elements. After considering the information received from ERCOT and other TSPs, the study element(s) report will be deemed complete and a final report shall be provided to the GE, ERCOT, and all TSPs.   The ten 10 business day review period will be used by the ERCOT Staff to determine if any transmission upgrades proposed and clearly identified in the Steady-State Study Report need to be submitted to the RPG review process.  Refer to Section 25 of the ERCOT Protocols for more information on the process to review transmission upgrades that are unrelated to the direct connection of new or modified generation.

Upon the transmittal of the last study element report, the TSP issuing such report will indicate that such study element report is the final report to be issued associated with the entire FIS.  At the end of the ten 10 business day review period following the issuance of the final FIS element report, the FIS will be deemed complete and the GE and TSP will have the specified amount of time to complete an interconnection agreement as detailed in this document. If an economic study of the direct interconnection facilities is required, pursuant to Section 3.2.4, Economic Study, and has not yet been completed, the GE and TSP may mutually decide whether that study must be completed before the FIS is deemed complete.

Should the GE wish to proceed with the proposed generation interconnection, the GE must execute an Interconnection Agreement with the respective TSP within 180 calendar days following the completion of the FIS (includes all major study element reports).

If, during the time after this FIS is completed and before the interconnection agreement is executed changes occur that substantially differ from the assumptions used for the FIS, ERCOT and the TSP(s) shall determine the impact of the changes on the results of the FIS.  All changes should be submitted to ERCOT on the RARF for a change comparison. If the proposed direct interconnection is negatively affected by the changes, the TSP(s) will work with the GE on a refresh of the FIS.

### Proof of Site Control

Before ERCOT will proceed with the initiation of a FIS, the GE must submit to ERCOT proof of site control.  To establish proof of site control, the GE must demonstrate through an affiliated company, through a trustee, or directly in its name that:

- The GE is the owner in fee simple of the real property to be utilized by the facilities for which any new generation interconnection is sought, or

- The GE holds a valid written leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought, or

- The GE holds a valid written option to purchase or obtain a leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought, or

- The GE holds a duly executed written contract to purchase or obtain a leasehold interest in the real property to be utilized by the facilities for which new generation interconnection is sought.

The GE must notify ERCOT of any substantive change in status of the arrangement used to demonstrate site control.

The GE must maintain site control throughout the duration of the FIS and until execution of an Interconnection Agreement.  Otherwise, ERCOT will consider the GINR withdrawn as of the date of the loss of site control unless the applicant can show within 30 calendar days that it has re-established site control or has established control of a new site that would not result in any material modification of any interconnection study requested under the current application.

### Confidentiality

Once a FIS is requested by the GE, in accordance with Protocol 1.3.1.2, the following information about the potential project will become public:

1.	INR Number

2.	Facility nameplate capacity

3.	Anticipated in-service date

4.	Facility fuel type

5.	County where facility located

All other data, documents or other information regarding the GINR (including the identity of the GE) will remain protected information until ERCOT receives written notice from the GE that this information may be made public or until a Standard Generation Interconnection Agreement (SGIA) is executed.  Since the FIS scope agreement contains possibly confidential cost estimates and represents an agreement between the GE and the lead TSP, it will remain as protected information and will not be released to parties other than those who are members of the confidential Transmission Owner Generation Interconnection email list except as required in a court of law or by regulatory authorities having jurisdiction.  Once classified as a public project through one of these steps, ERCOT will post the project description, all FIS reports, the results of the economic analysis of direct interconnection facilities costing over $25 million, and any information developed throughout the interconnection study process about transmission improvement projects that may be submitted for RPG review as a result of the new generation on the ERCOT website.

The lead TSP will notify the RPG email list within ten (10) business days of the signing of an Interconnection Agreement where the cost of the direct interconnection facilities is greater than $25 million.

## Interconnection Agreement

### Standard Generation Interconnection Agreement

Should the GE decide to proceed with the construction and completion of the proposed generation project and interconnection within the 180-day period following the completion of the FIS, they will execute an interconnection agreement with their respective TSP as a condition for obtaining transmission service.  This is in accordance with PUCT Substantive Rule §25.195 (Terms and Conditions for Transmission Service).  The GE and the TSP shall use the PUCT’s Standard Generation Interconnection Agreement (SGIA).   A template of the SGIA can be found on the ERCOT website.

Before an SGIA is signed, all studies included in the FIS scope must be completed, unless mutually agreed by the GE and the TSP.  The GE and TSP must meet and maintain compliance with all NERC Reliability Standards, ERCOT Protocols and Operating Guides requirements related to the interconnection by the time that the generation facility is energized.

While ERCOT is the proper entity for a GE to request a generation interconnection or change process, the actual negotiation of the interconnection agreement shall be conducted directly between the GE and the TSP.  ERCOT is not a party to the interconnection agreement and will not participate in these negotiations, nor will ERCOT arrange interconnection agreements.

A copy of the signed SGIA must be transmitted to ERCOT by the TSP within ten 10 business days of the execution of the Agreement.  The TSP is also required to submit this Agreement to the PUCT within 30 days of its execution.  The GE should also provide ERCOT with the status of its air permits, when it receives a permit for its project, and when it gives the TSP the notice to proceed.

### Other Arrangements for Transmission Service

In certain situations, the GE and the TSP may make alternative arrangements under which the TSP agrees to begin design or construction of facilities prior to the execution of the interconnection agreement.  In other instances, a notice to proceed may not be issued until some time after the interconnection agreement is signed.  Documentation of any alternative arrangements of this type should be transmitted to ERCOT by the TSP within ten 10 business days of execution of such agreement.

### Provisions for Municipals and Cooperatives

While all other provisions of this interconnection process shall apply, municipal utilities or generation and transmission cooperatives developing generation projects that will interconnect to their own transmission systems are exempt from the requirement for an executed interconnection agreement.  A letter from a duly authorized official from the municipal utility or cooperative confirming the entity’s intent to construct and operate the generation project will be deemed by ERCOT to be sufficient as a public commitment by the municipal utility or cooperative and will have the same impact as an interconnection agreement for all purposes.

Municipal utility or cooperative generation projects that are proposed to interconnect with the facilities of a different TSP, other than the municipal utility or cooperative that is developing the generation project, will be required to execute an interconnection agreement as discussed in this document.

4,4 INTERCONNECTION DATA, FEES, AND TIMETABLES

## Generation Plant Data Requirements

The GE is required to submit the most current “actual” facility information (generation, substation, and transmission/subtransmission if applicable) or best available “expected” performance data regarding the physical and electrical characteristics of its proposed facilities (in sufficient detail to provide a basis for modeling) to the point of interconnection with a TSP with its initial GINR Application.

Failure to supply the required data will result in delays in ERCOT processing the interconnection application and studies.  Recommendations resulting from these studies that are based on outdated, false, or bad data may adversely affect the safety and reliability of the ERCOT system and can result in damage to generation or transmission equipment.  Ongoing data updates and reviews are necessary throughout the interconnection process and service life of the generating plant to ensure the adequacy, reliability, and safety of the ERCOT system is maintained over the long term as soon as such updates become available. It must be realized by current and future owners/operators of the generating plant that ERCOT protocols and NERC standards require timely data updates and submission.  Failure to comply could result in financial penalties for entities not in compliance.

In an effort to produce the best available security screening study and FIS, ERCOT suggests that GEs begin collecting all appropriate engineering and equipment data from manufacturers as soon as the GE selects its major equipment for the proposed project.  While the following list is not intended to supersede the GE’s ongoing obligation to provide and update all information associated with the proposed facility as soon as the information is known, the following checklist is intended to list the minimum data and information to be provided to ERCOT at each step of the process:

### Application and Security Screening Study

- Generation entity information sheet (Appendix A)

- Generation interconnection screening study request data form (Appendix B)

### Full Interconnection Study

- Updates to above information

- Applicable information required for interconnection studies as described in the RARF instructions in all tabs applicable to the resource type within the RARF Excel spreadsheet located in the Resource Asset Registration Forms zip file located at http://www.ercot.com/gridinfo/generation/index.

- Provision of the appropriate dynamic model for the facility.  Some standard dynamic model forms are available within the Resource Modification Forms zip file located at http://www.ercot.com/gridinfo/generation/index

- dynmodel_StandardGenerator011508.zip has forms for generator, exciter, governor, power system stabilizer, other models for standard generators.

- dynmodel_CombinedCycleGovernor.zip has forms for the governor models of Combined Cycle units

- dynmodel_WindTurbine011609.doc has information about existing wind turbine models at ERCOT.

- If alternative models are required to appropriately represent the proposed generating facility, that alternative model may be provided by the GE, subject to verification by the lead TSP and ERCOT.

- In order to perform stability (transient and voltage) analyses, the GE shall provide unit stability information and data to the TSP(s) and ERCOT.  See the ERCOT Dynamics Working Group Procedural Manual for more detail and GE dynamics data requirements.

Data submitted for transient stability models shall be compatible with ERCOT standard models (Siemens/PTI PSS/E and Powertech Labs Inc TSAT, VSAT and SSAT).  If there is no compatible model(s), the GE is required to work with a consultant or software vendor to develop and supply accurate/appropriate models along with other associated data.  These models shall be incorporated into the standard model libraries of both software packages.  It is recommended that generation owners and developers encourage manufacturers and software vendors to work together to develop and maintain these important models.

### Prior to Start of Construction

- Any significant design changes in the generator(s) or main power transformer(s) to ensure compatibility with the existing transmission system.

### Prior to Commercial Service

- Registration and official RARF submittal

- Updates to RARF information based on “as-built” or “as-tested” data in all cases

- Proof of meeting ERCOT requirements (reactive, low-voltage ride-through standards, stability models, PSS)

### During Continuing Operations

The GE shall provide ERCOT and the TSP with any equipment data changes which result from equipment replacement, repair, or adjustment.  Unless otherwise required in the ERCOT Protocols or Operating Guides, the GE shall provide such data to ERCOT and the TSP no later than 60 days prior to the date of the actual change in equipment characteristics or during annual data update filings whichever occurs first.  This requirement shall also apply to all future owners throughout the service life of the project/plant.

## Interconnection Study Fees

PUCT Substantive Rule §25.198 (Initiating Transmission Service) states in part that the customer requesting transmission service shall be responsible for all costs associated with the completion of the security screening study and the FIS.

### Security Screening Study Fee

The ERCOT security screening study fee is a non-refundable fee ranging from $1,000 to $5,000 depending on the additional installed capacity associated with each specific interconnection request.  ERCOT has determined that basing this fee on additional installed capacity is reasonable because additional installed capacity generally determines the amount of work necessary to complete the study.  The appropriate security screening study fee must be remitted for each generation interconnection request (i.e., each individual interconnection location, in-service date, and additional plant capacity at this specific interconnection location) at the time the application is submitted to ERCOT.   The check should be made payable to Electric Reliability Council of Texas, Inc.

| Total Plant Capacity, MW | Screening Study Fee |
| --- | --- |
| 10 to 74 | $1,000 |
| 75 to 149 | $2,000 |
| 150 to 249 | $3,000 |
| 250 to 499 | $4,000 |
| 500 or greater | $5,000 |

### Stability Modeling Fee

The ERCOT stability modeling fee is a non-refundable stability modeling fee of $15 per megawatt of additional installed capacity and is paid directly to ERCOT when a FIS is requested.  This fee will reimburse ERCOT for the development of stability software models for each proposed generation unit and allow for continually updating current models as new equipment changes are made.  The check should be made payable to Electric Reliability Council of Texas, Inc.  Payment of the stability modeling fee to ERCOT does not release the GE from their obligation to provide ERCOT accurate and appropriate stability software models and data (including load) for each of their proposed generation plants.

### Full Interconnection Study Fee/Cost

The FIS fee/cost is paid directly to the TSP(s) completing the studies associated with the FIS.  The fee/cost will be agreed on and specified in the study scope agreement. The TSP(s) will directly invoice the GE for the reasonable costs associated with undertaking and completing the FIS.

ERCOT recommends that the GE and the TSP provide for a payment methodology and cancellation provision in the FIS scope agreement.  If the GE cancels the generating project during the term of the FIS, the GE is required to immediately notify ERCOT and the lead TSP.  The lead TSP should immediately notify any other TSPs that may be participating in the study, via the confidential Transmission Owner Generation Interconnection email list.  The GE is responsible for all costs associated with any work performed or non-cancelable commitments made prior to notifying ERCOT and the TSP(s) of the termination date of the project.  ERCOT highly recommends the TSP(s) receive the study fee before proceeding with work.

## Interconnection Process Timetables

PUCT Substantive Rule §25.198 (Initiating Transmission Service) provides deadlines for ERCOT and TSP(s) to complete and report on the required interconnection studies provided that the GE submits all required data and appropriate fee(s).  Therefore, it is vital that the GE ensure that ERCOT Staff and the TSP(s) performing these studies receive all required data in order to establish reasonable study models and assumptions that provide meaningful results and recommendations for interconnecting the proposed generating project.

Because the FIS is generally the “critical” path item in the generation interconnection process, ERCOT recommends that a timetable for the FIS be developed and included in the study scope agreement.  In addition, major improvements to the transmission system resulting from interconnection requests should be identified as early in the process as possible so project validity can be considered before the parties go forward with extensive interconnection studies.  Once the FIS is underway, the parties may determine that an adjustment to the original estimated completion date is necessary.  Should this schedule adjustment become necessary, the parties are to provide notice to ERCOT and the TSP(s) as soon as practicable, indicating the revised expected completion date.

The following timetable complies with PUCT Substantive Rule §25.198 (Initiating Transmission Service).   It is intended to serve as a guideline only and the times stated are not requirements unless stated elsewhere in this document. If the number of days shown is less than 30, these are business days; if 30 days and over, these are calendar days.

| TASK | Responsible Entity | Time Required to Complete (Days)) |
| --- | --- | --- |
| Acknowledgement of Generation Interconnection Request Application | ERCOT | 1 to 10 |
| Notification of Additional Information Needed to Complete Application | ERCOT | 1 to 15 |
| Perform Security Screening Study (after application deemed complete) | ERCOT | 10 to 90 |
| Decision to Pursue Full Interconnection Study (following issuance of Screening Study by ERCOT) | GE | up to 180 |
| Develop Scope Agreement for Full Interconnection Study (following GE’s notification to ERCOT of desire for Full Interconnection Study and remittance of appropriate fees) | ERCOT, TSP(s), GE | up to 60 |
| Perform Full Interconnection Study (following agreement on scope) | TSP(s) | 40 to 300 |
| Steady-State and Transfer Analysis |  | 10 to 90 |
| System Protection Analysis (following Steady State Analysis) |  | 10 to 30 |
| Dynamic and Transient Stability Analysis (following System Protection Study) |  | 10 to 90 |
| Facility Study |  | 10 to 90 |
| Study Report Review and Acceptance (following issuance of Full Interconnection Study) | ERCOT, TSP(s), GE | 10 to 15 |
| Negotiate and Execute Interconnection Agreement (following acceptance of Full Interconnection Study) | TSP and GE | 180 |

## GENERAL AND TECHNICAL STANDARDS

In addition to requirements under the NERC Reliability Standards, ERCOT Protocols and Operating Guides contain provisions that apply to generation interconnections.  As of the effective date of this Procedure, such provisions include, but are not necessarily limited to:

- Protocol 1.3.1

- Protocol 12.2 and 12.3

- Protocol 6.5.7

- Protocol 6.7.6

- Protocol 6.10.3

- Operating Guide 2.2.4

- Operating Guide 3.1.4

- Operating Guide 7.2.2

- Operations Procedure Steady-State Voltage Control Procedures

- Nodal Operating Guide 2.2.6 Power System Stabilizers

### Transformer Tap Position

The GE will contact the TSP providing the interconnection before the main power transformers are placed into service and will work with the TSP to select the tap position on the main power transformers, and the GE will confirm the use of this tap position with the TSP and ERCOT.  The main power transformer will be considered the step-up to transmission level voltage of the interconnection.

# APPENDIX A

GENERATION ENTITY INFORMATION SHEET

## GENERATION ENTITY INFORMATION SHEET

PLEASE PRINT CLEARLY – FORM MUST BE SIGNED AND SUBMITTED WITH REQUEST

Transmission Customer (Generating Entity):

Contact Person:

Title:

Company:

Mailing Address:

City:  		State:		ZIP:

Company Internal Mail Code(s):

Telephone Number:	(      )	Facsimile (FAX) Number:	(       )

Internet email Address:

Requested Transmission Energization Date (MM/DD/YYYY):

Generation In-Service (MM/DD/YYYY): Start  		through

____________________________________________ (generating entity) is, or will be upon commencement of service, an eligible customer.  An eligible customer is any of the following: the transmission provider (for all uses of its transmission system) and any electric utility, federal power marketing agency, exempt wholesale generator, qualifying facility, or power marketer.  An eligible customer may designate an agent to represent it in arranging for interconnection.

Accurate/appropriate information and test data about generator step-up transformers, all generator data including data for stability studies (transient, voltage, etc.) and sub-synchronous resonance data will be provided to ERCOT and interconnected TSP before the generation goes into commercial operation.  I understand that all of this data will become public and added to the ERCOT databases (including power flow base cases, stability, system protection, Capacity, Demand, and Reserve Report, etc) when an interconnection agreement is signed.  This data shall be reviewed and updated when the plant goes into commercial operation.  In addition, any updates to this information will be provided within 60 days to ERCOT and the TSP as changes or upgrades are made during the life of the plant.  This requirement also applies to all future owners of this project/plant.

The generating entity and any future owners of the plant agree to comply with these data requirements along with all applicable ERCOT and NERC requirements, including, without limitation, those contained in the ERCOT Protocols and ERCOT Operating Guides.  It is understood and agreed that such requirements are subject to change from time to time, and such changes shall automatically become applicable based upon the effective date of the approved change.

Authorized Signature:  		Date:

Name printed or typed:

By:

# APPENDIX B

## GENERATOR INTERCONNECTION REQUEST SCREENING STUDY DATA SHEET

See Excel Spreadsheet titled “Generation Interconnection Data Submission Guide” at http://www.ercot.com/gridinfo/generation/. This file identifies the data in the RARF that needs to be submitted for the Security Screening Study (SS) and Full Interconnection Study (FIS).

- Planning Criteria

  - Reliability criteria (Section 5 of the current operating guides – Rev 0)

  - Evaluate if section 7 (or parts thereof) of Operating Guides dealing with System Protection should be moved to the Planning Guides. (Rev 1 or 2)

  - Economic Criteria(from RPG Charter Rev 1)

  - Requirement for posting TSP Specific Planning Criteria (Rev 1 or 2)

# Planning

## Planning Criteria

### 5.1.1 Introduction

The Electric Reliability Council of Texas (ERCOT) power system consists of those generation and Transmission Facilities (60 kV and higher voltages) which are controlled by individual ERCOT Market Participants and which function as part of an integrated and coordinated power supply network.  Each reference in this document to ERCOT Market Participants includes Generation Resources (GRs), Qualified Scheduling Entities (QSEs), Competitive Retailers (CRs), Transmission/Distribution Service Providers (TDSPs), and other that use the transmission system.

In order to maintain reliable operation of the ERCOT power system, it is necessary that all ERCOT Market Participants observe and subscribe to certain minimum planning criteria. The criteria set forth herein, combined with the NERC Planning and Reliability Standards, constitute these minimum-planning criteria. Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, because ERCOT recognizes that events more severe than those outlined in these criteria could cause separation, other tests may also be performed if necessary for information purposes.

The complexity and uncertainty inherent in the planning and operation of the ERCOT power system make exhaustive testing impracticable; therefore, to gain maximum benefit from the limited number of tests which are performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

It is the responsibility of each ERCOT TDSP to perform tests appropriate to ensure the reliability of its own Transmission Facilities, and to recommend for further study by the ERCOT System Planning Function (SPF) or the ERCOT Reliability Operations Subcommittee (ROS) tests, which examine effects of importance to multiple ERCOT TDSPs or the ERCOT power system.  Upon consideration of such recommendations, the ERCOT SPF and the ERCOT ROS shall coordinate the performance of tests as necessary to assess the reliability of the planned ERCOT power system.

ERCOT (Regional Planning Groups or Transmission Planning) shall determine and demonstrate the need for any static and/or dynamic Reactive Power capability in excess of the explicit requirements of the Protocols and Operating Guide that is necessary to ensure compliance with the ERCOT Planning Criteria, and ERCOT (Transmission Planning) shall establish specific TSP responsibility for any associated facility additions.

The ERCOT SPF, in cooperation with the ERCOT Compliance Office, will review the ERCOT Planning Criteria every three years to ensure it meets the requirements in the NERC Planning and Reliability Standards.  The ERCOT SPF, in cooperation with the ERCOT Compliance Office, will periodically review the planning criteria, procedures, and practices of individual ERCOT TDSPs to insure consistency with NERC and ERCOT criteria.

### 5.1.2	Load Forecasts

Each ERCOT DSP directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual Load forecasts to the ERCOT SPF as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures. For each substation not owned by either a TSP or a DSP, the owner shall provide a substation Load forecast to the directly-connected TDSP sufficient to allow it to adequately include that substation in its ALDR response.

### 5.1.3	Resource Capability

ERCOT will periodically determine the minimum reserve margin required to ensure the adequacy of installed generation capability in ERCOT. ERCOT or the Public Utility Commission of Texas may also approve specific Market Participant requirements to ensure that the required minimum reserve margin is maintained.

The ERCOT SPF maintains a database containing existing and proposed generating capability historical and projected values for demand and energy; and proposed major transmission system additions.  This database is updated periodically and the Capacity Demand Reserve (CDR) Working Paper is produced annually.

### 5.1.4	Transmission Reliability Testing

The interconnection philosophy of ERCOT is to minimize loss of Load by remaining interconnected.  Interconnected system planning will include steady state and dynamic simulated testing by ERCOT TDSPs and the ERCOT SPF to represent specific occurrences for each type of contingency specified below or listed in Table I of the NERC Planning and Reliability Standards. Table I of the NERC Planning and Reliability Standards is included in this document for reference. The term “generating unit”, as used in Table I below, for the purpose of reliability testing shall be defined as the largest single generating unit operating at a given voltage level at each plant location.  In the case of a Combined Cycle Facility, the term “generating unit”, as used in Table I below, shall be defined as the total generating capacity of the entire train.   Also included are ‘ERCOT Clarifications and Definitions’ which are applicable to testing for NERC Planning Standards contingency types C and D.

The contingency tests will be performed for reasonable variations of Load level, generation schedules, planned transmission line Maintenance Outages, and anticipated power transfers.  At a minimum, this should include projected loads for the upcoming summer and winter seasons and a five-year planning horizon.  The ERCOT TDSPs involved should plan to resolve any unacceptable test results through the provision of Transmission Facilities, the temporary alteration of operating procedures (Remedial Action Plans), temporary Special Protection Systems, or other means as appropriate.

While the requirements listed in Table I address most ERCOT planning concerns, tests will also be conducted to ensure that the planned system conforms to the following additional requirements:

1.	The contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans), such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

2.	With any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the transmission element, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans) such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

With regard to (2) above, the term “single generating unit” experiencing a forced outage shall be defined as the largest single generating unit operating at a given voltage level at each plant location. In the case of a Combined Cycle Facility, a “single generating unit” experiencing a forced outage shall be defined as the entire train unless the combustion turbine and the steam turbine can operate separately, as stated in the Generation Resource Asset Registration form in the section labeled modes of operations. ERCOT will not unreasonably withhold acceptance of defining the Combined Cycle Facility with different modes of operations per the information provided in the Generation Resource Asset Registration and provided by trend analysis of historical forced outage data.

ERCOT will post the contingency unit list on MIS.

3.	Voltage stability margin shall be sufficient to maintain post-transient voltage stability within a defined importing (Load) area under the following study conditions:

- Peak Load conditions, with import to the area increased by five percent (5%) of the forecasted area Load, and NERC Category A or B operating conditions (see NERC Table I in ERCOT Planning Criteria); and

- Peak Load conditions, with import to the area increased by two and one half percent (2.5%) of the forecasted area Load, and NERC Category C operating conditions.

The ERCOT SPF is responsible for gathering Load data, for use in the ERCOT Load flow cases via the ALDR.  The ERCOT ROS coordinates with the ERCOT SPF in the performance of steady state and dynamic simulation testing of the bulk power system to determine the impact on the planned system of occurrences of the types of contingencies listed in the NERC Planning Standards.  The Steady State Working Group (SSWG), Dynamics Working Group (DWG) and System Protection Working Group (SPWG) work with the ERCOT SPF to create databases and perform tests as outlined in these criteria.

These databases created by the ERCOT ROS Working Groups are available for use by ERCOT Market Participants.  It is the responsibility of the individual ERCOT TDSPs to use these databases to perform steady state and dynamic tests appropriate to evaluate the compliance of their Transmission Facilities with the ERCOT Planning Criteria and to recommend, for further study by ERCOT, tests, which examine effects of importance to multiple ERCOT TDSPs or the ERCOT bulk power system.  Such tests are discussed by the ERCOT ROS and the ERCOT SPF and are subsequently performed under the direction of the ERCOT SPF or the ERCOT ROS as appropriate.  The individual TDSPs affected by identified issues will pursue appropriate solutions.

### 5.1.5	Reports Of Testing

The ERCOT SPF annually directs the preparation of the section of the EIA-411 Report requested by the Department of Energy which addresses the adequacy of the ERCOT bulk power system as well as input to various NERC reports. Studies performed by ERCOT and comments by the individual TDSPs regarding tests that they have performed provide the basis for statements concerning the adequacy of the planned ERCOT System.

### 5.1.6	System Modeling Information

Information on existing and future ERCOT System components and topology is necessary for ERCOT to create databases and perform tests as outlined in these criteria.  To ensure that such information is made available to ERCOT, the following actions by ERCOT Market Participants are required:

1.	Each TDSP, or its designated agent, shall provide accurate modeling information for all ERCOT Transmission Facilities owned or planned by the TDSP.  The information provided shall include, but not be limited to, the following:

a.	Information necessary to represent the TDSP’s Transmission Facilities in any model of the ERCOT Transmission Grid whose creation has been approved by ERCOT, including modeling information detailed in procedures of the SSWG, DWG, and SPWG;

b.	Identification of a designated contact person responsible for providing answers to questions ERCOT may have regarding the information provided; and

c.	TDSP owned or operated Transmission Facility data provided and used to accurately represent a Transmission Facility in a model shall be consistent to the extent practicable with data provided and used to represent that same Transmission Facility in any other model created to represent a time period during which the Transmission Facility is expected to be physically identical. All existing transmission line’s and transformer’s impedances (or equivalent branch circuit impedance) and ratings (Normal and Emergency) shall be identical, to the extent practicable.  If all normally closed breakers and switches are closed and normally open breakers and switches are open in the Network Operations Model, the calculated line flows between substations in the Annual Planning Model shall be consistent (very close), when all models use the same Load magnitude and distribution, generation commitment and Dispatch, and Voltage Profile. The TDSP shall provide an explanation to ERCOT for data inconsistencies.  	Any long-term changes to the reactive capability must be provided by the facility owner to ERCOT, as-planned at least thirty (30) days prior to implementation and as-built no later than thirty (30) days after implementation, as changes or upgrades are made during the life of the Reactive Power facilities.

Further, each TDSP owning or planning Transmission Facilities shall attend the scheduled meetings and otherwise participate in the activities of the SSWG and the SPWG, unless specifically exempted from these activities by ERCOT.

2.	Each Generation Resource (GR), or its designated agent, shall provide accurate modeling information for each existing or publicly-announced ERCOT generating unit for which it is the majority owner. The information provided shall include, but not be limited to, the following:

a.	Information necessary to represent the GR’s generation and interconnection facilities in any model of the ERCOT electrical system whose creation has been approved by ERCOT, including modeling information detailed in procedures of the SSWG, DWG, and SPWG; and

b.	Identification of a designated contact person responsible for providing answers to questions ERCOT may have regarding the information provided.

Typical or representative information may be provided for planned facility additions or modifications, but such information shall be revised using actual design or construction information no later than thirty (30) days after it becomes available.

Table I. Transmission Systems Standards — Normal and Contingency Conditions

| Category | Contingencies |  | System Limits or Impacts |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Initiating Event(s) and Contingency Component(s) | Components Out of Service | Thermal Limits | Voltage Limits | System Stable | Loss of Demand or Curtailed Firm Transfers | Cascadingc Outages |
| A – No Contingencies | All Facilities in Service | None | Normal | Normal | Yes | No | No |
| B – Event resulting in the loss of a single component. | Single Line Ground (SLG) or 3-Phase (3Ø) Fault, with Normal Clearing: 1. Generator 2. Transmission Circuit 3. Transformer Loss of a Component without a Fault. | Single Single Single Single | Applicable Rating a (A/R) A/R A/R A/R | Applicable Rating a (A/R) A/R A/R A/R | Yes Yes Yes Yes | No b No b No b No b | No No No No |
|  | Single Pole Block, Normal Clearing: 4. Single Pole (dc) Line | Single | A/R | A/R | Yes | Nob | No |
| C – Event(s) resulting in the loss of two or more (multiple) components. | SLG Fault, with Normal Clearing: 1. Bus Section 2. Breaker (failure or internal fault) | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
|  | SLG or 3Ø Fault, with Normal Clearing, Manual System Adjustments, followed by another SLG or 3Ø Fault, with Normal Clearing: 3. Category B (B1, B2, B3, or B4) contingency, manual system adjustments, followed by another Category B (B1, B2, B3, or B4) contingency | Multiple | A/R | A/R | Yes | Plannedd | No |
|  | Bipolar Block, with Normal Clearing: 4. Bipolar (dc) Line Fault (non 3Ø), with Normal Clearing: 5. Double Circuit Towerline | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
|  | SLG Fault, with Delayed Clearing: 6. Generator 8. Transformer 7. Transmission Circuit 9. Bus Section | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
| D e – Extreme event resulting in two or more (multiple) components removed or cascading out of service | 3Ø Fault, with Delayed Clearing (stuck breaker or protection system failure): 1. Generator 3. Transformer 2. Transmission Circuit 4. Bus Section 3Ø Fault, with Normal Clearing: 5. Breaker (failure or internal fault) Other: 6. Loss of towerline with three or more circuits 7. All transmission lines on a common right-of way 8. Loss of a substation (one voltage level plus transformers) 9. Loss of a switching station (one voltage level plus transformers) 10. Loss of a all generating units at a station 11. Loss of a large load or major load center 12. Failure of a fully redundant special protection system (or remedial action scheme) to operate when required 13. Operation, partial operation, or misoperation of a fully redundant special protection system (or remedial action scheme) for an event or condition for which it was not intended to operate 14. Impact of severe power swings or oscillations from disturbances in another Regional Council. | Evaluate for risks and consequences.  May involve substantial loss of customer demand and generation in a widespread area or areas.  Portions or all of the interconnected systems may or may not achieve a new, stable operating point.  Evaluation of these events may require joint studies with neighboring systems.  Document measures or procedures to mitigate the extent and effects of such events.  Mitigation or elimination of the risks and consequences of these events shall be at the discretion of the entities responsible for the reliability of the interconnected transmission systems. |  |  |  |  |  |

Footnotes to Table I.

- a)	Applicable rating (A/R) refers to the applicable normal and emergency facility thermal rating or system voltage limit as determined and consistently applied by the system or facility owner.

- b)	Planned or controlled interruption of generators or electric supply to radial customers or some local network customers, connected to or supplied by the faulted component or by the affected area, may occur in certain areas without impacting the overall security of the interconnected transmission systems. To prepare for the next contingency, system adjustments are permitted, including curtailments of contracted firm (non-recallable reserved) electric power transfers.

- c)	Cascading is the uncontrolled successive loss of system elements triggered by an incident at any location. Cascading results in widespread service interruption, which cannot be restrained, from sequentially spreading beyond an area predetermined by appropriate studies.

- d)	Depending on system design and expected system impacts, the controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, or the curtailment of contracted firm (non-recallable reserved) electric power transfers may be necessary to maintain the overall security of the interconnected transmission systems.

- e)	A number of extreme contingencies that are listed under Category D and judged to be critical by the transmission planning entity(ies) will be selected for evaluation. It is not expected that all possible facility outages under each listed contingency of Category D will be evaluated.

### 5.1.7	ERCOT Clarifications and Definitions of NERC Planning Standards Contingency Types C and D

#### 5.1.7.1	Category C

- Initiating Event and Contingency Component Definitions:

"Bus Section" shall be interpreted to mean any section of buswork, which would be isolated by normal relay/breaker operation when faulted.

"Manual System Adjustments" shall be interpreted to include only operator actions which a) would be made not later than 1 hour after clearing of the first fault, b) are made using remote control capability or communications with other operators having such capability, c) include circuit switching, changes in the schedules of generating units operating at clearing of the first fault, and changes in the schedules of other generating units which can contribute within 1 hour, and d) exclude the physical repair or replacement of damaged equipment and the starting of any generating unit which cannot contribute within 1 hour.

- Planned Loss of Demand or Curtailed Firm Transfer Definition:

All load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged (with associated written operating procedures).  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

- Cascading Outage Definition:

Cascading outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

- Implementation Guidelines:

Equipment ratings and permissible voltage levels shall be determined by the facility owner with the concurrence of the ERCOT SPF.

Evaluation of all the possible combination of facility outages under Category C is not required. Each TDSP with bulk transmission facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events and which, in the engineering judgment of the facility owner, the ERCOT SPF or any TDSP, may have unacceptable consequences.

#### 5.1.7.2	Category D:

- Large Load or Major Load Center Definition:

A large load or major load center shall be defined as a large single load or a group of electrically close loads comprising a peak load of between 50 and 500 MW.  Loss of this load or load center will not include any other system elements other than those directly connected to the lost load.

- Evaluation Implementation:

Evaluations of Category D contingencies are not required to be performed annually.  Evaluations should be performed for the following:

- Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study.

- Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, the ERCOT SPF or any TDSP, have unacceptable consequences.

# Data/Modeling

  - Transmission Planning Steady State models base case development (SSWG Procedures- Rev 1)(revised Nodal version Rev 2)

  - Dynamic Model development (DWG procedures Rev 1)

  - SPWG Procedures Model development (DWG procedures Rev 1)

  - TPIT Report Procedures (Rev 1 or 2)

  - ALDR  Procedures (Rev 1 or 2)

  - Economic Assumptions development Procedures (Rev 2)

  - Data Dictionary Explanation and Procedures (move from SSWG procedures-Rev 1)

  - Generator Data Procedures  for use in Transmission Planning (Rev 2)

  - Contingency List (Multiple Circuits) Submission and Procedures (move from SSWG procedures-Rev 1)

  - Connectivity node group development procedures with NMMS (Rev 1 or 2)

# Should the Planning Guides include PASA/SOO documentation? (PUC Sub Rule 25.505)

# Should the Planning Guides include CDR procedures? (Generation Adequacy TF/LOLP)

Unless noted otherwise, capitalized terms contained herein shall have the meaning ascribed to them in the ERCOT Protocols.

As defined in PUCT Substantive Rule  §25.211(c)(10)

ERCOT Protocols Section 1.3.1.1 (10)