| OGRR Number | 243 | OGRR Title | Disturbance Monitoring Requirements Clarification |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | May 19, 2010 |  |  |
| Proposed Effective Date |  | August 1, 2010 |  |  |
| Priority and Rank Assigned |  | Not applicable |  |  |
| Guide Sections Requiring Revision |  | 7.1.2.3, Data Recording Requirements 7.1.2.4, Data Retention and Reporting Requirements |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) changes data recording and reporting requirements for equipment operating at 100kV or above at Facilities where fault recording equipment is required. |  |  |
| Reason for Revision |  | The System Protection Working Group (SPWG) prefers that the fault data recording requirements allow for calculated electrical quantities which are used in modern protection system equipment and can be determined by modern fault analysis software. The SPWG also prefers that recording requirements for autotransformers should allow for monitoring of either high voltage or low voltage terminals and that specification in the fault reporting template of the recorded time standard (such as Central Prevailing Time (CPT) or Coordinated Universal Time (UTC)), replace the requirement of Central Standard Time (CST) recording requirements. |  |  |
| Overall Market Benefit |  | Improvement of Transmission Service Providers (TSPs) and Resource Entities ability to successfully comply with listed recording requirements. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 3/9/10, OGRR243 was posted. - On 3/26/10, a CEO Revision Request Review was posted. - On 4/21/10, the Operations Working Group (OWG) considered OGRR243. - On 5/10/10, an Impact Analysis was posted. - On 5/19/10, OWG considered the 4/21/10 OWG Recommendation Report and Impact Analysis for OGRR243. |  |  |
| OWG Decision |  | On 4/21/10, OWG was in consensus to recommend approval of OGRR243 as submitted. On 5/19/10, OWG was in consensus to forward the 4/21/10 OWG Recommendation Report as revised by OWG and Impact Analysis for OGRR243 to ROS. |  |  |
| Summary of OWG Discussion |  | On 4/21/10, it was noted that there was additional information regarding the requirements of fault recording equipment in Section 7.1.2, Fault Recording Equipment. On 5/19/10, the need to maintain consistency between the Protocols and Operating Guides by using CPT rather than CST in the Operating Guides was discussed. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Improvement of TSPs and Resource Entities ability to successfully comply with listed recording requirements. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Glenn Hargrave on behalf of SPWG |
| E-mail Address | grhargrave@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | (210) 353-4215 |
| Cell Number | (210) 394-1313 |
| Market Segment | Municipals |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

- 7.1.2.3	Data Recording Requirements

For equipment operating at 100kV or above at Facilities where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

- Two (2) sets of voltages for breaker-and-a-half and ring bus substation configurations.  One (1) set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform.

- For all lines, neutral (residual) current waveform.

- Circuit breaker status.

- Circuit breaker trip circuit status.

- Date and time stamp.

For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

- For all autotransformers, high or low voltage terminal current waveform for three (3) phases and either neutral/residual current waveform or current waveform in delta windings.

- For all lines, two (2) phase current waveforms.

- Status – carrier transmitter control (i.e. start, stop, keying).

- Status – carrier received.

- 7.1.2.4	Data Retention and Reporting Requirements

The Facility owner shall store all recorded fault data for at least a two (2)-year period.  This data shall be stored in the form of a computer file or files.

Facility owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five (5) Business Days, along with channel identification and scaling information to allow analysis of the recordings. Fault recordings shall be shared between Facility owners, upon their request, for the analysis of ERCOT System disturbances.

Data submissions shall be COMTRADE fault recordings (.cfg and .dat files) and one (1) or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel © spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel © spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

- Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |  |
| --- | --- | --- |
| From Bus (ERCOT short circuit database bus number) |  |  |
|  | To Bus (ERCOT short circuit database bus number) |  |
| Nominal Voltage of Faulted Branch or Bus (kV) |  |  |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location) |  |  |
| Time Zone (Central Prevailing Time (CPT), UTC, etc.) |  | Date (MM/DD/YYYY) |
|  |  | Time (HH:MM:SS, twenty-four (24) hour format) |
|  |  | Cause Code |
| Fault Recorder Data |  | Circuit (1, 2, A, B, N, S, etc.) |
| From Bus – Recorder Location (ERCOT short circuit database bus number) |  |  |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |  |
|  | Nominal Voltage of Monitored Branch (kV) |  |
|  | Measured Current Magnitude (primary value in RMS amperes) |  |
|  | Recorded Fault Duration (cycles) |  |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |  |
| Optional Comments (40 char. max.) |  |  |

When multiple recordings exist for a single event, data from the best recording (usually the closest recorder) is required.

ERCOT shall compile a summary list of all available 345 kV fault recordings annually based on each Facility owner’s submitted data.  This summary shall contain for each recording the date, time, fault recorder owner, fault recorder location, the primary system element recorded, and an optional use comment field.  This summary shall be available to any ERCOT Member upon their request.  Record summaries will be retained by ERCOT for a minimum of three (3) years.