## Slide 1: RMR Exit for Spencer 5 – Remedial Action Plans
June 3, 2010
Technical Advisory Group
Jay Teixeira

## Slide 2: Summary
ERCOT staff analysis of the Spencer 5 RMR exit strategy identified the need for several transmission line upgrades as well as transformer and capacitor bank additions.
To allow exit of RMR prior to completion of the identified projects, Remedial Action Plans (RAPs) were developed.

## Slide 3: List of RAPs needed for 2010**
TAC
June 3, 2010
RAP Description |  | Contingency/Overload pair | 
1 | Carrollton RAP | L: Lewisville Switch (645)-Highland E 138 kV(1970) line C: Lewisville Switch (645)-Highland(664) | 
 |  | L: Lewisville Switch (645)-Highland E 138 kV(1970) line C: Highland (664) - Canyon (668) | 
4 | Frisco RAP | L: Collins (2370) – Frisco (681) 138 kV line C: Denton Steam – Corinth; Teasley to Pockrus | 
6 | Frisco Voltage RAP | L: Low voltage at Frisco and Panther Creek C: Collin to Frisco 138 kV line | 
7 | Arco-Krugerville RAP | L: Collins (2370) to Frisco (681) 138 kV line After Operation of Carrollton RAP or Lake Pointe RAP | 
based on 2010 SSWG load level and one unit unavailable need for RAPs prior to completion of exit strategy projects will be reviewed each year |  |  | 

## Slide 4: Permanent RMR Exit Solutions
Project |  | Cost | Estimated Completion Date
1 | RD Wells to Hickory 69kV (Denton) | $10,167,000* | June 2010
2 | Upgrade Lewisville Switch to Highland (TNMP) 138 kV line to 290MVA or above | $521,170* | May 2015
3 | Add second 345/138 kV autotransformer at Lewisville switching substation | $17,165,150* | June 2012
4 | Upgrade Collin to Frisco 138 kV line to 326 MVA | $981,594* | June 2013
5 | Upgrade West Denton to Jim Christal to North Denton138 kV line to 250 MVA or above | $5,000,000 | Summer 2012
6 | Additional capacitor banks at Navo and Panther Creek Substations (interim for Mustang capacitor bank) | Included in item 7 | 2011
7 | New Mustang Substation and capacitor bank | $2,760,500* | June 2013
8 | Upgrade Arco to Krugerville 138 kV | $4,193,381* | May 2011
*Planned prior to Spencer NSO |  |  | 

## Slide 5: Cost Analysis
The estimated annual RMR fixed costs that would be uplifted on an on-going basis are greater than the annual carrying costs of the transmission projects, notwithstanding any additional production cost savings.
Projects planned prior to Spencer NSO not included in transmission project cost.

## Slide 6
Questions?

## Slide 7
Details

## Slide 8: RAP 1 – Carrollton RAP
Problem 1
  Contingent element: Lewisville Switch (645)-Highland(664)
  Overload element: Lewisville Switch (645)-Highland E 138 kV(1970) line (Rate A/B/C: 214/214/214)
  RAP operation: Open NW Carrollton (2361) – Lewisville Switch (646) 345 kV and 138 kV lines
  Level of overload: 121.2% Rate B (259.4 MVA)
  Estimated number of hours RAP could operate in year 2010: 722 hours

## Slide 9: RAP 1 – Carrollton RAP cont’d
722 hours
Roanoke
Denton
NW Carrollton
Contingency:
Lewisville Switch (645) to Highland E (1970) 138 kV line
Overload element:
Lewisville Switch (645) to Highland (664) 138 kV line
RAP action:
Open NW Carrollton (2361) –
Lewisville Switch (646) 345 kV line
RAP action:
Open NW Carrollton (2362) –
Lewisville Switch (645) 138 kV line

## Slide 10: RAP 1 – Carrollton RAP cont’d
138 kV Alternative Plan – RAP Operation
  Open TNMP Highland – TNMP Lewisville (branch 37050 – 37060) 138 kV line
  Collin – Frisco 138kV line is overload, open Arco – Krugerville 138 kV line (Branch 1993-1994).
    If Allison – Krum line is in-service, Collins– Frisco 138 kV line overload can be corrected by Collin Reactive SPS.
    If Allison – Krum 138 kV line is not in-service, Lewisville Switch (645)-Highland E 138 kV(1970) line may still be overloaded after opening Arco - Krugerville. Open Argyle – Corinth 138 kV line (Branch 1984-1985) to correct the problem

## Slide 11: RAP 1 – Carrollton RAP cont’d
Contingency
Lewisville 645 - Highland 664 138 kV line
Overload element
Lewisville 645 – Highland 1970 138 kV line
RAP action
Open Argyle 1984 – Corinth 1985 138 kV line
RAP action
Open TNMP Highland 37050 –
TNMP Lewisville 37060
RAP action
Open Arco 1993 –
Krugerville 1994 138 kV line

## Slide 12: RAP 1 – Carrollton RAP cont’d
Hybrid plan
  Perform the 345 kV-plan upon initial detection of overload on the Lewisville Switch (645) to Highland (1970) 138 kV line
  Switch to the Alternative 138 kV-plan and put the opened NW Carrollton – Lewisville 345 and 138 kV circuits back in service .
  This allows a quicker response since only 1 TSP is involved in the implementation of the 345 kV-plan.

## Slide 13: RAP 4 – Frisco RAP
  Contingent element: Denton Steam – Corinth & Teasley - Pockrus
  Overload element: Collin (2370) to Frisco (681) 138 kV line (Rate A/B/C: 256/256/256)
  RAP operation:
    Raise the voltage of the West Denton 138 kV side to 140kV
    Place Collin Series Reactor SPS in-service so that it will operate when the Collin to Frisco line overloads.
    If this does not resolve the overload, put all three capacitor banks at Navo in-service
    Verify Argyle and Corinth capacitors are on
  Level of overload: 109% Rate B (278.9 MVA)
  Estimated number of hours RAP could operate in year 2010: 278 hours

## Slide 14: RAP 4 - Frisco RAP cont’d
Contingency:
Denton Steam auto-transformer to Corinth &
Teasley to Pockrus 138 kV line
Spencer
North Denton
Collin
RAP action:
Put all three capacitor
Banks at Navo in-service
Overload element:
Collins (2370) to Frisco (681)
138 kV line
RAP action:
Raise the voltage of the
West Denton 138 kV side
To 140 kV
RAP action:
Collin Series Reactor SPS Operates
When Collin to Frisco line overloads
278 hours

## Slide 15: RAP 6 - Frisco Voltage RAP
  Contingent element: Collin to Frisco 138 kV line
  Low voltage element: Frisco and Panther Creek bus
  RAP operation:
    Turn on all 3 capacitor banks at Navo
    Raise voltage at West Denton to 1.02~1.05
  Level of problem:
    Low voltage at Frisco: 0.89718 p.u.
    Lewisville (645) – Highland (1970): 104% [due to the presence of Carrollton – Lewisville 138 kV line]
    Arco (1993) – Krugerville (1994): 106.3%
  Estimated number of hours RAP could operate in year 2010:
    <0.92 p.u. – 584 hours (Brazos Criteria)
    <0.90 p.u. – 90 hours (ERCOT Criteria)
    Arco to Krugerville – 132 hours
    Lewisville to Highland – 36 hours

## Slide 16: RAP 6 – Frisco Voltage RAP cont’d
Contingency:
Collins (2370) to Frisco (681)
138 kV line
Spencer
North Denton
Collin
Problem:
Low voltage at Frisco
RAP action:
Raise the voltage of the
West Denton 138 kV side
To 1.02~1.05 pu
RAP action:
Turn on all 3 capacitor
banks at Navo
90 hours

## Slide 17: RAP 7 – Arco-Krugerville RAP
Cause
  Carrollton RAP
Overload element: Collin (2370) to Frisco (681) 138 kV line (Rate A/B/C: 256/256/256)
RAP operation: Open Arco (1993) – Krugerville (1994)138 kV line
Level of overload (Collins – Frisco 138 kV line):
  Carrollton RAP – 345 kV plan
    Problem 1 - 115.8% (296.3 MVA) after Carrollton RAP [pre RAP: 103.9% 259.4 MVA Collins Series Reactor SPS would relieve this but not after Carrollton RAP so use Arco RAP instead]
    Problem 2 – 114.2% (292.3 MVA) after Carrollton RAP [pre RAP: 102.1% 261.4 MVA Collins Series Reactor SPS would relieve this but not after Carrollton RAP so use Arco RAP instead]
  Carrollton RAP – 138V plan
    Problem 1 – 103.2% (264.2 MVA) after Carrollton RAP [pre RAP: 103.9% 259.4 MVA Collins Series Reactor SPS would relieve this overload]
    Problem 2 – 101.5% (292.3 MVA) after Carrollton RAP [pre RAP: 102.1% 261.4 MVA Collins Series Reactor SPS would relieve this overload]

## Slide 18: RAP 7 – Arco RAP-Krugerville cont’d
Same # of hours as
Carrollton RAP & Highland RAP
Overload element:
Collins (2370) to Frisco (681) 138 kV line
Contingency:
overload caused by Carrollton RAP
RAP action:
Open Arco (1993) – Krugerville (1994)138 kV line
Collin
Krugerville
Arco
Navo
Panther Creek

## Slide 19
Questions?