| OGRR Number | 240 | OGRR Title | CREZ Facility Protection and Control Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Approved |
| Date of Decision |  | June 3, 2010 |  |  |
| Effective Date |  | July 1, 2010 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Sections Requiring Revision |  | 7.2.1, Introduction 7.2.1.2, Applicability (new) 7.2.2, Design and Operating Requirements for ERCOT System Facilities 7.2.4, Maintenance and Testing Requirements for ERCOT System Facilities 7.2.5.1, General Protection Criteria 7.2.5.2, Equipment and Design Considerations 7.2.5.3, Specific Application Considerations 8.3.4, TDSP and QSE Supplied Communications |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) provides more stringent protection and control requirements for all new Competitive Renewable Energy Zone (CREZ) 345 kV Facilities. |  |  |
| Reason for Revision |  | This OGRR provides requirements for the protection and control for the CREZ transmission system that supports the transfer of renewable energy reliably from remote areas to large Load centers. This OGRR is aimed at achieving fault clearing within the voltage curve described in North American Electric Reliability Corporation (NERC) Draft Reliability Standard PRC-024-01, Generator During Frequency and Voltage Excursions (http://www.nerc.com/docs/standards/sar/PRC-024-1_Draft1_2009Feb17.pdf). The proposed revisions also address new NERC Planning (http://www.nerc.com/filez/standards/Assess-Transmission-Future-Needs.html) and Protection (http://www.nerc.com/docs/standards/sar/Project2009-07_Tech_Paper_Reliability_of_Protection_Systems_2009Jan20.pdf)standards currently under consideration. Additional information has been provided in the 2/15/10 AEPSC comments. |  |  |
| Overall Market Benefit |  | The reliable transmission of renewable energy across the ERCOT Region, promoting environmental conservation and economic power to reliably support Texas commerce. |  |  |
| Overall Market Impact |  | Elevated protection and control standards promote ERCOT System stability while maximizing the utilization of renewable energy Resources. |  |  |
| Consumer Impact |  | Protection and control usually represents a small fraction of the cost of the investment of the CREZ power system. Enhanced protection and control systems will maximize the availability of the CREZ Transmission Facilities for the delivery of renewable energy Resources. |  |  |
| Procedural History |  | - On 2/15/10, OGRR240 was posted. - On 2/15/10, AEPSC comments were posted. - On 2/17/10, OGRR240 was granted Urgent status via ROS e-mail vote. - On 2/19/10, the Operations Working Group (OWG) considered OGRR240. - On 3/4/10, Luminant comments were posted. - On 3/4/10, Oncor comments were posted. - On 3/9/10, System Protection Working Group (SPWG) comments were posted. - On 3/11/10, ROS considered OGRR240. - On 5/7/10, OGRR240/242 Task Force comments were posted. - On 5/12/10, a second set of Oncor comments were posted. - On 5/13/10, ROS again considered OGRR240. - On 5/26/10, CenterPoint comments were posted. - On 5/26/10, Texas Regional Entity (TRE) comments were posted. - On 5/26/10, a CEO Revision Request Review and Impact Analysis were posted. - On 6/2/10, a third set of Oncor comments were posted. - On 6/3/10, TAC considered OGRR240. |  |  |
| OWG Decision |  | On 2/19/10, OWG was in consensus to recommend that ROS develop a cross-functional group with members from the SPWG, Dynamics Working Group (DWG), Steady State Working Group (SSWG), Critical Infrastructure Protection Working Group (CIPWG), communications experts, and OWG with a direction to develop a solution for ROS to consider in April. |  |  |
| Summary of OWG Discussion |  | On 2/19/10, the reason for Urgency was discussed. It was noted that Certificates of Convenience and Necessity (CCNs) have been filed and priority lines have been afforded expedited treatment providing for a six month approval but a resolution of communication and protection/control standards is necessary. It was also noted that the proposed language addresses three NERC Reliability Standards currently under development. Some members of SPWG expressed concern regarding the proposed language stating that adding requirements with specific CREZ lines in the Operating Guides could be problematic for some and that an alternate solution such as a document outside of the Operating Guides should be considered. |  |  |
| ROS Decision |  | On 3/11/10, ROS unanimously voted to refer OGRR240 to the OGRR240/242 Task Force. All Market Segments were present for the vote. On 5/13/10, the motion to reject OGRR240 failed via roll call vote. ROS then voted to recommend approval of OGRR240 as amended by the 5/7/10 OGRR240/242 Task Force comments and as revised by ROS via roll call vote. All Market Segments were present for the votes. |  |  |
| Summary of ROS Discussion |  | On 3/11/10, the ROS formed the OGRR240/242 Task Force to further evaluate the CREZ communication and relaying issues. It was noted that the OGRR240/242 Task Force will return to ROS in April with recommendations or options and should consider the 3/4/10 Oncor comments and the 3/4/10 Luminant comments. On 5/13/10, the value of a CREZ system with additional features in relation to the incremental costs associated with such features was discussed. Additionally, there was discussion regarding the communication attributes and the potential for added cyber-security risk. Market Participants questioned whether ROS was opining that “Option 1” represents “best practice” by endorsing the “Option 1” language in Sections 7.2.5.3 and 8.3.4. It was noted that the language in the 5/7/10 OGRR240/242 Task Force comments included language proposed by OGRR242, Section 7, Revisions to Meet Pending NERC Requirements for New Construction. |  |  |
| TAC Decision |  | On 6/3/10, TAC unanimously voted to recommend approval of OGRR240 as amended by the 6/2/10 Oncor comments and as revised by TAC. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 6/3/10, the 5/26/10 TRE comments were discussed. There was a question regarding the use of “should” instead of “shall” and if line ratings would be affected if not made a requirement for Transmission Service Providers (TSPs). It was clarified that the use of “should” relates to the communications methodology used for system protection, rather than directly to line ratings. It was noted that these changes in 8.3.4 should be limited to CREZ. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Renewable energy Resources usually lack the inertia to provide the same stability capability of the large coal or nuclear power plants. The CREZ transmission projects represent Facilities that will remain in-service for many decades with each protection and control system having an average life span of 20 – 30 years. |  |
|  | 2 | Dependencies on other projects or other timing requirements. |  |
|  | 3 | Increased reliability from properly designed protection and controls. |  |
|  | 4 | Removes ambiguity. |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Enhanced reliability. | Lowers risk of loss of Load caused by under-frequency events. |
|  | 2 | Reduced congestion. | Improved observability of the ERCOT System resulting in higher transfer capability. |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Maintain ERCOT System reliability as new generators are added to the ERCOT System. |  |
|  | 2 | Ability to add new renewable Resources more effectively. |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | Minimal impact to ERCOT systems. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Paul Hassink |
| E-mail Address | phassink@aep.com |
| Company | American Electric Power Service Corporation (AEPSC) |
| Phone Number | 918-599-2653 |
| Cell Number | 918-599-2653, 0# |
| Market Segment | Investor Owned Utility (IOU) |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| AEPSC 021510 | Provided additional information regarding the need for enhanced standards for the design, operation and maintenance of the new 345 kV Facilities associated with the CREZ transmission system. |
| Luminant 030410 | Expressed concern about changes being made to the ERCOT Operating Guides based on NERC Draft Reliability Standard PRC-024-01 as well as proposed new NERC Planning and Protection standards currently under consideration. |
| Oncor 030410 | Proposed language changes to align with the OGRR242. |
| SPWG 030910 | Documented how members of SPWG voted on the revisions proposed in the 2/15/10 AEPSC comments. |
| OGRR240/242 Task Force 050710 | Proposed language changes that included options in Sections 7.2.5.3 and 8.3.4 for ROS to consider as the task force could not reach consensus. |
| Oncor 051210 | Recommended adoption of the language revisions to Section 7, Disturbance Monitoring and System Protection, proposed by the OGRR240/242 Task Force; requested an additional 30 days for the task force to review language in Section 8.3.4. |
| CenterPoint 052610 | Proposed language changes to make proposed communication requirements specific to CREZ by incorporating 345kV circuits and associated stations. |
| TRE 052610 | Suggested that uses of “should” be revised to more definitive terms such as “shall”, “may”, or “must. |
| Oncor 060210 | Proposed language changes to clarify the applicability of redundant paths and revised the list of 345kV circuits and associated stations. |

Proposed Guide Language Revision

### 7.2.1	Introduction

The satisfactory operation of the ERCOT System (equipment operated above 60 kV), especially under abnormal conditions, is greatly influenced by protective relay system.

Protective relay systems are defined as the total combination of:

- The protective relays,

- Associated communications system,

- Voltage and current sensing devices, and,

- The dc system up to the terminals in the circuit breaker.

Although relaying of tie points between Facility Owners is of primary concern to the ERCOT System, internal protective relay system often directly, or indirectly, affects the adjacent area also.  Facility Owners are those entities owning facilities in the ERCOT System.  Facility Owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  Protective relay system of individual Facility Owners shall not adversely affect the stability of ERCOT System interconnections.  Additional minimum protective relay system requirements are outlined in NERC Planning and Reliability Standards.

### 7.2.1.2	Applicability

These objectives and design practices shall apply to all new protective relay system applied at 60 kV and above unless otherwise specified.  It is recognized that there may be portions of the existing ERCOT System that do not meet these objectives.  It is the responsibility of individual Facility Owners to assess the protective relay system at these locations and to make any modifications that they deem necessary.  Similar assessment and judgment should be used with respect to protective relay system existing at the time of revisions to this guide.  Special local conditions or considerations may necessitate the use of more stringent design criteria and practices.

### 7.2.2	Design and Operating Requirements for ERCOT System Facilities

- Protective relay system shall be designed to provide reliability, a combination of dependability and security, so that protective relay system will perform correctly to remove faulted equipment from the ERCOT System.

- For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one (1) location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in other sections of the Operating Guides.

- Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

- The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

- Applicable IEEE/ANSI guides shall be considered when applying the protective relay system on the ERCOT System.

- The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

- All Facility owners shall give sufficient advance notice to ERCOT of any changes to their Facilities that could require changes in the protective relay system of neighboring Facility owners.

- Facility owners’ operations personnel shall be familiar with the purposes and limitations of the protective relay system.

- The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused Direct Current (DC) control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within thirty (30) days.  This documentation shall be reviewed by ERCOT for verification of implementation.

- Upon ERCOT’s request, within thirty (30) days, Power Generation Companies (PGCs) shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

- Upon ERCOT’s request, within thirty (30) days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

- Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by Generation Entities, to ERCOT upon their request within thirty (30) days.

- Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include under-frequency or under-voltage Load shedding.  A “Type 1 SPS” is any SPS that has wide-area impact and specifically includes any SPS that a) is designed to alter generation output or otherwise constrain generation or imports over DC Ties, or b) is designed to open 345 kV transmission lines or other lines that interconnect Transmission and/or Distribution Service Providers (TDSPs) and impact transfer limits.  Any SPS that has only local-area impact and involves only the Facilities of the owner-TDSP is a “Type 2 SPS.”  The determination of whether an SPS is Type 1 or Type 2 will be made by ERCOT upon receipt of a description of the SPS from the SPS owner.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of NERC Standards relating to SPSs, and shall additionally meet the following ERCOT requirements:

- The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources and HVDC ties.

- The SPS shall be automatically armed when appropriate.

- The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one (1) or more of the SPS’s monitored Facilities exceeds ninety-percent (90%) of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be allocated as agreed by the SPS owner and the Generation Resource owner.

- The status indication of any automatic or manual arming of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility(ies) controlled by the SPS.

- When a Transmission Operator (TO) removes an SPS from service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market.  When an SPS is returned to service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

- The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS every five years, or sooner as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and posted on the ERCOT website.

- For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Service Request to ERCOT.

- For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a Service Request.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one (1) review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, and approval of ERCOT before completion of the required ERCOT review.

- The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of any Facility(ies) controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

- An ERCOT SPS review shall verify that the SPS complies with ERCOT and NERC criteria, guides, and Reliability Standards.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within thirty (30) days.

- As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the appropriate Reliability and Operations Subcommittee (ROS) working groups such as the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

- ERCOT shall develop a methodology to include the SPS in the Commercially Significant Constraint (CSC) limit calculations, if appropriate.

- ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

- SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 6.1.2, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

- ERCOT shall report all SPS operations and misoperations to the Texas Regional Entity (TRE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to TRE.  An operation and misoperation of an SPS with respect to reporting requirements to TRE occurs when changes to the Transmission System occur, including but not limited to circuit breaker operation.  Owners of SPS’s will provide a monthly report to ERCOT describing each instance an SPS armed/activated and reset.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to TRE.

- If an SPS which reduces and/or removes generation from service operates more than two (2) times within a six (6) month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

- For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the ERCOT Market Information System (MIS).  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a Service Request, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the SPS.

7.2.4	Maintenance and Testing Requirements for ERCOT System Facilities

- The Facility Owner shall test and verify the proper operation of each new or modified protective relay system and associated communications channels prior to placing the equipment in its zone(s) of protection in service.  For protective relay systems that utilize a propagation-delay-sensitive operating principle and a communication channel with potentially significant propagation delay, time-synchronized “end-to-end” testing of the protective relay system shall be performed to verify that communication channel performance (including alternate routes) is adequate for proper operation.

- Facility Owners shall have documented protective relay system maintenance and testing programs in place.  Documentation shall include identification of protective relay system, a summary of testing procedures including requirements for frequency of tests, and the date last tested.

- The Facility Owner shall periodically test and inspect all components of the protective relay system to assure continued reliability.  Identified deficiencies shall be corrected.  Documentation demonstrating compliance with the Facility Owner’s maintenance and testing programs shall be supplied to ERCOT or NERC upon their request within thirty (30) days.

#### 7.2.5.1	General Protection Criteria

Dependability

- Except as noted in Sections 4 and 5 below, all elements of the ERCOT System operated at 100 kV and above (i.e., lines, buses, transformers, generators, breakers, capacitor banks, etc.) shall be protected by two (2) protective relay systems.  Each protective relay system shall be independently capable of detecting and isolating all faults thereon.

- The protective relay system design should avoid the use of components common to the two (2) protective relay systems.  Areas of common exposure should be kept to a minimum to reduce the possibility of both protective relay systems being disabled by a single contingency.

- The use of two (2) identical protective relay systems is not generally recommended, due to the risk of simultaneous failure of both protective relay systems because of design deficiencies or equipment problems.

- Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.  This protection need not be duplicated.

- On installations where freestanding or column-type Current Transformers (CTs) are provided on one (1) side of the breaker only, the protective relay system should be provided to detect a fault on the primaries of such CTs.  This protection need not be duplicated.  Application of freestanding CTs requires extra care to ensure that the relaying is proper and that the schemes overlap.

Security

The protective relay system should be designed to isolate only the faulted element, except in those circumstances where additional elements should be tripped intentionally to preserve system integrity.  For faults external to the protected zone, each protective relay system should be designed to either not operate, or to operate selectively with other systems, including breaker failure.  (In this context, the limits of the protected zone are defined by the circuit breakers.)

Dependability and Security

- The protective relay system should be no more complex than required for any given application.

- To the maximum degree practicable, the components used in the protective relay system should be of proven quality, as demonstrated either by actual experience or by stringent tests under simulated operating conditions, to ensure that the reliability of the protective relay system is not degraded by the components.

- The protective relay system shall be designed to minimize the possibility of component failure or malfunction due to electrical transients and electromagnetic interference or external effects such as vibration, shock and temperature.

- Critical features associated with protective relay system and circuit breaker operation shall be annunciated or monitored.

- The protective relay system circuitry and physical arrangements shall be carefully designed so as to minimize the possibility of incorrect operations due to personnel error.

- Computerized fault studies shall be used during the planning or design stages to analyze the effects of an addition or modification to the ERCOT System and to determine proper protective relay system coordination.

- To the extent dynamic or transient analysis shows that a protection system, designed within the guidelines contained in these Operating Guides, is unable to operate in a manner that maintains continuity of service and/or system stability in accordance with NERC Reliability Standards and the Operating Guides, additional measures shall be considered for improvement to the operation of the protection system.  Additional measures may include redundant CTs, Voltage Transformers (VTs), power supplies and communication paths.

Operating Time

The objective of the protective relay system is to take corrective action in the shortest practical time with due regard to selectivity, dependability and security. In cases where clearing times are deliberately extended, consideration should be given to the following:

- Effect on ERCOT System stability or reduction of stability margins.

- Possibility of causing or increasing damage to equipment and subsequent extended repair and/or outage time.

- Effect of disturbances on service to customers and neighboring Facility Owners.

Testing and Maintenance

- The design of the protective relay system both in terms of circuitry and physical arrangement shall facilitate periodic testing and maintenance.  Test devices or switches should be provided to eliminate the necessity for removing or disconnecting wires during periodic testing.  Protective relays for transmission lines shall be designed to support periodic testing and maintenance while the transmission line remains in service.

- Commissioning of new equipment should consist of the following steps:

- Relay installation wiring diagrams cross-checked against schematics

- After completion of construction, physical check of wiring and relay installation

- Check and testing before energizing of all equipment in the zone of protection, including relay testing.  It is desirable to test the relays at the setting the relay will have in service

- Check of supporting paperwork, such as relay test reports

- Check that the relay settings when received from the manufacturer concur with the intended manufacturer’s specifications

- Calibrate and check that proper utility’s settings have been made

- Maintain a record of trip check and energizing procedure performance

- Maintain a record of in-service measurement of voltage, current magnitudes, phase angles, and a comparison to expected values and to other instrumentation

- Release to Facility owner for service

Analysis of System Performance and Associated Protection Systems

- Relay operation and settings shall be reviewed periodically and whenever significant changes in generating sources, transmission facilities, or operating conditions are anticipated.

- Naturally occurring faults and other system disturbances should be analyzed as a source of information as to the health of relay schemes in the system.  Sources of information usually available are:

- Short circuit study for the exact conditions of the fault

- Fault recorder traces

- Sequence of events data recording the opening and closing of contacts in the protective relay scheme and associated communication equipment

- Fault locator data

- SCADA logger output of breaker operation and alarms

- Interviews with operating personnel and/or other witnesses

- Field report of relay flags and breaker counter changes

- Field report of the fault location, if found

- Records of relay setting, relay testing, trip check and energize procedures as carried out, in-service measurements, relay wiring diagrams and schematics, manufacturers' information

- Other coworkers and SPWG members

- Manufacturers’ application and design engineers

- Steps one can follow in analyzing a disturbance are:

- Gather data

- Create a time line consisting of events and periods between events

- Compare actual and calculated values of current and voltage during the periods between events

- Compare actual and expected breaker operations and flags

- Choose the least complicated explanation for contradictory information and to fill in missing information

- Gather additional information as indicated to prove or disprove explanations

- Iterate

- Document by issuing a report of all findings, changes, and recommendations

- After a reasonable time, check back to see if the recommendations have been carried out

#### 7.2.5.2	Equipment and Design Considerations

Current Transformers

- CTs associated with the protective relay system shall have adequate steady state and transient characteristics for their intended function.

- The output of each CT shall remain within acceptable limits for the connected burdens under all anticipated fault currents to ensure correct operation of the protective relay system.

- CTs or their secondary windings shall be located so that adjacent protection zones overlap.

- CT secondary wiring shall be grounded at only one (1) point. When multiple CTs are interconnected, the combination shall have only one (1) ground.

- For all newly installed protective relay systems, the two (2) protective relay systems protecting a zone shall utilize isolated and separate CTs, or isolated and separate secondary windings in the case of free-standing CTs.

- Other considerations:

- Internal bushing CTs are preferred over external slip-over CTs

- 10L800 (C800) class CTs are preferred for relaying

- Breakers and free-standing CTs with four or more sets of CTs are preferred

- Over-the-bushing external CTs can sometimes solve problems when there aren't enough CTs.  Note that there may be an unprotected region between the external CT and the bushing CT.

- Shorting type terminal blocks should be provided for all CTs

Voltage Transformers and Potential Devices

- Voltage Transformers (VTs) and potential devices associated with the protective relay system shall have adequate steady state and transient characteristics for their intended functions.

- VTs and potential devices shall have adequate volt-ampere capacity to supply the connected burden while maintaining their relay accuracy over their specified primary voltage range.

- Usually one (1) set of VTs (with two separate secondary windings per VT) per bus (i.e. single bus substation configuration) or per power system element (i.e. ring bus and breaker-and-a-half substation configurations) is sufficient.

- The two protective relay systems protecting ERCOT System Facilities may use separate secondary windings of the VTs or one (1) of the secondary windings may be dedicated to supplying the polarizing potential and the other winding used to supply other protection and monitoring functions.  For all newly installed protective systems, if the two (2) protective relay systems protecting a zone each require a VT input for protection functions, they shall utilize isolated and separate VT secondary windings unless ERCOT determines that one of the secondary windings must be dedicated to metering applications.

- VT and potential device secondary wiring shall be grounded at only one (1) point.  (ANSI/IEEE C57 recommends grounding at the panel.)

- VT installations shall be designed with due regard to ferroresonance due to capacitance across the interrupter at 138kV and above.

- Other considerations

- Special attention should be given to the physical properties of secondary circuit fuses

- Capacitor coupled VTs are suitable for relaying and SCADA telemetry

- Report loss of VT voltage (VT fuse failure) over SCADA

Batteries and Direct Current (DC) Supply

- DC batteries associated with the protective relay system shall have a high degree of reliability.

- Two (2) batteries each with its own charger should be provided at each location.  An acceptable alternative is one (1) battery with two (2) separately protected branches.  The two (2) protective relay systems protecting a zone shall be supplied from the separate batteries or branches.  For transmission Facilities at 100kV and above, two (2) batteries shall be required in locations that remote backup clearing of lines and substation faults is not achieved.  For new or upgraded transmission Facilities at 200kV and above with two (2) or more transmission voltage circuit breakers, two (2) batteries each with its own charger, are required.

- Each battery shall have sufficient capacity to permit operation of the station, in the event of a loss of its battery charger or the AC supply source, for the period of time necessary to transfer the load to the other battery or to re-establish the supply source. Each battery and its associated charger shall have sufficient capacity to supply its share of the DC Load of the station.

- A fault at the battery terminals can only be interrupted by a mid-bank protective device.  If a mid-bank protective device is not used, then the connections between the battery terminals and the main protective devices shall possess the highest possible degree of reliability.

- Battery chargers and all associated circuits shall be protected against short circuits.  All protective devices shall be coordinated to minimize the number of DC circuits interrupted.

- The regulation of DC voltage shall be designed such that, under all possible loading conditions, voltage within acceptable limits will be supplied to all devices.

- DC systems shall be monitored to detect abnormal voltage levels, both high and low, DC grounds, and loss of AC to the battery chargers.  Loss of DC to relay schemes shall be alarmed.  Also, where possible the loss of AC to the battery chargers and loss of DC should be provided as SCADA alarm inputs.

- DC systems shall be designed to minimize AC ripple and voltage transients.

- The DC circuit protective devices used shall have published DC interrupting ratings suitable for the required circuit duty.

AC Auxiliary Power

- There should be two (2) sources of station service AC supply, each capable of carrying all the critical loads associated with the protective relay system.

- Failure of station service AC supply should be alarmed over SCADA.

Circuit Breakers

- Two (2) trip coils, one (1) associated with each protection system, shall be provided for each operating mechanism.  The failure of one (1) coil shall not damage or impair the operation of the other coil.

- The design shall be such that the breaker will operate if either both trip coils are energized simultaneously, or either trip coil alone, and verified by tests.

- Circuit breaker auxiliary switches used in protection systems should be highly reliable with a positive make-break action and good contact wipe.  Multiplier contacts simulating breaker auxiliary switches should be used with caution in protection systems.

- A three-phase and line-to-ground interrupting study to validate or indicate breaker interrupting rating shall be performed.

Communications Channels

- Where communication channels are required for the protective relay system purposes, the communication facilities shall have a degree of reliability no less than that of the other protective relay system components.  For extra security, the output contacts from two (2) independent channels may be wired in series.

- Where communication channels are required in each of the two (2) protective relay systems, the channels shall be separated physically and designed to minimize the risk of both channels being disabled simultaneously by a single contingency.

- Communication channels shall be provided with means to verify signal performance.

- Other considerations

- Report loss of channel over SCADA

- Automatic testing of power line carrier (PLC) is desirable to reduce false trips from failure to block

- Split up PLC Loads between DC sources so that loss of one (1) fuse does not disable all the carrier sets.  If all the carrier sets were to be disabled, then multiple false trips during a fault could result.

- Control cables and wiring

- See also Section 8.3.4, TDSP and QSE Supplied Communications.

Control Cables and Wiring

- Control cables, wiring and auxiliary control devices should be such as to assure high reliability with due consideration to published codes and standards, fire hazards, current-carrying capacity, voltage drop, insulation level, mechanical strength, routing, shielding, grounding and environment.

- Other considerations

- AC or DC go-and-return functions should be implemented in the same cable to avoid induction loops

- Individual wires in cables should have colored jackets, not black jackets with a "color" printed on the jacket

- Standardization of the relationship between wire colors and functions is desirable

- No splice in any wire or cable

- All cables terminated on terminal blocks

- Shielded cable should be installed in locations where electric fields, magnetic fields, or electromagnetic interference is sufficient to disrupt the reliable operation of the control cable and it cannot be mitigated by other means.

Environment

- Means shall be employed to maintain environmental conditions that are favorable to the correct performance of the protective relay system.  Particular attention should be given to solid-state equipment installations.

- Other environmental hazards to look out for:

| - Fire ants | - Rats |
| --- | --- |
| - Snakes | - Dust, dirt, grime |
| - Trash and leftover hardware | - Water |
| - Gunfire | - Theft of substation and transmission grounds |
| - Hand-held radio keyed near solid-state relays | - Batteries located in same room as relays (battery fires) |
| - Severe cold weather conditions can impact operation of circuit breakers, DC battery, and carrier signals. |  |

#### 7.2.5.3	Specific Application Considerations

Transmission Line Protection

- 1.	Each of the two (2) independent protective relay systems shall detect and initiate action to clear any line fault without undue system disturbance.  The protective relay system shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme, a widespread disturbance will not result.  A protective relay system, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other protective relay system, including breaker failure.

- 2.	For newly installed transmission line protective relay systems:

- Fuses shall not be used in the 3Vo polarizing supply for ground relays.

- Loss-of-potential function shall be used for schemes dependent on voltage for correct operations.   SCADA alarms shall be provided for Loss-of-potential conditions.

- Dual communication-aided protection over dual communications channels shall be used where dynamic and/or voltage stability studies indicate non-pilot protection operating times are inadequate.

- 3.	Transmission line protection should include:

- One independent protective relay system of phase and ground protection over a communications channel.

- A second independent protective relay system of at least two (2) zones of phase protection and

- at least two (2) zones of ground protection or  ground directional overcurrent relaying (time delay and instantaneous).

- “Ground chain protection” or switch-to-on-fault to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs and protection elements dependent on distance measurement.

- Recognition and trip for open conductor is desirable but not required.

- Overload protection is provided by SCADA analog alarms and dispatcher discretion.

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure.

- Short lines may require special attention, such as dual primary schemes, etc.

- For transmission Facilities with series compensation, dual communication-aided protection should be used.  At least one (1) of the two (2) protective relay systems should be differential type.

- OPTION 1:

- For any transmission line that has dual communication-aided protection systems, at least one (1) of the two (2) protective relay schemes should be of a differential type in any location where an adequate communications infrastructure exists or is planned and there are no mitigating circumstances (e.g. tapped loads).

- Transmission Station Protection

- 1.	Each zone in a station shall be protected by two (2) independent protective relay systems.  For zones not protected by line protection, at least one (1) of the two (2) protective relay systems shall be a differential type.

- 2.	The protective relay system shall be designed to operate for station faults so that, if ultimate clearing is accomplished by a breaker failure scheme, a widespread disturbance will not result.  The protective relay system shall be designed to operate properly for the anticipated range of currents.

- 3.	Station protection should consist of:

- Bus differential or bus overcurrent protection of all buses

- All transformers protected by transformer differential, transformer overcurrent, or fuses (for small transformers).  Note that ferroresonance is possible for fused transformers above 69kV.

- Sudden pressure relay protection for transformer main tanks and transformer tap changer compartments

- For transformers with conservator tanks, gas accumulator relay (also known as a Buchholz relay) protection for the transformer main tanks and transformer tap changer compartments are preferred in addition to sudden pressure relay protection.

Breaker Failure Protection

- 1.	Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.

- 2.	The breaker failure protection should be initiated by each of the protection systems that trip that breaker.  It is not necessary to duplicate the breaker failure protection itself.

- 3.	Induction cup, solid state, or microprocessor based current detectors shall be used to determine if a breaker has failed to interrupt.

- 4.	Plunger or clapper type overcurrent relays are not recommended as breaker failure fault detectors.

- 5.	For all newly installed or upgraded relay systems, a cross-tripping means such that each protective relay system can operate both circuit breaker trip coils without compromising the separation of the DC supplies is recommended.

- 6.	Breaker failure schemes shall be designed such that if fault clearing should be accomplished through operation of the breaker failure scheme, an uncontrolled separation and collapse of the ERCOT System will not result.  Breaker failure schemes shall be designed to be selective in time with other protective relay systems and/or particular system requirements.

Generator Protection

- 1.	Generator faults shall be detected by more than one (1) protective relay system.  These may include faults in the generator or generator leads, unit transformer, and unit-connected station service transformer.

- 2.	Generators shall be protected to keep damage to the equipment and subsequent outage time to a minimum.  In view of the special consideration of generator unit protection, the following are some of the conditions that should be detected by the protection systems:

- Unbalanced phase currents

- Loss of excitation

- Over-excitation

- Field ground

- Inadvertent energization (reverse power)

- Uncleared system faults

- Off-frequency

It is recognized that the overall protection of a generator will also involve non-electrical considerations.  These have not been included as part of this criteria.

- 3.	The apparatus shall be protected when the generator is starting up or shutting down as well as running at normal speed; this may require additional relays, as the normal relays may not function satisfactorily at low frequencies.

- 4.	A generator shall not be tripped for a system swing condition except when that particular generator is out of step with the remainder of the system.  This does not apply to protective relay system designed to trip the generator as part of an overall plan to maintain stability of the ERCOT System.

- 5.	The loss of excitation relay shall be set with due regard to the performance of the excitation system.

Automatic Under-Frequency Load Shedding Protection Systems

- Automatic under-frequency Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, Maintenance and Testing Requirements for ERCOT System Facilities, apply to under-frequency Load shedding protection systems as well.

- 1.	Automatic under-frequency Load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the system during major emergencies.

- 2.	The criteria for the operation of these protection systems are detailed in Section 2.9, Requirements for Under-Frequency Relaying.

- 3.	Automatic under-frequency Load shedding protection systems need not be duplicated.

- 4.	Generator and turbine under-frequency protection systems shall be coordinated with Section 2.9.

- 5.	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency Load shedding program.

- 6.	Automatic Load restoration for an under-frequency Load shedding operation is not currently utilized in ERCOT.

Automatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage Load shedding systems are classified as protective relay systems. The maintenance requirements, discussed in Section 7.2.4 apply to under-voltage Load shedding protection systems as well.

- 1.	The requirement for under-voltage relaying shall be determined by system studies performed/administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

- Amount of Load to be shed to restore voltage to minimum acceptable level or higher,

- The minimum and maximum time delay allowed before automatically shedding Load,

- The voltage level(s) at which to initiate automatic relay operation, and

- The location(s) for effectively applying under-voltage Load shedding protection systems.

- 2.	Automatic under-voltage Load shedding protection systems need not be duplicated.

- 3.	Analyses shall be performed on under-voltage Load shedding schemes by working groups and/or equipment owners as assigned by ERCOT to demonstrate that they are expected to act before generators trip Off-line due to the protective relay requirements described in Section 3.1.4.6, Protective Relaying and Voltage Ride-Through (VRT) Requirement.  A specific exemption from this analysis requirement may be provided by the ROS.

- 4.	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

- 5.	Automatic Load restoration for an under-voltage Load shedding operation is not currently utilized in ERCOT.

- 6.	The scheme shall be designed to ensure reliable operation and to prevent false tripping.

- 8.3.4	TDSP and QSE Supplied Communications

Each TDSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TDSPs these include, but may not be limited to, voice communications and SCADA for substations and other transmission facilities.  For QSEs, these include, but may not be limited to, voice and SCADA for generating plants and loads.

Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TDSP or QSE providing the path.

QSEs communicating with connected resources and TDSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability (i.e., separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.).

Option 1:

For each new Competitive Renewable Energy Zone (CREZ) transmission line, listed below, an associated communications path should be established to provide a high degree of dependability, security, and immunity from interference.  Additionally this communications path should support high bandwidth (155 mb/s or greater), low latency (unidirectional delay no greater that 1 millisecond per 100 miles), and be engineered to meet 99.999% availability with capacity reserved for regulated utility protection, monitoring and control.  Redundant communication paths are required unless this necessitates retrofitting existing facilities.

In this Operating Guide, CREZ, consist of the following new 345kV circuits and associated stations:

- Bluff Creek to Brown double circuit

- Brown to Newton double circuit

- Newton to Killeen double circuit

- Killeen to Salado add second circuit

- Scurry County South Switching Station to West Shackelford double circuit

- Scurry County South Switching Station to Tonkawas double circuit

- Scurry County South Switching Station to Long Draw Station double circuit

- Dermott Switching Station to Scurry County South Switching Station double circuit

- Dermott Switching Station to Willow Creek double circuit

- Central Bluff to Bluff Creek double circuit

- West Shackelford to Navarro/Sam Switch double circuit

- Sand Bluff Station to Divide double circuit capable

- Bearkat Station to Sand Bluff station double circuit capable

- Gillespie to Newton double circuit capable

- Kendall to Gillespie double circuit capable

- North McCamey to Odessa double circuit capable

- Bakersfield to North McCamey double circuit capable

- Bakersfield to Big Hill double circuit capable

- Big Hill to Kendall double circuit capable

- Big Hill to Twin Butte double circuit capable

- Riley to Edith Clarke double circuit

- Nazareth to Hereford double circuit capable

- Nazareth to Silverton double circuit capable

- Hereford to White Deer double circuit capable

- Silverton to Cottonwood Station double circuit

- Silverton to Edith Clarke double circuit

- Cottonwood Station to Dermott Switching Station double circuit

- Cottonwood Station to Edith Clarke double circuit

- White Deer to Silverton double circuit

- Gray to Riley double circuit

- Gray to White Deer double circuit

- Edith Clarke to West Shackelford double circuit

- Sweetwater East to Central Bluff double circuit

- Tonkawa to Sweetwater East double circuit

- Long Draw Station to Sand Bluff Station double circuit capable

- Long Draw Station to Grelton Station double circuit capable

- Grelton Station to Odessa double circuit capable

- Riley to Bowman double circuit

- Riley to West Krum double circuit

- West Krum to Anna double circuit

- Willow Creek to Hicks double circuit

- Bowman to Jacksboro double circuit capable

- Jacksboro to Willow Creek double circuit

- Willow Creek to Parker double circuit

QSEs and TDSPs shall supply, implement and maintain all data and voice communication facilities required to fulfill the obligations set forth in the Operating Guides.