| NOGRR Number | 037 | NOGRR Title | Synchronization with OGRR217, Relay Misoperation Report Format Change |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | April 21, 2010 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Guide Section Requiring Revision |  | Section 8, Attachment B: Relay Misoperation Report |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) changes the format for reporting yearly relay misoperations from a report format to a data format. |  |  |
| Reason for Revision |  | The System Protection Working Group (SPWG) prefers to have a data format for reporting relay misoperations as opposed to a report format. This will allow ERCOT to compile the data and distribute back to Market Participants for analysis and trending of similar problems between types of relays or schemes. |  |  |
| Overall Market Benefit |  | The new report format will help to improve the reliability of transmission protection systems. |  |  |
| Overall Market Impact |  | None |  |  |
| Consumer Impact |  | None |  |  |
| Procedural History |  | - On 3/24/10, NOGRR037 and a CEO Revision Request Review were posted. - On 4/21/10, the Operations Working Group (OWG) considered NOGRR037. |  |  |
| OWG Decision |  | On 3/24/10, On 4/21/10, the OWG was in consensus to recommend approval of NOGRR037 as submitted. |  |  |
| Summary of OWG Discussion |  | On 4/21/10, it was noted that this report goes to SPWG and ERCOT for review and that SPWG reports annually on certain misoperations. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | The new format will help to improve the reliability of transmission protection systems. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | The new report format will help to improve the reliability of transmission protection systems. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Glenn Hargrave on behalf of SPWG |
| E-mail Address | grhargrave@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | (210) 353-4215 |
| Cell Number | (210) 394-1313 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | (512) 248-3867 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |

Proposed Guide Language Revision

### Relay Misoperation Report

Relay misoperations shall be reported in any format compatible with ERCOT (i.e., Microsoft © Excel, Microsoft © Word, or PDF) except where a specific format is requested.  All fields of data specified in the table below shall be included in the report.  The file shall include the "Field Names" listed in the table below as headers for each field and the data size/format shall match "Size or Format" specified in the table below.

| Field Name | Type | Size or Format | Description |
| --- | --- | --- | --- |
| Misop_Date | Date | mm/dd/yyyy | The date that misoperation occurred. |
| Misop_Time | Time | hh:nn:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| Time_Zone | Text | 50 | Define the standard time of the misoperation time noted (i.e. GMT, CT, EST, etc.). |
| Utility | Text | 25 | Name of the facility owner. |
| Voltage | Text | 10 | Transmission voltage (345 kV, 138 kV, 69 kV, etc.). |
| Protected_Equipment | Text | 25 | The Transmission Element (line, autotransformer, bus, etc.) protected by the protection scheme. |
| Substation | Text | 50 | Name of the substation where the misoperated element or equipment is located. |
| Protection_Scheme | Text | 25 | Type of protection scheme applied (i.e. Differential, DCB, SPS, Step distance, etc.). |
| Equipment_Name | Text | 50 | Specific description of the protected transmission equipment. |
| CB_Number | Text | 50 | Unique circuit breaker number assigned or used by the facility owner that effected the actual isolation. |
| Fault_Type | Text | 50 | Type of fault occurred (L-L, L-G, L-L-G, 3L-G, etc. If the misoperation occurred for a non-fault condition, note this field with ‘N/A’). |
| Communication_Method | Text | 50 | Type of communication method used for the protection scheme (i.e. Pilot wire, fiber, power-line carrier, etc.). |
| Manufacturer | Text | 50 | Relay Manufacturer’s name. |
| Relay_Type | Text | 50 | Relay Type or style name (i.e. SEL-321, REL-512, CO-9, etc.). |
| Relay_Style | Text | 50 | Relay model number. |
| Misop_Category | Text | 50 | Relay events constitute as reportable protective relay system misoperation as detailed in Section 6.2.3, Performance Analysis Requirements for ERCOT System Facilities. |
| Misop_Description | Text | 32,767 | Description of the protective element/scheme failure that caused the misoperation. |
| Investigation_Results | Text | 32,767 | Description of the analysis results from the misoperation review and any deficiencies identified. |
| Corrective_Action | Text | 32,767 | An action plan to correct any deficiencies identified in the investigation results or any additional action plan to avoid similar operations in the future. |
| Target_Date | Date | mm/dd/yyyy | Target date to implement the corrective action plan at the terminal(s) where the misoperation(s) occurred. This could also be the date that the corrective action plan was implemented. |
| Recommendation | Text | 32,767 | System wide corrective action plan or long term solution to avoid similar misoperations (i.e. design changes, equipment replacements, etc.). |
| Report_By | Text | 25 | Individual who completed the report. |
| Phone | Text | 50 | Business phone number of the individual who completed the report. |
| Report_Date | Date | mm/dd/yyyy | The date at which the report was completed (i.e. when corrective action was implemented). |