## Slide 1
City of College Station
Load Forecasting
Presented by :
Brent Read
Utility Dispatch Operations Assistant
Notes: <number>

## Slide 2
BACKGROUND
32,000 Electric Meters
189,625 MW Peak Load in 2009
Unique Summer Load Curve because of Student Population
Represent 0.302% of Load for ERCOT System at Peak
Area continues to grow despite recession
Notes: City of College Station is the 9th largest Municipal electric provider in the State of Texas. We have about 20 miles of transmission lines with 5 existing substations and one under construction.
We have about 32,000 electric meters to serve a population of over 90,000. Of that 90,000 approximately 30,000 are students of Texas A&M or Blinn College.
Our Peak Load of 189,625 MW for 2009 happened in late June. At that time, many of our student population were not “in town” as they were home for the summer.
One of the major factors besides weather that affects our peak load is our student population. In mid May, our population decreases by about 30,000 until June 1st, where about 15,000 of the students return for the summer. In August, the rest of them come back for the fall semester. If our peak were to hit during one of those times when all of the students are in town it is possible that our estimates could be 5 to 10% below our actual summer peak.
With that said, we design our distribution circuits based upon a greater peak than our transmission projections. Since we represent only about 0.3% of the ERCOT loading (and the students have to move in from somewhere!), this variance should be minimal when considering the entire system.
Finally, because of the University and the growth of the Services Industry in College Station, the area still continues to grow at about 2%.
<number>

## Slide 3
Actual Peaks highly
Dependent on timing
Projections made
at 2% load growth
Linear trendline
For historical information
Notes: The following is a plot of our historical data for Summer Peak and the ALDR projections for future peaks through 2016.
(CLICK) If you look at our historical data you will see that the timing of the summer peak, along with weather anomalies such as hurricanes, can affect the Peak value for any individual year. Even with that, you will see that there is consistent growth for our area.
(CLICK) Plotting a linear trendline on the graph, you will see that the ALDR projections for 2010 through 2016 are close to this linear progression. If you were to plot this same graph leaving out the data for 2000, the line would actually be above the projections shown.
(CLICK) Even though we may vary from year to year, the 2% growth rate used for the future projections should be a fairly accurate representation .
<number>

## Slide 4
PROJECTIONS
ALDR projections are made using a linear projection at 2% based upon historical data
Data Set A projections are based upon SCADA data projected forward at a 2% growth rate
Data Set B projections are made based upon ALDR projections with known distribution projects being taken into account to distribute load between Substations
Notes: Projections:
The historical data that has been turned in for the ALDR is reviewed annually and the proposed growth rate is re-evaluated. The current growth rate has been determined using a linear projection to be around 2%.
Data Set A projections are based upon data gathered from our SCADA system and are also projected at a 2% growth rate.
Data Set B projections are based upon submitted ALDR data. Because of our plans for our distribution system, we are easily able to correlate future planning needs for the distribution system into load transfers between our substations.
<number>

## Slide 5
SYNOPSIS
Our load represents about 0.3% of the ERCOT total
WYSIWYG
Historical data confirms our current estimate of growth
Timing is a substantial issue in determining our peak load
Notes: To sum things up:
Our percentage of the ERCOT load is about 0.3%. We feel that our projections are as precise as possible, but they probably don’t affect the accuracy of the total load projections for the System.
From the old Lotus 1-2-3 term , “What You See is What You Get”. There is no diversity in our system like the larger systems where it might be 105 degrees in one service area and raining in another. Our peak is easily determined and well defined.
Even with all of the variables considered for weather and timing, our historical data currently trends to a 2% overall growth rate.
With that said, our projections for peak load for each individual year are very conservative. If summer peak were to happen between the first of August and the middle of September it is possible that our peak load would be 5 to 10% greater than our projections.
<number>

## Slide 6
Questions?
Notes: <number>