## Slide 1: AEP-Texas: Load Projections/Forecasting and Steady State Base Cases
ERCOT Reliability Operations Subcommittee Meeting
June 10, 2010
Austin, Texas

## Slide 2: Load Projections
AEP Economic Forecasting (aggregate loads by subregions or load areas and service company peaks) along with Distribution Asset Planning (points of delivery loads) prepares data for the Annual Load Data Request (ALDR) and submits the load data to ERCOT.
ERCOT provides the date and time of the ERCOT summer peak, winter peak, and minimum load for the previous year. AEP obtains the load data for these times along with the peak load at each bus from historical records.
The coincidence factor for each bus is calculated by dividing the load coincidental with the ERCOT peak by the seasonal peak load at the bus. This provides a percentage (coincidence factor) to calculate the future loads off of the forecasted peak at each bus.

## Slide 3: Load Projections
Service area and load area (subregion) forecasts provide a framework that guides the POD’s forecasts.
Load areas are defined by the transmission organization and include Laredo, Del Rio Triangle, Corpus Christi, Rio Grand Valley, San Angelo, Abilene, and Victoria.
Resulting POD forecasts are provided in the ALDR.

## Slide 4: Load Area Projections
Forecasts for geographical areas (load areas) involve analysis of historical county sales and hourly data and economic forecasts.
  Sales data is obtained from the customer information system by revenue town and revenue class.
  Interval MW data is obtained from SCADA and MV90 recorders via Transmission Dispatch and Load Research.
  Economic/Demographic data is obtained from Moody’s Economy.com by county and aggregated to the defined area.
  Sales are forecast through the use of revenue class base econometric models driven by economic activity.
  Peaks are forecast through the use of normalized historical load and typical weather for the area.

## Slide 5: Points of Delivery Load Projections
AEP-Texas has 616 PODs in the ALDR.
Initial POD non-coincident seasonal peaks are forecasted using time-series methods from historical metered loads from the preceding five years data.
POD forecasts are adjusted as necessary to account for switching, construction, large customers, etc.

## Slide 6: Large Industrial POD Projections
Company meters on customers with large loads capture net load on the system.
Limited information exists for load behind the meter for most large customers.
TDSP large customer representatives glean some knowledge of existing and future loads behind the meter, but knowledge is limited.
Customers with large loads on interruptible/curtailable type ERCOT driven programs are unknown to TDSP and thus not included in the ALDR.

## Slide 7: ALDR from ERCOT
AEP Transmission Planning receives ALDR data from ERCOT the first week of April
ALDR data in the AEP Transmission footprint include TNC, TCC, as well as 8 – 10 rural electric cooperatives and municipal PODs

## Slide 8: ALDR Raw Data
Data for individual loads appear in the ALDR “LoadDetail” tab as non-coincident peak data for each summer and winter in the forecast
Total system load appears in the ALDR “LoadSummary” tab as an ERCOT-coincident peak, for each summer and winter in the forecast

## Slide 9: ALDR Analysis
The ALDR data is analyzed
Suspect bus numbers are corrected
Summer and winter coincidence factors are investigated and corrected
Bus numbers changes due to voltage conversions receive special attention

## Slide 10: ALDR Processing
Validated ALDR data is read into an Access database for TCC, TNC, and each of the coops and municipals that AEP serves
Seasonal factors are used to develop case data for seasonal and off-peak load cases that aren’t in the ALDR
  Seasonal factors are summer, winter, spring and fall determined by company and load areas coincident with ERCOT peak, minimum and peak day minimum.

## Slide 11: Self-Serve and Industrial Load
Information on self-serve and industrial loads comes from industrial customer service reps
Modeling of self-serve generation and load is to the best of our knowledge, but is not based on metered values like other data
These loads do not vary seasonally or daily like other loads, so seasonal factors are not applied

## Slide 12: NCP to CP
Non-Coincident Peak loads must be adjusted downward to Coincident Peak loads for use in powerflow cases
The practice in ERCOT has been for TSPs to represent company-coincident loads, which are slightly higher than ERCOT-coincident loads

## Slide 13: Load Calibration
Systemwide coincidence factors are used to adjust ALDR non-coincident peak data to the ERCOT-coincident peak
Transmission losses, which range from 3.2% to 4.0%, are subtracted from total system load
Loads are calibrated to match the ERCOT-coincident peak value, plus 3.36% to account for company-coincident diversity

## Slide 14: Questions
Questions
Jeff Brown AEP Economic Forecasting (918) 599-2166
Vance Beauregard AEP Texas Transmission Planning (918) 599-2605