## Slide 1: South Texas Electric Cooperative
Load Forecasting Methodology
ROS Meeting, 6/10/10

## Slide 2: Types of Load Forecast
System Load Forecast
Substation Load Forecast for Powerflow Models

## Slide 3: System Forecast
Produced by Clearspring Energy Advisors, LLC, with data obtained from STEC distribution cooperative members.
Coincident forecast.
Annual forecasts are developed for each of the major revenue classes (residential, small commercial, etc.) for customers and kWh per customer. kWh sales are then calculated as the product of the two series. Methods used to project these series include econometric (regression), trending and judgment.
Annual energy is allocated to a monthly series based on historic shares. Using this series and historic monthly load factors, monthly peak demand projections are calculated. The other approach that is sometimes used is to develop econometric models of monthly energy and weather to forecast monthly peaks (the most recent study relied on load factors).
The sum of each individual member forecast is calculated to determine the STEC forecast.

## Slide 4: Substation Forecast
Used in conjunction with the System Forecast to create powerflow models.
Non-coincident forecast.
STEC member cooperatives provide individual substation load data.
Substation loads are adjusted for factors such as distribution feeder swapping and load transfers for new substations.
Substation load projections are extrapolated from historical load data based on 2, 5, and 10 year curve fits.
System knowledge and engineering judgment determine best curve fit.

## Slide 5: DSA (Dataset A)
For the SSWG Data Set A summer peak case non-coincident peak individual substation load forecast data is scaled to fit the STEC System Forecast. Off-peak, spring, fall, and winter loads are scaled from the summer peak case loads based upon historical system load levels.

## Slide 6: DSB (Dataset B)
STEC non-coincident peak individual substation load forecast data is used for the loads in the SSWG Data Set B summer peak cases. The minimum case loads are scaled from the summer peak case based upon historical STEC system load levels.

## Slide 7: Power Factors
Individual substation load data and hourly interval MW and Mvar data are used to determine substation power factors for DSA cases.
For DSB cases the individual substation power factors determined for DSA may be adjusted when power factor corrections are necessary and expected to meet ERCOT requirements.

## Slide 8: Questions
?