## Slide 1: NPRR 220
Bill Blevins
Mgr. Operations Engineering

## Slide 2: What is being removed by this NPRR?
6.5.7.6.2.2 Deployment of Responsive Reserve Service
  (6) ERCOT shall allocate the deployment of Responsive Reserve proportionally among QSEs that provide Responsive Reserve using Resources that are not on high-set under-frequency relays. If ERCOT has deployed 500 MW of Responsive Reserve, and additional Responsive Reserve is needed, ERCOT shall declare that an EEA is in effect and shall follow provisions in Section 6.5.9.

## Slide 3: NERC DCS recovery requirements
R4.1. A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre- Disturbance value.
R4.2. The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. This period may be adjusted to better suit the needs of an Interconnection based on analysis approved by the NERC Operating Committee.

## Slide 4: What ERCOT has developed based on protocols
The automatic term of this deployment is activated by LFC when the system frequency drops below a user defined threshold (e.g. 59.91). The calculated amount of capacity that is required for the automatic term is the amount of MW needed to restore the frequency back to the responsive reserve recall threshold minus the amount of available regulation that can be deployed in 10 minutes.
Whenever the total amount of automatic Responsive Reserve is greater than 500 and the same is limited by 500MW and LFC shall generate an operator alarm. This alarm will assist the Operator to initiate EECP.(now EEA)

## Slide 5: Deployment of RRS in LFC
RRS deploy Freq limit is the frequency which will initiate EMS to calculate RRS deployments.
RRS Recall limit is the range at where RRS will be recalled.
The Primary RRS limit is the Automatic limit on RRS deployment. It can be adjusted by the LFC engineers.
RRS = (Current Frequency-Responsive Reserve Recall Frequency*10*Frequency Bias) – (S(Reg‑Up Ancillary Service Remaining) + S (Available Raise Capacity))
Where S is the sum of all respective QSE’s values from Resources with appropriate status codes

## Slide 6: Issues
SCED may show available room due to congestion.
  Available Capacity=HDL-SCED BP
Units that are not expecting to be deployed will be responding to Unit trips and not those carrying RRS until all Regulation and SCED up room is consumed.(Not necessarily the optimal design.)
RUC should be checking to see if the RRS is able to be deployed. So by LFC requesting the capacity for SCED to use only makes SCED more efficient and will allow SCED to use the Reserves if there are binding constraints on the Available Capacity.

## Slide 7: What is impact based on considering historical Reserve Deployments in 2009
178 Responsive Reserve deployments in 2009
  Of these 45 events required deploying more than 500MWs of Responsive Reserve
  None of these events resulted in declaring a NERC Energy Emergency (EEA)
  None of these deployments resulted in EEA 2B which deploys EILs .
  Since Nodal SCED uses cost curves and constraints to decide how to dispatch basepoints it will always choose whether to use the released capacity…. so less RRS will be used in general

## Slide 8: What is impact continued keeping the 500 MW EEA limit
ERCOT would be required to post on the NERC Reliability Coordinator Information System (RCIS) it is in an EEA due to a unit trip in accordance with NERC standards.
  This would appear that ERCOT was deficient in it’s contingency reserves when in reality it was deploying reserves in response to contingency events.
  The impact of the existing language is that it would slow down ERCOTs response to large unit trips by putting in an administrative step to declare an EEA before using more than 500 MW of the 2300 MWs of Reserves it carries.
  Operators may have to manually calculate the additional Reserves needed.

## Slide 9: What is conflict with the NERC standard
NERC EOP-002-2.1.
R6. If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to:
  R6.2. Deploying all available operating reserve.
DCS events are based on the single Largest Hazard 1354 MW in ERCOT.
  80% of the single largest hazard is a reportable DCS event and these events are typically > 1000 MW unit trips.
NERC EOP-002-2.1 R6.2 ERCOT should be deploying all available operating reserve to comply with DCS events and should not be using EEAs until it has deployed its reserves

## Slide 10: NERC EEA reports

## Slide 11: NERC Reports request information to check on Reserves

## Slide 12: What is impact benefit of the NPRR
This NPRR resets the ability of ERCOT to deploy Reserves as it has historically and removes an administrative requirement placed on ERCOT by Nodal protocols.
Remove dependency on SCED up room to ensure Reserves are used if SCED needs the Reserves.
Allows the system to calculate the reserve required and to release that to SCED for all DCS events.
Removes conflict between NERC standard and protocols.