## Slide 1: Austin Energy Load Forecast Outputs
Annual and monthly energy sales
Net to System Generation
Annual, Monthly Peak Demand
Long Term Hourly Load forecast

## Slide 2: Austin Energy Process Overview
Sector models (Residential, Commercial, Industrial)
  statistically adjusted end use modeling with economic drivers and demand side management trends
  Historical KWh, meter reading schedules, net to system
Net To system is a function of current month sales and next month sales
Peak model is a function of Net to System, temperature and DSM Active Load Control deployment

## Slide 3: Base Case Scenario Assumptions
Risks:
Impacts of New Law – 2007 Energy Independence & Security Act (EISA) & 2009 American Recovery and Reinvestment Act (ARRA)
Magnitude and speed of economic recovery
Impact of major industrial key accounts and their expansion plans
Magnitude of New DSM Savings Goals in light of economic conditions
<number>

## Slide 4: Peak Demand Model Specification
Resource Peak Demand requirements (ResourcePeakMWy,m ):
ResourcePeakMWy,m = PeakMWy,m - DLC y,m
where:
PeakMW y,m - Peak One Hour MW Demand Regression Model estimates before any DSM Direct Load Control (DLC) deployments in forecast year y, month m
DLC y,m - DSM Active Load Control (ALC) Program deployments measured in MW in forecast year y, month m.
Peak One Hour MW Demand Regression Model:
PeakMWy,m = f ( ExtremeDayTempy,m , NTS y,m )
where:
ExtremeDayTemp y,m - Peak Day Extreme Max/Min Temperature in forecast year y, month m
NTS y,m - AE’s Net-to-System Generation or Net Energy for Load Requirements in forecast year y, month m

## Slide 5: Peak Demand Model Specification
In regression model form, the Peak One Hour MW Demand model is specified by the following equation:
where:
NovHDD y,m , DecHDDy,m, JanHDDy,m ,FebHDDy,m ,MarHDDy,m - Peak Day Min. Dry Bulb Temperature Heating Degree-Days for the months of November, December, January, February, and March in year y, month m, based on 55 F heating breakpoint temperature.
FebCDD y,m , MarCDDy,m, AprCDDy,m , …, ,OctCDDy,m - Peak Day Max. Dry Bulb Temperature Cooling Degree-Days from the months of February till October in year y, month m, based on 65 F cooling breakpoint temperature.
TrendVar - Linear Time Trend variable

## Slide 6: One Hour Peak MW Model Performance
Model Stats:

## Slide 7: Austin Energy Load Flow Inputs
System Peak = Substation Loads + Losses
Substation Load Allocation Considerations:
Actual Metered Load History
Distribution Feeder Configuration/Switching History
Abnormal Load Levels for Industrial Customers
Adjust for High-Probability Spot Load Growth
Scale Trended Loads to Match Forecasted Peak