OPERATING PROCEDURE

MANUAL

Reliability Unit Commitment Desk

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, Barcalow | Preparers |  |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| 1.1 | 1.0 / 0 | New procedure – Purpose |  |
| 1.2 | 1.0 / 0 | New procedure – Scope |  |
| 1.3 | 1.0 / 0 | New procedure – Roles/Responsibilities |  |
| 1.4 | 1.0 / 0 | New procedure – General Duties |  |
| 2.1 | 1.0 / 0 | New procedure – System Operator Responsibility and Authority |  |
| 2.2 | 1.0 / 0 | New procedure – Review Weather Data and Updates |  |
| 2.3 | 1.0 / 0 | New procedure – Review Load Forecast Information |  |
| 2.4 | 1.0 / 0 | New procedure – Monthly AS Requirement Posting |  |
| 2.5 | 1.0 / 0 | New procedure – Publish AS Requirements & Review System Conditions Forecast |  |
| 2.6 | 1.0 / 0 | New procedure – Increase AS Capacity needs above Day-Ahead Requirements |  |
| 2.7 | 1.0 / 0 | New procedure – RMR Unit Commitment |  |
| 2.8 | 1.0 / 0 | New Procedure – Three Part Communication |  |
| 3.1 | 1.0 / 0 | New procedure – Tasks prior to Execution of HRUC |  |
| 3.2 | 1.0 / 0 | New procedure – Review, Approve, and Post HRUC Results |  |
| 3.3 | 1.0 / 0 | New procedure – HRUC Failure/Timeline Deviation |  |
| 3.4 | 1.0 / 0 | New procedure – Approve/Reject Resource Decommitment Request |  |
| 4.1 | 1.0 / 0 | New procedure – Tasks prior to Execution of OFFLINE Study |  |
| 4.2 | 1.0 / 0 | New procedure – Tasks prior to Execution of DRUC |  |
| 4.3 | 1.0 / 0 | New procedure – Review, Approve, and Post DRUC Results |  |
| 4.4 | 1.0 / 0 | New procedure – DAM/DRUC Failure/Timeline Deviation |  |
| 5.1 | 1.0 / 0 | New procedure – Tasks prior to Execution of WRUC |  |
| 5.2 | 1.0 / 0 | New procedure – Review WRUC Results |  |
| 6.1 | 1.0 / 0 | New procedure – Market Notices |  |
| 7.1 | 1.0 / 0 | New procedure – Monthly Testing of Satellite Phones |  |
| 7.2 | 1.0 / 0 | New procedure – Responding to Market Participant Issues |  |
| 7.3 | 1.0 / 0 | New procedure – Verbal Dispatch Instruction Form |  |

- Introduction

## 1.1	Purpose

## 1.2	Scope

## 1.3	Roles/Responsibilities

## 1.4	General Duties

- .General Tasks

2.1	System Operator Responsibility and Authority

2.2	Review Weather Data and Updates

2.3	Review Load Forecast Information

2.4	Monthly AS Requirement Posting

2.5	Publish AS Requirements & Review System Conditions Forecast

- Review Load Forecast Information

- Review Weather Data Information

- Publish Ancillary Service Requirements

- Verification of Published A/S Requirements

2.6	Increase AS Capacity needs above Day-Ahead Requirements

2.7	RMR Unit Commitment

2.8	Three Part Communication

- Hourly RUC

3.1	Tasks prior to Execution of HRUC

3.2	Review, Approve, and Post HRUC Results

- VSAT and RUC perform full AC analysis of all contingencies

3.3	HRUC Failure/Timeline Deviation

- HRUC Timeline Deviation

- HRUC Timeline Failure

3.4	Approve/Reject Resource Decommitment Request

- Day-Ahead RUC

4.1	Tasks prior to Execution of OFFLINE Study

4.2	Tasks prior to Execution of DRUC

- By 13:00 each day

- By 13:30 each day

- By 14:00 each day

- By 14:25 each day

- By 14:30 each day

4.3	Review, Approve, and Post DRUC Results

4.4	DAM/DRUC Failure/Timeline Deviation

- DAM Timeline Deviation/Failure

- DRUC Timeline Deviation/Failure

- Weekly RUC

5.1	Tasks prior to Execution of WRUC

- By 02:00 each day

- By 02:30 each day

5.2	Review WRUC Results

- By 04:30 each day

- Emergency Operation

6.1	Market Notices

- OCN

- Advisory

- Watch

- Emergency Notice

- Notifications

- Perform Miscellaneous

7.1	Monthly Testing of Satellite Phones

- Primary Control Center

- Alternate Control Center

7.2	Responding to Market Participant Issues

7.3	Verbal Dispatch Instruction Form

# 1.	Introduction

## 1.1	Purpose

This procedure provides the System Operator assigned to the Reliability Unit Commitment (RUC) Desk with detailed procedures required for performing the duties assigned to that position.  The RUC Desk is responsible for the oversight of the WRUC, DRUC, and HRUC market operation within ERCOT.  The RUC Desk is responsible for ensuring that the RUC Market is facilitated and closed according to market protocols and ERCOT procedures.  The RUC Desk also coordinates with the Real-Time Desk, Transmission and Security Desk, Resource Desk, Shift Engineer, Shift Supervisor and other ERCOT operators as necessary to maintain the ERCOT grid reliability.  The RUC Desk shall also respond to QSE’s inquiries about the RUC commitments and other related tasks.

The Weekly Reliability Unit Commitment (WRUC) process is an eight-day (not including the current Operating Day; i.e., the time for which ERCOT has a COP and Load Forecast) look-ahead planning tool that is used to help ERCOT manage Generation Resources having start up times longer than the DRUC or HRUC study periods as well as project the transmission congestion for the next seven days.  The WRUC process will be executed by the Operator each day at 02:00.  The WRUC DOES NOT send commitment and dispatch instructions to QSEs.

The Day-Ahead Reliability Unit Commitment (DRUC) Market runs for each hour of the next operating day.  It normally commences at 14:30 on the day prior to the operating day and normally concludes at 16:00 on the day prior to the operating day.

The Hourly Reliability Unit Commitment (HRUC) Market will be run every hour for each hour of the rest of the current day and the next operating day after 18:00 or if DRUC for the next Operating Day has run, or else it runs for the next Operating Day.

## 1.2	Scope

The instructions contained in this procedure are limited to those required for the RUC Desk.  Instructions for other ERCOT control room positions are contained in separate procedures, one for each position.  This procedure does not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and perform any other duties required or requested by appropriate ERCOT supervision.

## 1.3	Roles/Responsibilities

ERCOT Shift Supervisor

The Shift Supervisor is responsible for supervising the RUC Desk position and may at times be responsible for performing the instructions contained in this procedure.

ERCOT System Operator, Reliability Unit Commitment Desk

The ERCOT System Operator – Reliability Unit Commitment Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

  - Reliability Coordinator.

  - Balancing Authority

  - Transmission Operator

  - Interchange Coordinator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT electric system.  These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

## 1.4	General Duties

Respond to Market Participant questions and issues.

- Receive questions and issues from Market Participants as they are submitted.

- Respond to Market Participant questions and issues when appropriate information is available.

- Refer any questions or issues for which information is not available to the Shift Supervisor and request that appropriate information is provided.

# 2.	General Tasks

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-2.1 R1 | EOP-001-0 R4.1 | IRO-001-1.1 R3 | PER-001-0 R1 |
|  | TOP-001-1 R1 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

- English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Authority shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

- The SO shall review the ERCOT Daily Operations Plan (DOP) and calculate and post the allocated Responsive Reserve and other Ancillary Services Obligations.  The SO shall ensure compliance with the ERCOT Protocols and Operating Guides on identified transfer limits.  The SO receives all specified notifications for the MPs with regard to energy transactions (Balanced Schedules), AGC control modes, routine adjustments, and equipment limitations or outages.

- The SO processes all Balanced Schedules and Resource Plans. The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate advisories and watches, emergency notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s frequency control system.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan that has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 2.2	Review Weather Data and Updates

Procedure Purpose: To review and update the weather forecast as necessary.

| Protocol Reference | 5.5.2(9)(c) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R1, R5 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The DRUC process uses the weather forecast for each hour of the Operating Day. The HRUC process uses the weather forecast information for each hour of the balance of the RUC Study Period. |
| 1 | Bring up the following web page on Internet Explorer: https://os.ercot.com/weatherdata/ The Meterlogix phone number is (952) 882-4312. NOTE: For a specific database load, each weather station will indicate both successful transmission with the date and time for each. IF: - The last database load is less than one (1) hour old THEN: - Go to Step 2; otherwise continue. IF: - The last database is more than one (1) hour old THEN: - NOTIFY the Shift Supervisor and/or the Help Desk to notify the Market Information System (MIS) On Call person. |
| 2 | Periodically during the day, repeat Step one to ensure the weather updates are running. |
| LOG | LOG any significant problems including any action taken. |

## 2.3	Review Load Forecast Information

Procedure Purpose: To ensure reasonability of load forecast

| Protocol Ref. | 6.5.7.1.13(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002-2 R1, R5 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | REVIEW the hourly load forecast periodically for the operating day and next day in the EMS. |
| 1 | IF: - Adjustments need to be made THEN: - Adjust using one of the following: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) |
| NOTE | The Net Error Subtracted from the Load Forecast is scheduled based on the 2010 AS methodology. If ERCOT subtracts a MW value from the load forecast during the month additional NSPIN will be procured. |

## 2.4	Monthly A/S Requirement Posting

Procedure Purpose:  To notify Market Participants of Monthly Ancillary Service requirements.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 |  | Revision: 0 | Effective Date: |
| --- | --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | - BY the 20th of each month, use the “Free Form” function on the Notice Builder to post the projected Ancillary Services requirements for the following month. (See Section X of the Desktop Reference Guide: Posting Messages to the Market Information System). - Obtain A/S requirement values from Operations Planning: - REGDN - REGUP - RRS - NSPIN - USE a constant value of 2300 MW for Responsive Reserve for hour ending 0100 through hour ending 2400. - Anytime changes to the Ancillary Services requirements are received, inform the market prior to the effective date and time, or immediately, if necessary. |

## 2.5	Publish A/S Requirements & Review System Conditions Forecast

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Ref. | 4.2.1.1 | 4.2.1.2 | 4.2.3 |  |
| --- | --- | --- | --- | --- |
| Guide Ref. |  |  |  |  |
| NERC Std. | TOP-002-2 R1, R5 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Load Forecast Information |  |
| 1 | - REVIEW the hourly load forecast for the and next operating day in the EMS. |
| 2 | IF: - Adjustments need to be made THEN: - Adjust using one of the following: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) |
| NOTE | The Net Error Subtracted from the Load Forecast is scheduled based on the 2010 AS methodology. If ERCOT subtracts a MW value from the load forecast during the month additional NSPIN will be procured. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the and next operating day in the EMS. |
| 2 | Bring up the following web page on Internet Explorer: https://os.ercot.com/weatherdata/ The Meterlogix phone number is (952) 882-4312. NOTE: For a specific database load, each weather station will indicate both successful transmission with the date and time for each. IF: - The last database load is less than one (1) hour old THEN: - Go to Step 3; otherwise continue. IF: - The last database is more than one (1) hour old THEN: - NOTIFY the Shift Supervisor and/or the Help Desk to notify the Market Information System (MIS) On Call person. |
| NOTE | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. |
| 3 | Using the usual sources, evaluate the weather forecast for at least two days out. IF: - Two (2)-Day Ahead scheduling is necessary (and possible) THEN: - Follow the instructions in the “Prepare the Day-Ahead Summary Report” procedure. |
| Invalid SPS/RAP due to Outage |  |
| 1 | Review outages notes and coordinate with Outage Coordinator and/or Shift Engineer to determine if an outage with have an effect on SPS/RAP/PCAPs. IF: - An SPS/RAP will be disabled next day due to an outage, THEN: - Notify the DAM operator to deactivate the invalid SPS/RAP |
| ### Publish Ancillary Service Requirements |  |
| 1 | Verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | PUBLISH the hourly ERCOT system total A/S requirements prior to 0600 |
| ### Verification of published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Operating Day System Conditions; Weather assumptions - The forecast of hourly loads by System Weather Zones and Load Zones Forecast - MIS; Markets; Day-Ahead Market; Operating Day System Conditions; System Weather Zones and Load Zones Forecast - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan |
| LOG | LOG any significant problems including any action taken. |

## 2.6	Increase A/S Capacity needs above Day-Ahead Requirements

Procedure Purpose:  When ERCOT determines the need to increase the Ancillary Services Plan above the Day-Ahead requirements.

| Protocol Reference | 3.9.2(6) | 6.4.8.1.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Identify the need to Increase A/S Capacity |  |
| 1 | IF: - Following the close of the Day-Ahead Market, conditions develop such that additional Ancillary Services may be needed, THEN: - Discuss with the Shift Supervisor the service needed and amounts. - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | IF: - It is determined that A/S capacity is needed, THEN: - Notify all QSEs of intent to procure additional Ancillary Services. - Issue a Watch by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for increasing the A/S capacity from the Day Ahead Market due to [Reason]. An additional [MW] of [Reg-Up, Reg-Down, RRS, Non-Spin] is needed for the following [Hours]. At the completion of this call, ERCOT will open a SASM. [QSE] please repeat this back to me. That is correct, thank you.” |
| 3 | IF: - Increased need of Ancillary Services capacity above that specified in the Day-Ahead, THEN: - Refer to the “Supplemental Ancillary Services Market” procedure for the DRUC Desk. |
| NOTE | If ERCOT determines that it needs more A/S during the Adjustment Period, then the QSE’s allocated portion of the additional A/S may be Self-Arranged. |

## 2.7	RMR Unit Commitment

Procedure Purpose: This task is performed to notify ERCOT Market Operations of RMR resources that are required, in the Day-Ahead, to maintain system security/stability of the ERCOT Interconnection.

| Protocol Reference | 4.3(2) | 4.4.8 | 6.5.1.1(d) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| PBSES | Permian Basin unit for RMR service is dependent both upon the amount of West Texas Wind generation (Wind) as well as total ERCOT Load. When there is high output of Wind, Permian Basin generation may be needed for local congestion; loss of one Odessa EHV 345/138 kV Autotransformer overloading the other Odessa EHV 345/138 kV Autotransformer. However, this may contribute to West – North IROL. During times of low Wind, local generation and/or high loads, the unit may be required for local congestion or for the loss of Odessa EHV –Morgan & Quail Switch 345 kV overloads Big Springs Switch – Big Springs West 138 kV. The steps below have been provided to serve as a recommendation for procuring Permian Basin RMR service, based on the difficulty in predicting when this resource may be needed. If none of these steps identify the need for RMR generation, then none may be needed. |
| 1 | Each day, between 0600 and 0900: DETERMINE, by referring to the system area requirements, which RMR Resources and synchronous condenser Resources may be required for each hour of the operating day. - Consult the Daily Outage Notes for indications of required RMR generation need. - Consult the “ERCOT ISO RMR Weekly Forecast” spreadsheet posted at the link provided below. From this page, click on “RMR Dispatch Forecast Weekly Reports,” and then open the spreadsheet that corresponds to the current operating week. - http://www.ercot.com/gridinfo/generation/rmr/ Note: Changes in system configuration in the area due to planned or forced outages may also create the need to schedule RMR generation. This can also be evaluated through STNET studies, DRUC and HRUC studies. |
| 2 | By 0900, - SELECT the appropriate tabs for each RMR resource and FILL IN the next day’s delivery requirements for secure operations. - The MW values entered should be within the unit’s Low Sustained Limit (LSL) and the High Sustained Limit (HSL). SAVE the file to the “System Operations” server (P:/drive) in the “RMR Unit Commitment” folder. |
| 3 | E-mail the spreadsheet to the “RMR Commitment” group (ERCOT Market Operations (DAM Desk), Internal Settlements, DRUC Desk, Shift Supervisors and various internal ERCOT personnel). - Output Schedules and/or Energy Offer Curves for RMR resources will be created by ERCOT Market Operations. |
| 4 | Periodically review the quantities of RMR Services deployed by ERCOT for each previous hour of the current Operating Day - MIS; Grid; Generation; Reliability Unit Commitment; ********* |

## 2.8	Three-Part Communication

Procedure Purpose:  To ensure that three part communication is used for all directives.

| Protocol Reference | 6.5.7.8(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |

# 3.	Hourly RUC

## 3.1	Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit/de-commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 5.3(3) | 6.3.1(1) | 6.3.2(2) |
|  | 6.3.2(3)(a) | 6.4.1 | 6.4.2.5(3)(b) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Tasks prior to execution of HRUC |  |
| NOTE | The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved. |
| Continuous Monitoring | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow IF: - The EMSI Workflow Controller (Time Stamped – runs every 5 minutes) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous), THEN: - Notify EMMS Production Support, Shift Engineer and Shift Supervisor |
| Load Forecast | Periodically monitor the Load Forecast to ensure it is accurate: IF: - Adjustments need to be made, they will be done in the EMS and updated to the MMS, THEN: - Adjust using one of the following: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) |
| Wind Forecast Updates | Periodically monitor the Wind Forecast and verify data is updating: IF: - Wind forecast is not updating, THEN: - Notify Supply Integration & Grid Application, aka Operations Planning Support, - Be aware that results could be skewed for next HRUC run. |
| RMR Consideration | IF: - An RMR unit needs to be considered in HRUC, THEN: - Notify the QSE to update COP status to “OFF”. IF: - An RMR unit is needed but is not to be considered in HRUC, THEN: - Commit unit before HRUC is executed. |
| COP Validation | REVIEW REFERENCE DISPLAY: Market Participation>Monitoring>Event Manager>Events IF: - A Resource Forced Outage has occurred and the QSE has not update their COP, OR - COP Validation ERROR THEN: - Select “START-NOW" in the Status column - Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere. |
| Review AS Differences | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE Market Participation>Monitoring>Event Manager>Events IF: - AS Differences exist, THEN: - Verify the Notification Flag is set to “Y”, SELECT: - Send Notification to the appropriate QSE. |
| Bad/Suspect Telemetry | Periodically monitor: IF: - Notified by Real-time desk or Shift Engineer of bad/suspect telemetry, THEN: - Determine if issues will be resolved for next HRUC run, - Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved. - Consider requesting Shift Engineer to manual over-ride of SCADA values (Be aware that this could skew the results), If it’s determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - An RMR unit is needed but is not to be considered in HRUC, THEN: - Commit unit before DRUC is executed. IF: - Additional resources are needed to solve for transmission congestion, THEN: - Consult with the Shift Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods, THEN: - Change ‘blank’ to ‘Commit’, - List reason. |
| Set Flags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the HRUC input data, CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No” and - “Use Save case set to “Yes” |
| Deselect Contingencies | IF: - It has been determined with the help of Engineering Support that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC, THEN: - After the Shift Engineer has deselected the contingency, - Post to the MIS Secure Area contingency that was deselected with the reason and no later than one hour after deselection. |
| VERIFY | REVIEW REFERENCE DISPLAYS: System Administration>Data Management - Connect to Schema is set to ONLINE Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” Market Operation>EMS Interface>EMSI Workflow Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour |
| ### Verify HRUC has executed |  |
| 1 | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Verify execution of the HRUC sequence by XX:10 |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 3.9(7) | 3.9.2(4)&(5) | 5.1 (7)&(9) | 5.3(3) |
| --- | --- | --- | --- | --- |
|  | 5.5.1(11) | 5.5.2 | 5.5.3 | 6.3(1) |
|  | 6.3.1(1) | 6.3.2(2) | 6.4.8.1.2 | 6.4.8.1.3 |
|  | 6.5.9(2) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| MONITOR | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Market Participation>Monitoring>Event Manager>Events - Monitor the HRUC Workflow display to determine when it is complete. - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - The load forecast is not reasonable for each hour, THEN: - Be aware that this could skew the HRUC results, IF: - Any under/over generation, THEN: - Notify the Resource Desk Operator and the Shift Supervisor. |
| QSE’s Request to Change Resource supplying A/S | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - On detection of a change in COP for Resources providing A/S, THEN: - Review the impact on deliverability and communicate to the QSE if the change is not approved. - QSE must update its COP to reflect the decision. IF: - AS Infeasibilities exist, THEN: - Send Notification, IF: - AS Replacement Approval is needed. THEN: - Review and determine if possible, IF: - Not acceptable, THEN: - Enter NO in the Approved column, - Enter reason in the comment column, - Send notification. If ERCOT does not act on the request by the beginning of the Operating Hour in which the change will take effect, the request is deemed approved. |
| A/S Insufficiency From SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency, THEN - Commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Section X of the Desktop Reference Guide. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints, THEN: - Provide the following information to QSE with two hours’ advance notice of: - amount by which the QSE must reduce the A/S currently allocated to each affected Resource - start and stop times of the reduction, - Notify the Real-Time Desk Operator and the Shift Supervisor. THEN: - Within the two-hour advance notice period, the QSE may do one or more of the following: - Substitute capacity from other Resources represented by that QSE to meet its A/S supply responsibility - Substitute capacity from other QSEs using A/S trades; or - Inform ERCOT that all or part of the A/S capacity needs to be replaced IF: - A QSE elects to substitute capacity, THEN: - Determine the feasibility of the substitution IF: - The substitution is deemed infeasible, THEN: - Notify the QSE, - Notify the Shift Supervisor and determine if a SASM should be opened, IF: - It is determine if a SASM should be opened, THEN: - Instruct the Resource Desk Operator to issue a Watch by the Hotline and MIS Posting, - Instruct the DRUC Desk Operator to execute a SASM. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity, IF: - Invalid, no further action is required, - Valid, THEN: - Create Suggestion Plan for Constraint, - Manually commit resources as needed Refer to Section X of the Desktop Reference Guide. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit, THEN: - Determine the validity, - Determine the temporal constraints for each of the units. IF: - A HRUC recommended resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and there is no reliability reason requiring the resource commitment decision to be made immediately. THEN: - ERCOT shall de-select the resource prior to approving the HRUC study - Change ‘Commit’ to ‘blank’, - List reason. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters Every effort should be made to manually commit resources that are needed before HRUC execution. IF: - Additional resources are needed to solve for transmission congestion and were not picked up in the HRUC run, THEN: - Commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason. |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments, Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| ### VSAT and RUC perform full AC analysis of all contingencies |  |
| NOTE | IF: - RUC cannot complete the process, THEN: - Notify the Transmission & Security Desk Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable after all necessary modifications have been made, THEN: - Approve the results, OR IF: - The results are unacceptable, THEN: - Determine whether to rerun HRUC, OR - Follow the Manage HRUC Timeline Deviation/Failure |
| LOG | Log actions taken. |

## 3.3	HRUC Failure/Timeline Deviation

Procedure Purpose:  To address situations in which the HRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain Emergency conditions.

| Protocol Reference | 6.5.9.3.4 (d) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### HRUC Timeline Deviation |  |
| Warning or Error Messages | IF: - HRUC market software gives “Warning” or “Error” messages, THEN: - Refer to (Section X of the Desktop Reference Guide) |
| By XX:25 | IF: - Warning or Error messages could NOT be resolved by XX:25, THEN: - Discuss with EMMS Production Support, Shift Engineer and Shift Supervisor whether to approve the market results or not. |
| Run Aborted By XX:50 | IF: - ERCOT varies from timing requirements or omits one or more Adjustment Period and Real-Time procedures, OR - HRUC results are NOT approved by XX:50, THEN: - Discuss with EMMS Production Support, Shift Engineer and Shift Supervisor and decide whether to abort the current run, IF Aborted: - Issue an Emergency Notification by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice for the timeline deviation of the HRUC at [Hour Ending] due to [state issue]. VDIs will be issued if needed. [QSE] please repeat this back to me. That is correct, thank you.” |
| Commit/ De-Commit Resources By VDI | IF Needed: - Commit/De-Commit Resources by issuing, VDIs for the following: - Changes in the following from the last HRUC run - COP Resource Status - COP AS - Load Forecast - Wind Forecast - Forced Outage - Delay in Planned Outage - Resolving transmission constraints identified using EMS Network Application Study Network. |
| ### HRUC Timeline Failure |  |
| Failure | IF: - HRUC software fails without expectation of timely repair, THEN: - Notify EMMS Production Support, Shift Engineer and Shift Supervisor - Issue an Emergency Notification by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice for the failure of the HRUC software at [Hour Ending] due to [state issue]. VDIs will be issued if needed. [QSE] please repeat this back to me. That is correct, thank you.” |
| Commit/ De-Commit Resources By VDI | IF Needed: - Commit/De-Commit Resources by issuing, VDIs for the following: - Changes in the following from the last HRUC run - COP Resource Status - COP AS - Load Forecast - Wind Forecast - Forced Outage - Delay in Planned Outage - Resolving transmission constraints identified using EMS Network Application Study Network. |

## 3.4	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Adjustment Period.

| Protocol Reference | 5.5.3 | 6.4.6.2 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Adjustment Period |  |
| NOTE | The Adjustment Period is for each Operating Hour, the time between 1800 in the Day-Ahead up to the start of the hour before that Operating Hour. |
| 1 | A QSE may request to decommit a Resource for any interval that is not a RUC-Committed Interval by indicating a change in unit status in the QSE’s COP. IF: - A Resource Status changes from “ONLINE” to “OFFLINE” during the hour before the HRUC run, HRUC identifies this as a request by the QSE to de-commit the Resource, THEN: - Results show that the de-commitment request is denied if next HRUC run commits the Resource. |
| 2 | Log actions taken. |

# 4.	Day-Ahead RUC

## 4.1	Tasks prior to Execution of OFFLINE study

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the DRUC process. Perform an unconstrained OFF-LINE study to compare with the normal DRUC study.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 6.3.1(1) | 6.3.2(3)(a) | 6.4.2.5(3)(b) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Before a DRUC study is performed |  |
| Setting parameters for OFFLINE study | REVIEW REFERENCE DISPLAY: System Administration>Data Management CHANGE: - Connect to Schema TO: - OFFLINE |
| Verify parameters for OFFLINE study | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “No”, if prior to 14:30 - “Use Save case set to “No” Market Operation>EMS Interface>EMSI Workflow Market Operation>EMS Interface>EMSI Workflow Messages - EMSI has completed successfully within the last hour |
| EXECUTE off-line study | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages - The RUC study time interval is set properly, - The “Execution Mode” is set to “Unconstrained”, - The current data management mode is “OFFLINE”, - Execute the entire DRUC sequence (Run All) in OFFLINE mode. |

## 4.2	Tasks prior to Execution of DRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 6.3.1(1) | 6.3.2(3)(a) | 6.4.2.5(3)(b) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### By 13:00 each day, perform the following |  |
| COP | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>Market Operator Data> Missing COP Check Market Participation>Monitoring>Event Manager>Events VERIFY: - “Missing COP Check” has automatically notified the QSEs of missing COPs SELECT: - “START-NOW" in the Status column if not already completed by Market Operations. |
| Load Forecast | Review the Day Ahead Load Forecast in the EMS IF: - Adjustments need to be made in the EMS, THEN: - Adjust using one of the following: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) Reference Displays: - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) - Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of DRUC. |
| Outage Notes/Off-Line Studies | IF: - Resources are needed for identified Voltage issues, THEN: - Once COPs have been updated, identify the appropriate resources that can be utilized if needed. |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow IF: - The EMSI Workflow Controller (Time Stamped – runs every 5 minutes) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous), THEN: - Notify EMMS Production Support, Shift Engineer and Shift Supervisor |
| Bad/Suspect Telemetry | CHECK: - EMS Operator Alarms for major Generation Resources statuses with BAD/SUSPECT quality codes, IF: - Issues exists and will not be resolved before DRUC execution, THEN: - Discuss with Shift Supervisor if the DRUC should be run or delayed until the issues can be resolved. - Consider requesting Shift Engineer to manual over-ride of SCADA values (Be aware that this could skew the results), If it’s determined to delay DRUC, follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| RMR Consideration | IF: - An RMR unit needs to be considered in DRUC, THEN: - Notify the QSE to update COP status to “OFF”. IF: - An RMR unit is needed but is not to be considered in DRUC, THEN: - Commit unit before DRUC is executed. |
| ### By 13:30 each day, perform the following |  |
| Deselect Contingencies | IF: - It has been determined with the help of Engineering Support that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC, THEN: - After the Shift Engineer has deselected the contingency, - Verify posting of the contingency that was deselected on MIS Secure Area. The reason should be noted and posted no later than one hour after deselection. |
| NOTE | The DRUC process may not be used to buy Ancillary Service unless the Ancillary Service Offers submitted in the DAM are insufficient to meet the requirements of the Ancillary Service Plan. |
| NOTE | By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure. |
| ### By 14:00 each day, perform the following |  |
|  | As time permits, try to contact QSEs that have NOT submitted a COP for the DRUC study period. |
| Review AS Differences | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE IF: - AS Differences exist, VERIFY: - HRUC Desk Operator has sent Notification, IF: - Not, THEN: - Verify the Notification Flag is set to “Y”, SELECT: - Send Notification to the appropriate QSE. |
| Long Lead Times | Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. IF: - Resources are identified, THEN: - Commit the necessary resources as needed. |
| ### By 14:25 each day, perform the following |  |
| NOTE | If the DAM did not complete by 1330, then DRUC likely needs to be delayed. MPs need an hour between the completion of DAM and the opening of DRUC. |
|  | Verify that the DAM has completed. IF: - DAM is aborted/ postponed after 1430, THEN: - Follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| Setting parameters for ONLINE | REVIEW REFERENCE DISPLAY: System Administration>Data Management CHANGE: - Connect to Schema TO: - ONLINE |
| VERIFY | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” Market Operation>EMS Interface>EMSI Workflow Market Operation>EMS Interface>EMSI Workflow Messages - EMSI has completed successfully within the last hour |
| ### At 14:30 each day, perform the following |  |
| DSI | EXECUTE: - The DSI sequence VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact EMMS production support personnel immediately to determine the cause and expected time of resolution. |
| VERIFY | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MI DAM AS Insufficiency This display will give the Operator an indication if any A/S insufficiencies have occurred in DAM. If insufficiencies exist, the Operator can start looking at resources that can be committed to resolve the insufficiency in DSP. |
| E-tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule - Verify that E-tags are being imported into the MMS. |
| Verify | - Identify and correct Bad/Suspect Telemetry - Modify Input for Block Load Transfer (BLT) movement - Modify Input for Verbal Dispatch Instructions Refer to Section X of the Desktop Reference Guide |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays>External Input Data>DSI Data Processes>DSI Operator Manual Commitment IF: - An RMR unit is needed but is not to be considered in HRUC, THEN: - Commit unit before DRUC is executed. IF: - Additional resources are needed to solve for voltage issues, THEN: - Consult with the Shift Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods, THEN: - Change ‘blank’ to ‘Commit’, - List reason. |
| Set Flags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the DRUC input data, CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No” and - “Use Save case set to “Yes” |
| EXECUTE | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages Execute the entire DRUC sequence (Run All). |
| STNET Studies | Notify: - Shift Engineer to run NSA for each hour of the next operating Day. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 5.1 (9)&(11) | 5.3.(3) | 5.5.1(9) | 5.5.2 |
| --- | --- | --- | --- | --- |
|  | 5.5.3(2) | 6.3.1(1) | 6.4.6(4) | 6.4.8.1(3) |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | QSE’s may not change the quantity provided of each type A/S awarded through the procurement process or the aggregate amount of self-arranged A/S from the DAM. |
| MONITOR | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages Market Participation>Monitoring>Event Manager>Events |
| REVIEW | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with the Market Operations and Shift Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete. - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, follow the “Resolve Unreasonable Results” section of the procedure Refer to Section X of the Desktop Reference Guide |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour - Any under/over generation THEN: - Notify the HRUC Desk Operator |
| NOTE | The RUC process may not be used to buy A/S unless the A/S Offers submitted in the DAM are insufficient to meet the requirements of the A/S Plan. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - Notified from Market Operations of A/S Insufficiency from DAM, THEN - Commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints. - Refer to Section X of the Desktop Reference Guide. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist, THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the HRUC Desk Operator THEN: - The QSE may do one of the following: - Substitute capacity from Resources represented by that QSE; - Substitute capacity from other QSEs using A/S Trades; or - Ask ERCOT to replace the capacity IF: - A QSE elects to substitute capacity, THEN: - Determine the feasibility of the substitution IF: - The substitution is deemed infeasible or QSE asks ERCOT to replace the A/S, THEN: - Notify the Shift Supervisor and determine if a SASM should be opened, |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity IF: - Invalid, no further action is required - Valid THEN - Locate the constraint on the DSP Constraint Summary display - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, notify the HRUC Desk Operator OR, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | DRUC Operators can decide to postpone a commitment, if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit THEN - Determine the temporal constraints for each of the units IF: - A DRUC recommended resource start-up time allows enough time to re-evaluate the need for its commitment in the HRUC Study Period, and there is no reliability reason requiring the resource commitment decision to be made immediately. THEN: - ERCOT shall de-select the resource prior to approving the DRUC study, - Change ‘Commit’ to ‘blank’, - List reason - Communicate any Resources removed from DRUC to the HRUC Operator. |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Every effort should be made to manually commit resources that are needed before DRUC execution. IF: - Additional resources are needed to solve for transmission congestion or voltage issues and were not picked up in the DRUC run, AND - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period. THEN: - Change ‘blank’ to ‘Commit’ - List reason |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unresolvable. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments Determine if: - Outage related - Possible Network Model error - COP error for Combine Cycle configurations / JOU - Qualifying Facilities should be de-committed ONLY as a last resort THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made, THEN: - Approve the results. -OR- IF: - The results are unacceptable, THEN: - Determine whether to rerun DRUC, OR - Follow the Manage DRUC Failure/Timeline Deviation procedure |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |

## 4.4	DAM/DRUC Failure/Timeline Deviation

Procedure Purpose: To address situations in which the DAM/DRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain Emergency conditions.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### DAM Timeline Deviation/Failure |  |
| A/S Insufficiency | ERCOT will not begin executing the DAM sooner than 30 minutes after issuing a Watch. IF: - Notified by Market Operations of a A/S insufficiency in the DAM results, THEN: - Issue a by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due insufficient Ancillary Services or Energy Offers in the DAM. ERCOT is requesting additional Ancillary Service Offers. [QSE] please repeat this back to me. That is correct, thank you.” |
| DAM Timeline Deviation | IF: - Notified by Market Operations that the DAM Market timeline is deviated, THEN: - Notify Shift Supervisor - Issue an Emergency Notice by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice for the timeline deviation of the Day Ahead Market on [effected date] due to [state issue]. [QSE] please repeat this back to me. That is correct, thank you.” |
| DAM Failure | IF: - Notified by Market Operations that the DAM Market has failed THEN: - Notify Shift Supervisor - Issue an Emergency Notification by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to the failure of the Day Ahead Market on [effected date] due to [state issue]. ERCOT will require all schedules and trades to be submitted in the Adjustment Period. ERCOT will be opening a SASM at [XX:XX]. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### DRUC Timeline Deviation/Failure |  |
| NOTE | After 1800, HRUC will run for the rest of the current day and the next day even if DRUC has not run successfully. |
| DRUC Delay | By 16:00 IF: - DRUC is delayed due to a delay in DAM run THEN: - Notify Shift Supervisor - Issue an Emergency Notification by the Hotline and MIS Posting Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice for the timeline deviation of the DRUC on [effected date] due to [state issue]. DRUC will be starting at [time], instead of the normal time of 1430. [QSE] please repeat this back to me. That is correct, thank you.” |
| ABORT Process | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow By 18:00 IF: - DRUC results cannot be approved, THEN: - “Abort DRUC Process” |
| Software Failure | IF: - DRUC software fails without expectation of timely repair, THEN: - Notify EMMS Production Support, Shift Engineer and Shift Supervisor - Issue an Emergency Notification by the Hotline and MIS Posting - Notify the HRUC Desk Operator that they may need to procure the necessary resources for the following Operating Day Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to a software failure of the DRUC Market. It is not expected to function in time to clear the market for [state date]. [QSE] please repeat this back to me. That is correct, thank you.” |

# 5.	Weekly RUC

## 5.1	Tasks prior to Execution of WRUC

Procedure Purpose:  A look-ahead planning tool that is used manage Generation Resources having start up times longer than the DRUC or HRUC study periods as well as project the transmission congestion for the next 168 hours.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.2(5) | 6.3.1(1) |
| --- | --- | --- | --- | --- |
|  | 6.3.2(3)(a) | 6.4.2.5(3)(b) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### By 02:00 each day, perform the following |  |
| NOTE | The load forecast only goes out 168 hours. The study period for WRUC will be for that time period. |
| Load Forecast | Review the Load Forecast in the EMS IF: - Adjustments need to be made in the EMS, THEN: - Adjust using one of the following: (Refer to Section X of the Desktop Reference Guide: Suggested Method for Task Performance) Reference Displays: - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) - Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of WRUC. |
| Outage Notes/Off-Line Studies | IF: - Resources are needed for identified Voltage issues, THEN: - Identify the appropriate resources that can be utilized if needed. |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow IF: - Ensure the “Retrieve WRUC Data” is set to “YES” in EMSI - The EMSI Workflow Controller (Time Stamped – runs every 5 minutes) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous), THEN: - Notify EMMS Production Support, Shift Engineer and Shift Supervisor |
| NOTE | By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure. |
| VERIFY | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>UC Displays>WRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>WRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>WRUC Displays>DSI Displays>DSI Execution Control Parameters - “Check Market Status set to “Yes”, - “Use Save case set to “No”, Verify the following WRUC settings are correct. - EMSI has completed successfully within the last hour, - The RUC study time interval is set properly, - The “Execution Mode” is set to “constrained”, - The current data management mode is “ONLINE”, - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. |
| ### By 02:30 each day, perform the following |  |
|  | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages EXECUTE: - The DSI sequence VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact EMMS production support personnel immediately to determine the cause and expected time of resolution. |
|  | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>WRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the WRUC input data, CHANGE: - The appropriate flags to “No”, to prevent the data from being over-written. - “Retrieve MF Interface Data”, - “Retrieve MI Interface Data” and - “Retrieve EMS Interface Data” |
| EXECUTE | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages Execute the entire WRUC sequence (Run All). |

## 5.2	Review WRUC Results

Procedure Purpose:  To identify commitments with a long lead time and develop a list of violated/binding constraints that have a high-probability of being binding in SCED or DAM.

| Protocol Reference | 5.1 (9)&(11) | 5.5.1(9) | 5.5.2 | 6.3.1(1) |
| --- | --- | --- | --- | --- |
|  | 6.4.6(4) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | WRUC doesn’t send commitments or dispatch instructions to QSEs. WRUC does not retrieve any QSE-submitted Three-Part Supply Offers. WRUC relies exclusively on the QSE-submitted COPs. |
| MONITOR | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity IF: - Invalid, no further action is required - Valid THEN - Locate the constraint on the DSP Constraint Summary display - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources |
| Long Lead Times | Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. |
| ### By 04:30 each day, perform the following |  |
| High-probability constraints | Review the binding /violated constraints and check the outage notes to see if any predicted constraints are missing in the list. IF: - Identified or notified by the Transmission & Security Desk Operator of any Real Time congestion to be binding, THEN: - Add those constraints to the list, if they are not already listed, - Send the list to the Shift Engineer. The Shift Engineer will review it and update it if needed. and post before 6 AM, in MIS, the updated list of transmission constraints as that having a high-probability of being congested in SCED or DAM in the next seven days.After the Shift Engineer has deselected the contingency, Post to the MIS Secure Area contingency that was deselected with the reason and no later than one hour after deselection. |
| NOTE | The Shift Engineer will post before 6 AM, in MIS, the updated list of transmission constraints as that having a high-probability of being congested in SCED or DAM in the next seven days. - “List of transmission constraints that have a high-probability of being binding in SCED or DAM” |
| Long Lead Times | Create a list of all Resources committed by WRUC, which have startup time greater than 24 hours. These Resources may be candidates for “manual commitment” in the upcoming DRUC case. |
| LOG | - Any unreasonable constraints/commitments - Commitments with long lead time and any possible alternatives - List of violated constraints and long lead time Resources, if any, which are the only solution for resolving those violated constraints. - List of transmission constraints that have a high-probability of being congested in the next seven days. - Any capacity insufficiency/surplus identified (to send Market Notice) |

# 6.	Emergency Operations

## 6.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - There is a hurricane in the Gulf with >20% chance of landfall in Texas according to the National Hurricane Center (http://www.nhc.noaa.gov). - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TSPs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a hurricane in the Gulf with >50% chance of landfall in Texas according to the “National Hurricane Center” http://www.nhc.noaa.gov. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a hurricane in the Gulf with expected landfall in Texas. - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procedure Ancillary Services from existing offers. - ERCOT may instruct TSPs or DSPs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time deadlines. - DRUC failure - HRUC failure - SASM failure - SCED failure |
| ### Notifications |  |
| HOTLINE | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TSPs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TSP] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a [state Notice type] for [state reason]. [TSP] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| POST | All notices must be posted on the MIS |
| LOG | Make log entry. |

# 7.	Perform Miscellaneous

## 7.1	Monthly Testing of Satellite Phones

Procedure Purpose:  To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001 R2 | EOP-005 R5 |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with Transmission Service Providers (TSPs) As the Shift Supervisor makes the call to the individual TSP, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TSP. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Section X of the Desktop Reference Guide) for a list of the TSPs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Bridge are Desk specific, located on the bottom right of page 11 of the MX Turret phone as identified below: - BKST DRUC – DRUC Desk - BKST HRUC – HRUC Desk - BKST RTD – Real-Time Desk - BKST TS#1 – Transmission Desk #1 - BKST TS#2 – Transmission Desk #2 |
| 1 | IF: - The preprogrammed number does not function correctly, THEN: - Refer to the ERCOT Satellite Phone User Guide (See Section X of the Desktop Reference Guide) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TSPs fails to connect to the Bridge call, THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the TSPs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |

## 7.2	Responding to Market Participant Issues

Procedure Purpose:  Responding to Market Participant issues regarding website questions, SCED deployments, LMPs, etc.

| Protocol Reference | 6.5.7.1.13(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If the MPs are not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |
| 2 | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |
| 3 | If the MPs is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |
| 4 | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |

## 7.3	 Verbal Dispatch Instruction (VDI) Form

|  |  |  |  | VDI# ___________________________ |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Date Issued |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | THIS IS FOR SETTLEMENTS INFO. |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | ONLY. NO INSTRUCTION WAS |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | GIVEN. |  |  |  |  |
| VERBAL DISPATCH INSTRUCTION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Operating Date (mm/dd/yy)_________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (Date of Occurrence) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ERCOT System Operator ______________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | (ERCOT system operator) |  |  |  |  |  |  |  |  |  |  |  |
| issued a Verbal Dispatch Instruction to ___________________________, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | (Receiving Entity) |  |  |  |  |  |  |  |
| Operator, ________________________ at _________________________, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (Receiving entity’s operator) |  |  |  |  |  |  |  | (Time & Date issued) |  |  |  |  |  |  |
| The instruction was as follows: Example: “Have the output of ‘unit x1’ at |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 MW for intervals ending “1430” thru “1445”. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ______________________________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ______________________________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ______________________________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The Instruction was given due to the following reasons: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ______________________________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit that was given instructed output level:_____________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Output Level at time of instruction: ___________________MW |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Desired Output Level: “Have unit at ___________________MW” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Duration of Instruction: “Have unit at __________________MW, for the following |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Intervals.” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hour/Interval Ending_____________ through Hour/Interval Ending____________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Operator VDI Confirmation:____________(verified Entity Operator has repeated Instruction) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |