Dynamics Working Group

Procedural Manual

Revision 6

ROS Approved

January 14, 2010

TABLE OF CONTENTS

I.	Introduction	5

II.	Dynamics Data	6

A.	General	6

B.	Dynamics Data for Equipment Owned by Generating Entities (GE) or Power Generation Companies (PGC)	6

1.	Dynamics Data Requirements for New Equipment	6

2.	Updates to Existing Dynamics Data	10

C.	Dynamics Data for Equipment Owned by Load Entities and Transmission-Distribution Service Providers (TDSP)	11

1.	Load Acting As a Resource (LaaR, high-set relays for frequency set points above 59.3 Hz)	11

2.	Underfrequency Firm Load Shedding Relay Data (UFLS)	11

3.	Undervoltage Load Shedding Relay Data	11

4.	Protective Relay Data	11

5.	Load Model Data	12

6.	Other Types of Dynamics Data	12

D.	Missing Dynamics Data	13

E.	Dynamics Data Storage	13

III.	Overview of DWG Activities	14

A.	Updating Dynamics Data and Flat Starts	14

1.	Initiating Annual Dynamics Data Update	14

2.	Dynamics Data Screening	14

3.	Flat Start	14

B.	Post Flat Start Activities	15

1.	Distribution of Flat Start Results and the Dynamics Data Base	15

2.	Stability Book	15

C.	Other DWG Activities	15

1.	Dynamic Disturbance Recording (DDR) Equipment Annual Review	15

2.	Event Simulation	17

# Introduction

Each TO (Transmission Owner) shall have a designated Dynamics Working Group (DWG) member.  Each designated DWG member shall be identified in a DWG members list that is communicated to ROS (Reliability and Operations Subcommittee) by the DWG Chair The list will be updated in the monthly DWG report to ROS whenever membership changes and annually in the first DWG report to ROS after ROS approves a new DWG Chair.

To adequately simulate the behavior of the ERCOT system it is necessary to develop and maintain dynamic simulation-ready base cases and associated dynamics data files using actual equipment data together with appropriate dynamic simulation software.  The ERCOT Steady State Working Group (SSWG) power flow cases provide transmission system representations which, along with the dynamics database, are used by the Dynamics Working Group to create dynamic simulation cases ready to run under Siemens PTI’s PSS/E software.

# Dynamics Data

## General

For conventional generation, generator dynamics data includes generator, governor, excitation system, power system stabilizer, and excitation limiters.  Associated generator data includes main power transformer, auxiliary and start-up transformers, start-up load, running load, and protection functions likely to trip the machine during an event.  For wind generation, dynamics data includes the items listed in section II B 1.  Other types of data needed for dynamics study unrelated to the generator include load shedding relay data, protective relay data, FACTS devices (e.g., DVARS, SVC, STATCOM, SMES), DC connections, and Variable-Frequency Transformer data.  The facility owner is responsible for providing the dynamics models and data to ERCOT via the RARF.  Information shall be provided with the legal authority to provide the information to all ERCOT TO/TOPs. If any of the information is considered confidential, the facility owner shall indicate such, and the information will be held confidential under ordinary ERCOT Transmission Provider code-of-conduct rules.

For Resources installed prior to 1990 estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained..

Some studies, such as subsynchronous resonance studies or other special dynamic studies, may require additional data not normally collected, such as switchable shunts, transformer taps dynamics, load model data, etc.  Such data is collected on an as needed basis.  The Resource owner is responsible for providing such data to ERCOT upon request.

## Dynamics Data Requirements for Generating Entities (GE)

### Dynamics Data Requirements for New Equipment

Note: This section addresses the requirements stated in sections R.1.1, R.1.2, and R.1.5 of NERC Standard MOD-013-1.

Whenever new generation facilities [as defined in Operating Guide 3.1.4] larger than 10 MW connect to the ERCOT system, the GE connecting the generation is required to go through the formal “ERCOT Generation Interconnection or Change Request Procedure”.  An integral part of this process is the submission of generator dynamics data and associated generator data for each unit.  Planning Guide Sections XXX define the connection process and data submittal requirements.  The data submittal requirements in this section are additional requirements as referenced in Planning Guide Section XX, INTERCONNECTION DATA FEES AND TIMETABLES, Generation Plant Data Requirements.  The interconnection process usually results in the data evolving from “conceptual” to “as built”. The most current facility data or expected performance data should be submitted to ERCOT with the initial study request.  “As built” data is required for completed generation facilities.

Data submitted for stability models shall be compatible with ERCOT standard models or Siemens PSS/E standard library models.  If there is no compatible model(s), the GE is required to work with a consultant and/or software vendor to develop and supply accurate/appropriate models (user written models) along with associated data.  A user written model is any model that is not an ERCOT standard model or Siemens PSS/E library model.

Siemens PSS/E standard library models allow time constants of less than 1 cycle (0.016667 seconds) but use an internal method so that a ¼ cycle (0.004167 seconds) integration time-step can be used for simulations.  For example, Siemens PSS/E uses an internal integration for models that would normally require less than a ¼ cycle integration time-step.  User written models shall not require an integration time-step less than ¼ cycle.  Should any model constant be less than one cycle, the model shall incorporate an internal method to allow for a ¼ cycle integration time-step.  No user written model shall restrict the DWG from using any integration time-step less than or equal to a ¼ cycle in simulations.

GEs are responsible for tuning generator, exciter, power system stabilizer, excitation limiters, and governor model parameters. Resource data submissions are made to ERCOT via the RARF. If ERCOT, the interconnecting TO, or the DWG identifies inappropriate or incomplete dynamics data, ERCOT will take action to resolve discrepancies with the Resource owner.  The TO (Transmission Owner) to which the Resource is connected is responsible for incorporating the dynamics data received from ERCOT into the ERCOT Dynamics database during annual updates.

Traditional Resources Interconnecting More Than 10 MVA of Generation Capacity:

- The Resource shall provide all dynamics data and associated generator data.  The data must be provided in the form of PSS/E model data sheets and dynamics model records with tuned parameters.

- Classical model data is not acceptable.

- Estimated and/or typical model data is not acceptable for units after they are already connected to the ERCOT system.

- In accordance with Section XX of the Planning Guides, all non self-serve generation connected to the transmission system at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled.  This translates to (1) no lumping of generating units and (2) explicit modeling of each step-up transformer.

- Planning Guide Section XX states that station auxiliary load for generating plants should not be modeled explicitly at the generator bus.  However, explicit modeling of station auxiliary load may be necessary for dynamic simulations.  For this reason, Resources are required to submit associated generator data, as defined above.

- All combustion turbine and combined cycle generation shall use the CIGRE governor model, as developed by Siemens PTI and implemented by ERCOT, unless explicitly exempted by the DWG.

All Wind Facilities:

In order to adequately simulate the behavior of the ERCOT system, it is necessary for all wind plants to be modeled.  Unlike traditional generation resources, wind generators do not have generic models.  In addition, each wind technology requires a substantially different model to accurately simulate its dynamic performance.  The Resource owner is responsible for providing all models and data for their facility.. There are three sources of wind models: the ERCOT wind models; Siemens PTI wind models; and other, including the equipment manufacturer. If an ERCOT or Siemens PTI wind model is not appropriate for the facility, the Resource shall obtain the most accurate and appropriate model and the associated data for their wind plant from the manufacturer, and supply it to ERCOT and the TO to which it is connected, with the legal authority to provide such data to all transmission providers.  Models and data will be held confidential under ordinary ERCOT Transmission Provider code-of-conduct rules.  Regardless of the model source, the Resource shall provide the following data:

- Model shall be compatible with the PSS/E version currently used in ERCOT.

- Model, data and description of voltage control method.

- Model, data and description of how the Resource will meet ERCOT reactive requirements.

- A one-line diagram of the proposed facility.

- Data for all transformers.  The data shall include:

  - MVA rating.

  - High and low side rated voltage.

  - Number of taps, and step size.

  - Impedance, including base values if different from rated values listed above.

- Generator data including:

  - Generator manufacturer and model.

  - Rated voltage.

  - Rated MVA.

  - Reactive capability, leading and lagging.

  - Rated MW output.

  - Net MW output.

  - Transient or subtransient reactance.

  - Transient or subtransient time constant.

  - Total inertia constant, H, of generator, including the shaft and gearbox.

  - Under frequency and under voltage protection.

  - Over frequency and over voltage protection.

- If the machine can be modeled using one of the ERCOT or Siemens PTI wind models, state which model applies to the facility.  Include instruction on how to set up and execute analysis.

- If the model is not an ERCOT or Siemens PTI model, provide either dynamic model source code for the machine and associated data or dynamic model object code for the machine and associated data.

  - If providing object code, the object code must be updated for PSS/E version changes or as requested by the DWG and/or ERCOT.

  - If the machine can be modeled using one of the ERCOT wind models, state which model applies to the facility.  Include instruction on how to set up and execute analysis.

  - Models for the wind turbine, system protection, reactive resources, etc., can be embedded into a single source code or be provided separately.

  - Models need to account for rotor mass, aerodynamic energy conversion, pitch control.

  - Models shall account for multiple wind farm interactions.

- If the model is not an ERCOT model, the following requirements apply:

  - Wind models using bus numbers shall be compatible with the ERCOT bus numbering system, and shall allow the user to determine the bus numbers.

  - Wind models shall be capable of adjusting both load flow and dynamic parameters in response to changing network conditions, and the presence of multiple windfarms.

- Number of machines by manufacturer types

- List any reactive sources such as capacitor banks, STATCOMS, etc. Provide the number of devices, location of the devices, step size, speed of switching, location where voltage is sensed and controlled, control strategy, and voltage limits.  For dynamic reactive devices, provide the appropriate PTI model and data.

- Line data from the point of connection to each wind generator.  Include:

  - Line type (overhead or underground)

  - Line length

  - Line resistance in ohms/1000 ft

  - Line reactance in ohms/1000 ft

  - Line susceptance in mhos/1000 ft

### Updates to Existing Dynamics Data

Any change in generator dynamics data or associated generator data, wind generator items listed in II B 1, or other types of equipment listed in this procedure, determined either through field testing or after changing relevant equipment or equipment settings, shall be reported by the Resource Owner to ERCOT and the TO to which they are connected within 30 days.  The updated information will be provided in the same form (such as PSS/E model data sheets) as required in section II B 1. The requirements of section II B 1 apply to all updated models and data.

## Dynamics Data for Equipment Owned by Load Entities and Transmission-Distribution Service Providers (TDSP)

### Load Acting As a Resource (LaaR, high-set relays for frequency set points above 59.3 Hz)

At least annually, ERCOT will provide to the DWG the updated LaaR models and associated model data..

### Underfrequency Firm Load Shedding Relay Data (UFLS)

ERCOT shall collect the underfrequency firm load shedding relay data on an annual basis.  Each TO is responsible for preparing the UFLS PSS/E relay model records for the loads within their system.  The models should contain the necessary information to properly represent the UFLS relay actions in a dynamic study.

### Undervoltage Load Shedding Relay Data

Note: This section addresses requirements stated in NERC Standards PRC-20 and PRC-21.

Annually, or after installation of any undervoltage load shedding (UVLS) relays, the TO installing the UVLS relays will submit the corresponding PSS/E relay model ERCOT.  The models should contain the necessary information to properly represent the undervoltage relay actions in a dynamic study, including:

- Owner and operator of the UVLS program.

- Size and location of customer load, or percent of connected load, to be interrupted.

- Corresponding voltage set points.

- Overall scheme clearing times (includes all time delays, breaker clearing times, etc).

The TO should indicate any other schemes that are part of or impact their UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems.  If requested by ERCOT, a TO shall provide its UVLS data to ERCOT within 30 calendar days.

All UVLS data will be documented in the annual Stability Book.

### Protective Relay Data

The operation of protection, control, and special protection systems can affect the dynamic performance of the ERCOT system during and following contingencies.  Planning, documenting, maintaining, or other activities associated with these systems is outside the scope of the DWG. When directed by ROS the DWG shall identify and document protection, control, and special protection systems which affect multiple transmission providers. ROS will direct the appropriate individuals or groups outside the DWG to provide any necessary assistance.  The specific information to be considered for inclusion will depend on the type, purpose, and scope of study.

Protection, control, and special protection systems included in the dynamics database should be in the form of a standard PSS/E model or models.  A descriptive model, such as a time-based sequence of events, is also acceptable.  Protection, control, and special protection systems adequately modeled for dynamic purposes by other working groups only need to be referenced in the DWG study reports.

As part of the annual database update the responsible TO shall review and update, as necessary, protection, control, and special protection systems already in the DWG database.  This review should include evaluating the existing data for applicability and accuracy.  Obsolete data should be deleted.  These updates may also be required as needed to perform ERCOT dynamic studies.

### Load Model Data

Note: This section addresses the requirements stated in NERC Standard MOD-013-1 (R1.4).

A key component of any dynamic study is the load model and its representation as a function of changing frequency or voltage.  The load model can have a significant effect on results of dynamic analysis.  For this reason, it is important to consider the load model and to use an appropriate model for study.  The DWG will document, in a table in the annual Stability Book, standard load models for each area, composed of a mix of constant impedance, constant current, and constant power generally used in studies.  A standard load-frequency dependency model (LDFRAL) will also be documented in the Stability Book.

Every dynamics study submitted to an ERCOT regional planning group shall document the load modeling assumptions in the body of the report.

### Other Types of Dynamics Data

Note: This section addresses requirements stated in NERC Standards MOD-013-1 (R1.3).

When a dynamic element  is modeled in the SSWG base cases, such as SVC, STATCOM, SMES, DC ties, and Variable-Frequency Transformer data, the responsible TO will provide the corresponding PSS/E model during the annual database update or as needed for DWG studies.

## Missing Dynamics Data

The DWG is responsible for reviewing the dynamics data on an annual basis, and reporting any missing data or unresolved issues relating to data submission requirements to the ROS.  If there are any problems with the data ERCOT will work with Resource Owners to resolve the problems. The final responsibility for the submission and the accuracy of the data lies with the Resources Owner. All of the data and the revisions requested by ERCOT from the Resource Owner shall be provided within 30 days from the date of request.  Until valid data becomes available, ERCOT, or the TO to whose system the generator is connected, shall recommend an interim solution to the modeling problem.

## Dynamics Data Storage

ERCOT shall be responsible for storing all of the dynamics data obtained from interconnected generators.  It shall maintain a repository of dynamics data with tuned parameters and will maintain the submitted revisions. All of the generator data, associated generator data, and wind generation items listed in II.B.1 received by ERCOT shall be forwarded to the DWG member of the TO to which the generator is connected within 30 days of receipt.  ERCOT staff shall inform the Texas Regional Entity (TRE) if any data is missing or has not been made available.

Overview of DWG Activities

## Updating Dynamics Data and Flat Starts

### Initiating Annual Dynamics Data Update

Each year ERCOT, in consulatation with the DWG, will initiate dynamic data collection and perform the flat start process.  For revisions to the existing dynamics data, the DWG utilizes the previous year’s dynamics data as a basis.  For each flat start, TO’s will send their updated dynamics data in electronic format to ERCOT.  The updated dynamics data will be provided in a file that contains data for all equipment connected to the reporting TO.  The changes in the data must be identified and submitted with the updated data.  The dynamics data has been tuned throughout the years to ensure proper operation of the models.  In the event the original manufacturer’s data may have been modified during this process, the parameters in the ERCOT dynamics database should not be changed to match manufacturer’s data unless it is absolutely certain that the data is correct.  Obsolete data should be deleted. Data for mothballed units shall be retained.

Other revisions of data that should be submitted to ERCOT include updates to the load model (CONL), Zsource corrections, generation netting, or any other modifications to the network necessary for dynamic studies.

### Dynamics Data Screening

TO’s should review the dynamics data for equipment connected to their system for completeness and applicability.  The data should be appropriate for the model, and the model should be appropriate for the equipment.  Before submitting data for inclusion in updated dynamics base cases, each TO should perform dynamics data screening.  Other documents such as The Guide for Condution Flat-Starts and The ERCOT Modeling Guide for Dynamic Stability provides additional information about modeling.

### Flat Start

The DWG, in consultation with ERCOT, will annually determine all flat start activities and corresponding completion schedules for the year.  The DWG performs three annual flat starts; (1) for the summer on-peak base case of the current year data set A without wind models, (2) for the summer on-peak base case of the current year data set A with wind models, and (3) for a future summer on-peak base case of the current year data set B without wind models.  The DWG may choose to flat start additional cases.  ERCOT will add all of the updates to the ERCOT dynamics database and perform a flat start.  The initialization of data should have no unacceptable errors and demonstrate that simulation output channels do not deviate from an acceptable range for a ten-second run with no disturbance.  ERCOT will contact the appropriate TO or Generating Resource to resolve any problems with the data encountered during the flat start process. The product of a successful flat start will be a simulation-ready base case (the unconverted base case) with its associated dynamic data files including user models, stability data change documentation, and IDEV files.  The product of a successful flat start also includes the steps taken to build the flat start case such as network model changes (i.e. changing the schedule of the North DC, tuning voltages, etc.).  .

## Post Flat Start Activities

### Distribution of Flat Start Results and the Dynamics Data Base

Upon completion of each flat start, an electronic copy of all dynamics data and final data files will be distributed electronically in PTI format to each DWG member and to ERCOT System Planning for archiving.  This dynamic data distribution must be within the schedule established by the DWG for the given flat start.

### Stability Book

The Stability Book is an annual document used to record dynamics data changes and/or corrections required during the flat start processes.  Recommendations to revise load flow data are also included in the book.  DWG Members shall communicate these recommendations to their respective SSWG member to eliminate recurring problems.

To verify the successful completion of the flat start process,this book shall also contain plots of the flat start results. The plots shall include, at a minimum, the six (6) worst units (based on angle deviation).

The stability book also includes: dynamics data in the DOCU ALL PTI format;

and load shedding relay data submitted by each TO.

Sections II.C.3, and II.C.5 identify additional information that will be included in the Stability Book.

## Other DWG Activities

### Dynamic Disturbance Recording (DDR) Equipment Annual Review

Note: This section addresses NERC Blackout Recommendation 12b.

The purpose for installing dynamic disturbance recording (DDR) equipment is to:

- Collect actual data following a dynamic disturbance.

- Enable the results of dynamic simulations to be evaluated for effectiveness.

Location Requirements:

ERCOT , in consultation with the DWG, shall prepare a list and perform an annual review of facilities that operate above 100 kV, are part of a dynamic stability (not transient stability) interface, and require the installation of a DDR.  The DWG shall forward any revised DDR facility list to the Reliability and Operating Subcommittee (ROS) for its review and approval.  Upon approval of the DDR facility list, facility owners shall have six months to install and place in service DDRs at each listed facility.

DDRs shall be removed or taken out of service by the same process.

Data Recording Requirements:

At a minimum, the following shall be recorded for equipment operating at 100 kV or above at facilities where DDR equipment is required:

- Bus Voltage

- Line Current

- MW and MVAR flow

- Frequency

Triggering Requirements:

DDR equipment triggering shall occur for one or more of system voltage magnitude, current magnitude, or frequency magnitude disturbances (V, I, or f) without requiring any circuit breaker operations or trip outputs from protective relay systems.

Disturbance recording equipment shall be capable of continuous recording for not less than 5 minutes and shall be retrievable for a period of not less than 72 hours.

Dynamic Disturbance Recorders (DDR’s) shall be time synchronized when practical.

The sampling rate for DDR’s shall be at least 240 samples per second.

Data Reporting Requirements:

At DDR installations where communication equipment exists and it is practical, communication from the device to an ERCOT central database shall be automatic.  Where communication equipment does not exist, or automatic communication from the device to ERCOT is not practical, facility owners who have installed DDR's shall report data for any event they consider significant to ERCOT.  ERCOT may request facility owners who have installed DDR's to report data for any event.  ERCOT’s request shall be made within 24 hours after the event and the facility owner will provide the requested data to ERCOT within 30 days.  DDR data of significant events shall be reported to ERCOT at least annually for compilation into a database.

The database compiled by ERCOT shall be made available to all ERCOT TO’s for verifying and improving system models, or analyzing system disturbances.  Submitted data will be retained by ERCOT for a minimum of one year.

DDR records shall be provided to ERCOT and NERC upon request. Disturbance records shall be retained and made available for at least one year from the date the record was made.  DDR records shall be shared between TO’s, upon request, for the analysis of system disturbances.

Maintenance and Testing Requirements:

DDR equipment must be maintained and tested in accordance with the manufacturer’s recommendations.  Maintenance and test records shall be provided to ERCOT upon request within 30 business days.

### Event Simulation

Note: This section addresses NERC blackout recommendation 14.

When directed by ROS the DWG will simulate an actual disturbance event for the purpose of assessing the fidelity of the ERCOT dynamics models and data with actual system performance during the event. The DWG will annually consider recent significant events to determine their suitability for an event simulation. and communicate its conclusions in the monthly DWG report to ROS.

run PSS/e Dynamics:
run MakeCnv.idv

Update
base case

*.sav

Update
dynamic file

*.dyr

Update
user model

UserM.for

run MakeSnap.idv
close  PSS/E

Switch to FORTRAN:

>COMPILE UserM

>CLOAD4 UserM

run PSS/E Dynamics:

run RunFlat.idv

run PSS/E Plotter:

run PlotFlat.idv

NO

YESNO

Table 2 - Directory and files to process Wind Machines model objects

ErcotWind.lib (aggregation of all machine’s *.lib file

Siemens PTI has authorized use of PTI information to be included in this Procedural Manual.