| OGRR Number | 243 | OGRR Title | Disturbance Monitoring Requirements Clarification |
| --- | --- | --- | --- |

| Date | June 24, 2010 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | JC Culberson / Matt Morais |
| E-mail Address | jculberson@ercot.com / mmorais@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-4505 / (512) 225-7177 |
| Cell Number |  |
| Market Segment | N/A |

Comments

ERCOT submits these comments to revise language in 7.1.2.4, Data Retention and Reporting Requirements.  Revisions are needed to remove a potential conflict with NERC Reliability Standards which requires a three year retention period of all, applicable recorded fault data.

Additionally, ERCOT recommends striking the language listed in the last paragraph of Section 7.1.2.4, as it places a data retention requirement on ERCOT that is an existing requirement for Transmission Owners (TOs) and Generator Owners (GOs) (as defined by the North American Electric Reliability Corporation (NERC), in the ERCOT Region for a minimum of three years.  Requiring ERCOT to retain these records results in a duplication of efforts already required of the TOs and GOs in the ERCOT System; as the applicable Facility owners (TOs and GOs) must archive all Disturbance Monitoring Equipment (DME) information in accordance with R5 of PRC-018, Disturbance Monitoring Equipment Installation and Data Reporting.

Revised Proposed Guide Language

- 7.1.2.3	Data Recording Requirements

For Facilities operating at 100kV or above where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

- Two (2) sets of voltages for breaker-and-a-half and ring bus substation configurations.  One (1) set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform.

- For all lines, neutral (residual) current waveform.

- Circuit breaker status.

- Circuit breaker trip circuit status.

- Date and time stamp.

For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

- For all autotransformers, high or low voltage terminal current waveform for three (3) phases and either neutral/residual current waveform or current waveform in delta windings.

- For all lines, two (2) phase current waveforms.

- Status – carrier transmitter control (i.e. start, stop, keying).

- Status – carrier received.

- 7.1.2.4	Data Retention and Reporting Requirements

The Facility owner shall store all recorded fault data for at least a three (3)-year period.  This data shall be stored in the form of a computer file or files.

Facility owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five (5) Business Days, along with channel identification and scaling information to allow analysis of the recordings. Fault recordings shall be shared between Facility owners, upon their request, for the analysis of ERCOT System disturbances.

Data submissions shall be COMTRADE fault recordings (.cfg and .dat files) and one (1) or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel © spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel © spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

- Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |  |
| --- | --- | --- |
| From Bus (ERCOT short circuit database bus number) |  |  |
|  | To Bus (ERCOT short circuit database bus number) |  |
| Nominal Voltage of Faulted Branch or Bus (kV) |  |  |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location) |  |  |
| Time Zone (Central Prevailing Time (CPT), UTC, etc.) |  | Date (MM/DD/YYYY) |
|  |  | Time (HH:MM:SS, twenty-four (24) hour format) |
|  |  | Cause Code |
| Fault Recorder Data |  | Circuit (1, 2, A, B, N, S, etc.) |
| From Bus – Recorder Location (ERCOT short circuit database bus number) |  |  |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |  |
|  | Nominal Voltage of Monitored Branch (kV) |  |
|  | Measured Current Magnitude (primary value in RMS amperes) |  |
|  | Recorded Fault Duration (cycles) |  |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |  |
| Optional Comments (40 char. max.) |  |  |

When multiple recordings exist for a single event, data from the best recording (usually the closest recorder) is required.