## Slide 1: 8-Hour LFC Test Update Preliminary results as of June 23rd NATF Meeting June 23, 2010
<number> Texas Nodal
Notes: <number>

## Slide 2
<number> Texas Nodal
Outline of Discussion
LFC Test Overview
Successes of LFC test
Issues during LFC test
  ERCOT Issues
  Market Issues
Other observations and analysis
Next steps for 48-hour LFC Test in July
Agenda

## Slide 3: LFC Test Overview
http://nodal.ercot.com <number>
  June 17, 2010
Test Activities | Approx Timeline
Market WebEx start | 7:00 AM
ERCOT - MP pre-test troubleshooting period | 7:00 AM – 10:00 AM
Test start | 10:00 AM
Zonal-Nodal cutover | 10:00 AM – 10:46 AM
System frequency controlled by nodal systems | 10:46 AM – 5:10 PM
RRS Scenario | 2:15 PM – 2:25 PM
EMBP Scenario | 3:00 PM – 3:20 PM
Nodal-Zonal cutover | 5:10 PM – 5:42 PM
Test end | 5:42 PM
Market WebEx end | 5:50 PM

## Slide 4: LFC Test Overview for June 17th
http://nodal.ercot.com <number>
Constraint List

## Slide 5
<number> Texas Nodal
ERCOT operational perspective
The switching of control between systems went smoothly
Frequency was controlled for duration of test by nodal systems
Planned operational scenarios were executed as planned
CPS1 scores were passing except for one hour
ERCOT Operators able to manage numerous active constraints with SCED
Successes during test

## Slide 6
<number> Texas Nodal
Issues during test for ERCOT
Issue #1 – Missing Shift Factors for constraints in SCED for brief period
  Shift Factors integration from EMS to MMS from1320-1339 had issues
    Shift factors were ignored by SCED for 29 minutes
    Dispatch closely monitored by Operators until resolved
    Issue corrected and evaluating improved monitoring to prevent re-occurrence
Issue #2 – Missing Shift Factors for Electrical Bus affect SPP calculation
  EMS integration did not properly provide electrical bus shift factors
    Load Zone, Hub, and Electrical Bus LMPs/SPPs incorrect
    Resolution identified and in place later this week
Analysis is on going and will be communicated once more information is available
Issues during test

## Slide 7
<number> Texas Nodal
Issues during test for Market Participants
Telemetry
  Consistency between JOU owners (e.g., telemetry, COP)
  Incorrect Ancillary Service values in telemetry for Resource
  Resource Status Codes incorrect
Zonal Resource plan in agreement with Nodal
Resource with nodal Output Schedule offering BES into zonal market
Resources not following their nodal basepoints
Resources not following regulation signals
Incorrect HSL/LSL values telemetered
Issues during test

## Slide 8
<number> Texas Nodal
West-to-North Stability Limit
Two months ago ERCOT created nodal W-N stability limit in nodal
For LFC tests, ERCOT reduces limit to be less than zonal so that OC1 in zonal would not be activated
Prior to the LFC test at 0915, the W-N constraint was activated in zonal
Beginning the LFC test at 1000, nodal constraints for W-N limit were in place
During transition to nodal and until 1300, Nodal and Zonal W-N limit exceeded
Constraint relieved at 1300 for remainder of test
Continuing further analysis to review dispatch, basepoints, etc
ERCOT will work closely with market for W-N management for 48-hour test
Next steps
ERCOT will continue to provide updates on the market calls and next NATF regarding results and lessons learned from 8-hour LFC test
Other Observations and Analysis

## Slide 9
<number> Texas Nodal
Continue analysis of 8-hour test and consider improvements to 48-hr test
-Can discuss at next NATF
Week of June 28
  48-Hour LFC Test Workshop
Week of July 20
  Conduct 48-Hour LFC Test (July 20, 21, 22)
Next Steps for the 48-hour LFC Test