| NOGRR Number | 038 | NOGRR Title | Synchronization with OGRR243, Disturbance Monitoring Requirements Clarification |
| --- | --- | --- | --- |

| Date | July 6, 2010 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | JC Culberson / Matt Morais |
| E-mail Address | jculberson@ercot.com / mmorais@ercot.com |
| Company | ERCOT |
| Phone Number | (512) 248-4505 / (512) 225-7177 |
| Cell Number |  |
| Market Segment | N/A |

Comments

ERCOT submits these comments to revise language in 6.1.2.4, Data Retention and Reporting Requirements.  Revisions are needed to remove a potential conflict with NERC Reliability Standards which requires a three year retention period of all, applicable recorded fault data.

Additionally, ERCOT recommends striking the paragraph 5 of Section 6.1.2.4, as it is currently not a requirement for ERCOT and the data should already be retained by Transmission Owners (TO) and Generator Owners (GO), as defined by NERC, in the ERCOT Region for a minimum of three years.  Requiring ERCOT to retain these records results in a duplication of efforts already required of the TO and GO in the ERCOT System; as the applicable Facility owners (TOs and GOs) must archive all Disturbance Monitoring Equipment (DME) information in accordance with R5 of PRC-018,Disturbance Monitoring Equipment Installation and Data Reporting.

Revised Proposed Guide Language

- 6.1.2.3	Data Recording Requirements

(1)	For facilities operating at 100kV or above where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

(a)	Two sets of voltages for breaker-and-a-half and ring bus substation configurations.  One set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform;

(b)	For all lines, neutral (residual) current waveform;

(c)	Circuit breaker status;

(d)	Circuit breaker trip circuit status; and

(e)	Date and time stamp Central Prevailing Time (CPT).

(2)	For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

(a)	For all autotransformers, high or low voltage terminal current waveform for three phases and either neutral / residual current waveform or current waveform in delta windings;

(b)	For all lines, two phase current waveforms;

(c)	Status – carrier transmitter control (i.e. start, stop, keying); and

(d)	Status – carrier received.

- 6.1.2.4	Data Retention and Reporting Requirements

(1)	The facility/equipment owner shall store all recorded fault data for at least a three year period.  This data shall be stored in the form of a computer file or files.

(2)	Facility/equipment owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five days, along with channel identification and scaling information to allow analysis of the recordings.  Fault recordings shall be shared between facility/equipment owners, upon their request, for the analysis of ERCOT System disturbances.

(3)	When multiple recordings exist for a single event, only report to ERCOT and NERC of data from the best recording, usually the closest recorder is required.

(4)	Data submissions shall be COMTRADE fault recordings, .cfg and .dat files, and one or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel© spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel© spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |
| --- | --- |
|  | From Bus (ERCOT short circuit database bus number) |
|  | To Bus (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Faulted Branch or Bus (kV) |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location. If physical location not found, leave blank) |  |
|  | Date (MM/DD/YYYY) |
|  | Time (HH:MM:SS, 24 hour format) |
|  | Cause Code |
| Fault Recorder Data | Circuit (1, 2, A, B, N, S, etc.) |
|  | From Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Monitored Branch (kV) |
|  | Measured Current Magnitude (primary value in RMS amperes) |
|  | Recorded Fault Duration (cycles) |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |
| Optional Comments (40 char. max.) |  |