| NOGRR Number | 038 |  |  | NOGRR Title | Synchronization with OGRR243, Disturbance Monitoring Requirements Clarification |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Timeline | Normal |  |  | Recommended Action |  | Approval |  |
| Date of Decision |  |  |  | May 19, 2010 |  |  |  |
| Proposed Effective Date |  |  |  | To be determined. |  |  |  |
| Priority and Rank Assigned |  |  |  | To be determined. |  |  |  |
| Guide Section(s) Requiring Revision |  |  |  | 6.1.2.3, Data Recording Requirements 6.1.2.4, Data Retention and Reporting Requirements |  |  |  |
| Revision Description |  |  |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guides with OGRR243 by changing data recording and reporting requirements for equipment operating at 100kV or above at Facilities where fault recording equipment is required. |  |  |  |
| Reason for Revision |  |  |  | The System Protection Working Group (SPWG) prefers that the fault data recording requirements allow for calculated electrical quantities which are used in modern protection system equipment and can be determined by modern fault analysis software. The SPWG also prefers that recording requirements for autotransformers should allow for monitoring of either high voltage or low voltage terminals and that specification in the fault reporting template of the recorded time standard (such as Central Prevailing Time (CPT) or Coordinated Universal Time (UTC)), replace the requirement of Central Standard Time (CST) recording requirements. |  |  |  |
| Overall Market Benefit |  |  |  | Synchronization of Nodal Operating Guides; the suggested recording and reporting modifications will clarify fault recording requirements and improve the ability of ERCOT, Transmission Service Providers (TSPs), and Resource Entities to determine and implement compliant fault recording equipment. |  |  |  |
| Overall Market Impact |  |  |  | None. |  |  |  |
| Consumer Impact |  |  |  | None. |  |  |  |
| Procedural History |  |  |  | - On 3/26/10, NOGRR038 and the associated CEO Revision Request Review were posted. - On 5/19/10, the Operations Working Group (OWG) considered NOGRR038. |  |  |  |
| OWG Decision |  |  |  | On 5/19/10, OWG was in consensus to recommend approval of NOGRR038 as revised by OWG. |  |  |  |
| Summary of OWG Discussion |  |  |  | On 5/19/10, the need to maintain consistency between the Protocols and Operating Guides by using CPT rather than CST in the Operating Guides was discussed. |  |  |  |
| Quantitative Impacts and Benefits |  |  |  |  |  |  |  |
| Assumptions |  | 1 | The new format will help to improve the reliability of transmission protection systems. |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Market Cost |  |  | Impact Area |  |  |  | Monetary Impact |
|  |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Market Benefit |  |  | Impact Area |  |  |  | Monetary Impact |
|  |  | 1 | Improvement of TSPs and Resource Entities ability to successfully comply with listed recording requirements |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Additional Qualitative Information |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Other Comments |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Glenn Hargrave on behalf of SPWG |
| E-mail Address | grhargrave@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | (210) 353-4215 |
| Cell Number | (210) 394-1313 |
| Market Segment | Municipality |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| None. |  |
| Proposed Guide Language Revision |  |

- 6.1.2.3	Data Recording Requirements

(1)	For equipment operating at 100kV or above at facilities where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

(a)	Two sets of voltages for breaker-and-a-half and ring bus substation configurations.  One set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform;

(b)	For all lines, neutral (residual) current waveform;

(c)	Circuit breaker status;

(d)	Circuit breaker trip circuit status; and

(e)	Date and time stamp Central Prevailing Time (CPT).

(2)	For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

(a)	For all autotransformers, high or low voltage terminal current waveform for three phases and either neutral / residual current waveform or current waveform in delta windings;

(b)	For all lines, two phase current waveforms;

(c)	Status – carrier transmitter control (i.e. start, stop, keying); and

(d)	Status – carrier received.

- 6.1.2.4	Data Retention and Reporting Requirements

(1)	The facility owner shall store all recorded fault data for at least a two year period.  This data shall be stored in the form of a computer file or files.

(2)	Facility owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five days, along with channel identification and scaling information to allow analysis of the recordings.  Fault recordings shall be shared between facility owners, upon their request, for the analysis of ERCOT System disturbances.

(3)	When multiple recordings exist for a single event, only report to ERCOT and NERC of data from the best recording, usually the closest recorder is required.

(4)	Data submissions shall be COMTRADE fault recordings, .cfg and .dat files, and one or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel© spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel© spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |
| --- | --- |
|  | From Bus (ERCOT short circuit database bus number) |
|  | To Bus (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Faulted Branch or Bus (kV) |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location. If physical location not found, leave blank) |  |
|  | Date (MM/DD/YYYY) |
|  | Time (HH:MM:SS, 24 hour format) |
|  | Cause Code |
| Fault Recorder Data | Circuit (1, 2, A, B, N, S, etc.) |
|  | From Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Monitored Branch (kV) |
|  | Measured Current Magnitude (primary value in RMS amperes) |
|  | Recorded Fault Duration (cycles) |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |
| Optional Comments (40 char. max.) |  |

(5)	ERCOT shall compile a summary list of all available 345 kV fault recordings annually based on each facility owner’s submitted data.  This summary shall contain for each recording the date, time, fault recorder owner, fault recorder location, the primary system element recorded, and an optional use comment field.  This summary shall be available to any ERCOT Member upon their request.  Record summaries will be retained by ERCOT for a minimum of three years.