| NPRR Number | 239 | NPRR Title | Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Recommended Approval |
| Date of Decision |  | July 1, 2010 |  |  |
| Proposed Effective Date |  | Upon the Nodal Protocol Transition Plan’s Texas Nodal Market Implementation Date as prescribed by zonal Protocol Section 21.12, Process for Transition to Nodal Market Protocol Sections. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Nodal Protocol Section Requiring Revision |  | 6.5.7.10, WGR Ramp Rate Limitations (new) |  |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) proposes a requirement that certain Wind-powered Generation Resources (WGRs) limit the unit ramp rate to 10% per minute of their nameplate rating as registered with ERCOT. The proposed language is based on the concept set forth in zonal Protocol Section 6.5.13, WGR Ramp Rate Limitations. |  |  |
| Reason for Revision |  | The intent of this NPRR is to maintain system reliability as it allows ERCOT to avoid frequency spikes due to WGRs’ ability to ramp up or ramp down almost instantaneously. |  |  |
| Overall Market Benefit |  | Enhance system reliability by limiting frequency deviations associated with near-instantaneous ramping of WGRs. Decreased need for Ancillary Service procurement and deployment to compensate for variability in WGR production. |  |  |
| Overall Market Impact |  | Unknown. |  |  |
| Consumer Impact |  | Likely positive consumer impact associated with decreased need for Ancillary Service procurement and deployment to compensate for variability in WGR production. |  |  |
| Credit Impacts |  | ERCOT Credit Staff and the Credit Work Group (Credit WG) have reviewed NPRR239 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - On 5/13/10, NPRR239, a CEO Revision Request Review, and an Impact Analysis were posted. - On 5/20/10, PRS considered NPRR239. - On 6/10/10, Wind Coalition comments were posted. - On 6/17/10, PRS considered the 5/20/10 PRS Report and Impact Analysis for NPRR239. - On 7/1/10 TAC considered NPRR239. |  |  |
| PRS Decision |  | On 5/20/10, PRS voted to recommend approval of NPRR239 as submitted. There were two abstentions from the Consumer and Independent Generator Market Segments. All Market Segments were present for the vote. On 6/17/10, the motion to endorse and forward the 5/20/10 PRS Report as amended by the 6/10/10 Wind Coalition comments and Impact Analysis for NPRR239 to TAC failed via roll call vote. PRS then voted to endorse and forward the 5/20/10 PRS Report and Impact Analysis for NPRR239 to TAC. There were three abstentions from the Consumer (2) and Municipal Market Segments. All Market Segments were present for the votes. |  |  |
| Summary of PRS Discussion |  | On 5/20/10, ERCOT Staff explained that NPRR239 is largely based on the language of PRR771, Ramp Rate Limitation of 10% per minute of On-Line Installed Capability for Wind-powered Generation Resources. The alternative of a 20% limit was discussed. Concerns were expressed that at a 20% limit, WGRs would go below the base point and result in pricing issues. On 6/17/10, the alternative of a 20% ramp rate limit as proposed in the 6/10/10 Wind Coalition comments was again discussed. ERCOT Staff stated that it would be amenable to a 20% ramp rate limit if ERCOT’s control capability was enhanced, for example, through stricter Base-Point Deviation Charge and Generation Resource Energy Deployment Performance (GREDP) rules, but that implementing such changes would have system impacts. |  |  |
| TAC Decision |  | On 7/1/10, TAC voted to recommend approval of NPRR239 as recommended by PRS in the 6/17/10 PRS Report. There was one abstention from the Municipal Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 7/1/10, a Market Participant recognized current resource and system constraints, but noted the desire to consider the alternative of a 20% ramp rate limit post TNMID once experience is gained operating in the nodal market. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Unknown. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Enhance system reliability by limiting frequency deviations associated with near-instantaneous ramping of WGRs. | Not quantified at this time. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Likely positive consumer impact associated with decreased need for Ancillary Service procurement and deployment to compensate for variability in WGR production. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | John Dumas |
| E-mail Address | jdumas@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-3195 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Jonathan Levine |
| E-Mail Address | jlevine@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Wind Coalition 061010 | Proposed a 20% ramp rate limitation. |

Proposed Protocol Language Revision

6.5.7.10	WGR Ramp Rate Limitations

(1)	Each WGR that is part of an Interconnection Agreement signed on or after January 1, 2009 shall limit its ramp rate to ten percent per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

(2)	The requirement of paragraph (1) above does not apply during a Force Majeure Event or during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available wind resource.

(3)	Each WGR that is part of an Interconnection Agreement signed on or before December 31, 2008 and that controls power output by means other than turbine stoppage shall limit its ramp rate to ten percent per minute of its nameplate rating (MWs) as registered with ERCOT when responding to or released from an ERCOT deployment.

(4)	The requirement of paragraph (3) above does not apply during a Force Majeure Event, during intervals in which a decremental deployment instruction coincides with a demonstrated decrease in the available wind resource, or during unit start up and shut down mode.

(5)	The ramp rate requirement of paragraph (3) above shall not apply to a WGR during a limited compliance transition period if the WGR:

(a)	Meets the technical specifications of paragraph (3) above but does not comply with the ramp rate requirement; and

(b)	Submitted a compliance plan to ERCOT on or before June 1, 2009 that details the technical limitations leading to non-compliance, a work plan to achieve compliance by a reasonable date, and a ramp rate mitigation plan describing the WGR’s best efforts to adhere to the WGR ramp rate limitation during the applicable compliance transition period.

(6)	The ramp rate requirement of paragraph (3) above shall not apply to a WGR that:

(a)	Does not meet the technical specifications of paragraph (3) above; and

(b)	Submitted an operations plan to ERCOT on or before June 1, 2009 describing the WGR’s best efforts to adhere to the WGR ramp rate limitation.

(7)	WGRs subject to the ramp rate limitations of paragraphs (1) and (3) above are exempt from the requirements of the applicable paragraph upon receipt of a valid Dispatch Instruction from ERCOT to exceed the applicable ramp rate limitation when necessary to protect system reliability.

(8)	WGRs that operate under a Special Protection System (SPS) are exempt from the ramp rate limitations of paragraphs (1) and (3) above when decreasing unit output to avoid SPS activation.

(9)	WGRs that meet the requirements of paragraphs (1) and (3) above are compliant with ramp rate limitation requirements when the number of five-minute averages of eligible intervals meeting ten percent of nameplate capacity per minute ramp rate limit is equal to or greater than 90% of eligible intervals per month.  Intervals where paragraphs (2), (4), (7) or (8) above apply shall be excluded as eligible intervals for this performance metric.  ERCOT shall initiate a review process with the WGR where the WGR’s score is less than 90%.  Scores that remain below 90% for three consecutive months shall be considered to have failed the ramp rate limitation performance measure.