ERCOT Operations Report

Jun 2010 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 06/03/2010 18:55:58 | 59.888 | 7 | Unit trip with 477 MW |
| 06/05/2010 12:57:10 | 60.132 | 444 | Large SCE change +600 MW in 5 minutes. Out of Down Regulation |
| 06/08/2010 09:00:18 | 60.102 | 21 | Large SCE change +553 MW in 9 minutes. Out of Down Regulation. Wind generation increased 1490 MW in 45 min. |
| 06/14/2010 17:58:30 | 59.884 | 8 | Out of Up Regulation. Wind dropped by 300 MW in 1 min due to storms |
| 06/15/2010 16:54:50 | 59.882 | 6 | Unit trip with 560 MW |
| 06/18/2010 19:19:36 | 59.890 | 6 | Unit trip with 585 MW |
| 06/21/2010 07:23:34 | 59.890 | 145 | Incorrect offset calculation and Out of Up Regulation |
| 06/23/2010 15:19:56 | 59.716 | 212 | Unit trip with 733 MW, 157 MW, 157 MW, 168 MW and 38 MW. |
| 06/23/2010 15:50:13 | 60.124 | 615 | Due to deployment of LaaRs. (Related to DCS event) |
| 06/23/2010 18:02:24 | 60.115 | 152 | SCE change +360 MW and Non-conforming load trip of 110 MW |
| 06/29/2010 11:49:21 | 59.881 | 4 | Unit trip with 760 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 6/2/10 0:27:22 | 6/2/10 0:56:44 | 0:29:22 | 352.2 | Large SCE change -1300 MW in 20min. |
| 6/3/10 18:56:01 | 6/3/10 19:05:26 | 0:09:25 | 437.6 |  |
| 6/9/10 7:53:32 | 6/9/10 8:04:52 | 0:11:20 | 368.2 | Unit Trip |
| 6/9/10 9:19:14 | 6/9/10 9:36:28 | 0:17:14 | 325.5 | Large SCE change -600 MW in 9min. |
| 6/10/10 0:04:24 | 6/10/10 0:17:18 | 0:12:54 | 341.5 | Large SCE change -700 MW in 10min and out of up reg |
| 6/14/10 17:58:28 | 6/14/10 18:20:48 | 0:22:20 | 453.7 |  |
| 6/15/10 16:54:51 | 6/15/10 17:05:28 | 0:10:37 | 428.7 |  |
| 6/18/10 19:19:34 | 6/18/10 19:26:14 | 0:06:40 | 426.9 |  |
| 6/19/10 7:28:11 | 6/19/10 7:47:51 | 0:19:40 | 346.9 | Incorrect offset calculation |
| 6/21/10 7:16:58 | 6/21/10 7:49:51 | 0:32:53 | 426.9 |  |
| 6/23/10 15:19:59 | 6/23/10 15:49:21 | 0:29:22 | 1150.0 |  |
| 6/27/10 18:06:55 | 6/27/10 18:19:41 | 0:12:46 | 325.5 | Incorrect offset calculation |
| 6/29/10 11:49:23 | 6/29/10 12:03:23 | 0:14:00 | 474.9 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| DFW | 47 | 17 | 5 | 22 | 0 | 69 |
| Western | 0 | 2 | 2 | 4 | 16 | 20 |
| North | 0 | 1 | 1 | 2 | 8 | 10 |
| Houston | 5 | 1 | 2 | 3 | 0 | 8 |
| E RIO | 1 | 3 | 0 | 3 | 0 | 4 |
| Northeast | 0 | 0 | 4 | 4 | 0 | 4 |
| San Antonio | 0 | 2 | 0 | 2 | 0 | 2 |
| Austin | 0 | 0 | 1 | 1 | 0 | 1 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| South | 0 | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 | 0 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 | 0 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 53 | 26 | 15 | 41 | 24 | 118 |

| Historical Totals | Jun-10 | Jun-09 | May-10 |
| --- | --- | --- | --- |
| Austin | 0 | 5 | 0 |
| Bryan Area | 0 | 5 | 0 |
| Corpus | 0 | 15 | 0 |
| DFW | 64 | 51 | 87 |
| E RIO | 4 | 31 | 0 |
| Houston | 6 | 2 | 78 |
| Laredo | 0 | 14 | 0 |
| North | 9 | 37 | 18 |
| Northeast | 0 | 0 | 0 |
| San Antonio | 2 | 12 | 0 |
| South | 0 | 11 | 0 |
| W RIO | 0 | 1 | 0 |
| Western | 18 | 14 | 4 |
| Total | 103 | 198 | 187 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Meadow - PH Robinson 345KV | North Alvin - Hastings 138KV | 16 |
| Matador - Paducah 69KV | Aspermont - Spur 138KV | 13 |
| Graham - Parker 345KV | Barton Switch - Oran 138KV | 13 |
| Watermill Switch - West Levee Switch & Sargent Road 345KV | Duncanville South - Cedar Hill TU 138KV | 12 |
| Graham SES - Parker Switch 345KV | Leon Switch - Flat Creek 138KV | 10 |
| Base Case | Matador - Paducah 69KV | 9 |
| Jack County - Reno 138KV | Rhome TU - Decatur Tap 138KV | 9 |
| Hamilton - Sonora 138KV | Sonora - Friess Ranch 69KV | 8 |
| Comanche Peak SES - Johnson Switch 345KV | Wolf Hollow - Rocky Creek 345KV | 7 |
| Oklaunion - Fisher Road - Bowman 345KV | Bomarton TU - Baylor County Tap 69KV | 5 |
| Barney Davis - Airline and Rodd Field 138KV | Airline CSW - Cabaniss 138KV | 4 |
| Lobo - San Miguel 345KV | Freer - San Diego 69KV | 4 |
| Moss Switch - Holt Switch 138KV | Odessa North - Odessa Basin 69KV | 4 |
| Roanoke Switch - West Denton & Lewisville Switch 345KV | West Denton - Jim Cristal 138KV | 4 |
| Sandow SW - Temple SW 345kV | Hearne 138/69KV AT1 | 4 |
| Roanoke - West Denton & Roanoke - Lewisville 345KV | West Denton - Ft Worth 138KV | 3 |
| Whitepoint - DuPont Switch Ingleside #1 138KV | Rincon - Whitepoint 138KV | 3 |
| Ingleside Cogen Switch - DuPont Switch Ingleside138KV | DuPont Switch Ingleside - DuPont PP1 Ingleside 138KV | 3 |
| Moss Switch - Holt Switch 138KV | Odessa North 138/69KV AT1 | 3 |
| Sherry Switch - Handley & Executive Parkway 138KV | Sherry Switch - Park Row 138KV | 3 |
| Hutto - Gilleland 138KV | Round Rock - Round Rock Northeast 138KV | 2 |
| Willow Valley - Bluff Creek 138KV | Ackerly Vealmoor - Ackerly 69KV | 2 |
| Austrop - Sandow Switch 345KV | Round Rock - Round Rock Northeast 138KV | 2 |
| Base Case | Stanton East Switching Station 138KV - Midland East 138KV | 2 |
| Graham SES - Parker Switch 345KV | Jacksboro switch - Graham SES 345KV | 2 |
| Graham SES - Parker SW 345KV | Graham SES- Jacksboro Switching 345KV | 2 |
| Morgan Creek 2H 345/138KV AT | Morgan Creek 4H 345/138KV AT | 2 |
| Oklaunion Unit | Leon Switch - Flat Creek 138 kV | 2 |
| Olney - Westover 69 KV | Elbert Switch to Seymour. | 2 |
| Wink TNP AT1 138/69KV AT | Wickett TNP - Permian Basin 69KV | 2 |
| Cagnon 345/138KV autotransformer 3 | Cagnon 345/138KV autotransformer 4 | 2 |
| Ferguson - Wirtz - Coronado 138KV | Ferguson - Wirtz 138KV | 2 |
| Fredericksburg - Gillespie LCRA 138KV | Fredericksburg AT2 138/69KV | 1 |
| Sherry - Everman 345KV | Tatte East Tap- Oak Hill 2 Tap 138KV | 1 |
| Base Case | ENA Snyder - WKN Breaker 69KV | 1 |
| Base Case | WKN_BKR - MEC Plainview 69KV | 1 |
| Bellaire 345/138KV AT2 | Bellaire 345/138KV AT4 | 1 |
| Collin - Anna Switch 345KV | Payne Switch - EPCO POI 138KV | 1 |
| Dilley Switch - San Miguel Switch 138KV | Derby Sub - Pearsall Switch 69KV | 1 |
| Fort Bend - East Bernard 138KV | Flewellen - Peters REIT 138KV | 1 |
| La Palma - Rio Hondo 345KV | Raymondville 2 - Raymondville 1 69KV | 1 |
| Renner Switch 345/138KV AT2 | Allen Switch 345/138KV AT1 | 1 |
| Twin Butte - San Angelo Red Creek 345KV | San Angelo Red Creek 345/138KV AT2 | 1 |
| West Levee 345/138KV AT1 | West Levee 345/138KV AT2 | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West – North | 19 |
| North – Houston | 11 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

Olney – Westover 69 kV PCAP

New Procedures/Forms/Operations Bulletins

None

## Blackout/Load Shed Incidences

None

EEA

6/23 15:35	ERCOT declared EEA 1 for Adjusted Responsive Reserve below 2300MW.

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

06/21 17:00 60,698 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2007 | 2008 | 2009 | 2010 |
| January | 4.55 | 3.30 | 4.11 | 3.78 |
| February | 3.75 | 3.59 | 3.49 | 3.79 |
| March | 2.70 | 3.29 | 3.24 | 2.24 |
| April | 3.00 | 2.45 | 2.66 | 2.47 |
| May | 3.22 | 3.01 | 2.90 | 2.63 |
| June | 4.46 | 2.81 | 2.89 | 2.84 |
| July | 4.29 | 2.55 | 2.83 | NA |
| August | 3.11 | 3.66 | 3.07 | NA |
| September | 3.78 | 4.99 | 3.68 | NA |
| October | 3.08 | 2.79 | 2.92 | NA |
| November | 2.95 | 2.60 | 1.93 | NA |
| December | 3.74 | 4.54 | 3.70 | NA |
| Annual Average | 3.55 | 3.29 | 3.11 | 2.96 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 6/23/10 | 15:28 | 18:45 | Watch issued for ARRS below 2500 MW. |
| 6/23/10 | 18:45 | 19:15 | Advisory issued for ARRS below 3000 MW. |
| 6/28/10 | 11:30 | 0:00 | Operating Condition Notice (OCN) issued for Tropical Storm Alex in the Gulf of Mexico. |
| 6/29/10 | 0:15 | 11:00 | Operating Condition Notice (OCN) issued for Tropical Storm Alex in the Gulf of Mexico. |
| 6/29/10 | 11:00 | 0:00 | Advisory issued for Tropical Storm Alex in the Gulf of Mexico. |
| 6/30/10 | 0:15 | 0:00 | Advisory issued for Hurricane Alex in the Gulf of Mexico. |

Transmission Watch

6/01 00:15	Transmission Watch issued due to forced outage at Gails substation.  Implemented Block Load Transfer up to 2 MW from ERCOT (Gails substation) to SPP (Draw substation).

6/15 00:15	Transmission Watch issued due to forced outage on Flomot - Muleta 69KV.  BLT implemented for up to 2 MW of ERCOT load to SPP at Estelline.

Emergency Notice

None

Texas RE Event Analysis

6/12 09:39	Stanton Switch Station SPS #46 activated. ERCOT does not see any evidence that the Stanton East Switching Station SPS #46 SPS failed to operate as designed.

6/19 23:04	Stanton Switch Station SPS #46 activated. ERCOT does not see any evidence that the Stanton East Switching Station SPS #46 SPS failed to operate as designed.

6/23 15:19	Emergency Notice for a NERC Reportable Disturbance Control Standard (DCS) Event for loss of 1253 MW of generation. ERCOT declared Level 1 of its Energy Emergency Alert (EEA) due to Adjusted Responsive Reserve dropping below 2300 MW after Loads acting as Resources (LaaRs) were deployed.

6/26 22:18	Stanton Switch Station SPS #46 activated. Investigation is still ongoing.

6/30 12:55	Loss of Military highway bus (jointly owned by AEP and PUB) and four 138kV lines during the storms from hurricane Alex. Investigation is still ongoing.

Others

6/21  06:50	Held the real-time balancing deployments for IE 0700 due to an incorrect offset calculation for IE 0715, resumed with IE 0730.

6/26  00:15	Held real-time balancing energy deployments IE 24:00 on 06-25-10 for IE 00:15 on 06-26-10 due an incorrect offset calculation. Resumed with IE 00:30 deployments.