## Slide 1: PDCWG Report to ROS
July 15, 2010
Sydney Niemeyer

## Slide 2: PDCWG Meeting July 7, 2010
BAL-001-TRE Update:
  Workshop scheduled for August 6, 2010
    Detailed instruction and demonstration of Primary Frequency Response measure and evaluation.
    Met Center from 9:00 am to 3:00 pm
    Update of latest draft of regional standard.
  LCRA is independently evaluating standard and writing instructions for evaluation tools.
  Additional 1670 MW of capacity is now testing proposed Governor settings: droop curve with no step function and lower dead-band.

## Slide 3: Status as of July 7, 2010
Units with Governors presently set with an intentional deadband less than or equal to +/-0.01666 Hz and droop curve with no step function.
  13,987 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    5534 MW Coal
    3780 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    1224 MW Steam Turbine – natural gas fired
    240 MW Hydro

## Slide 4: PDCWG Meeting July 7, 2010 continued
Nodal 8 hour LFC test review:
  Concern with Regulation deployments as being excessive for frequency error.
    Contributed to unit oscillation and large frequency oscillations.
    CPS1 hour data was significantly lower than recent CPS1 hour data.
    Encourage further tuning of LFC regulation deployment in future testing.

## Slide 5: PDCWG Meeting July 7, 2010 continued
Texas Renewables Integration Plan SP-05 Impact of Wind Turbines on System Inertia.
  Submitted comments to the RTWG.
Frequency Event review.
  June 23, 2010 15:20 DCS event was reviewed. Primary Frequency Response evaluation will be available in August.
Completed NPRR for Synchronization with PRR 824 and PRR 833.

## Slide 6
CPS1 = 147.23

## Slide 7
CPS1 = 157.73

## Slide 12
of ERCOT Frequency

## Slide 14
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 145.43