| NPRR Number | 232 | NPRR Title | Clarification of Block Load Transfer Registration and Deployment |
| --- | --- | --- | --- |
| Date |  | June 15, 2010 |  |
| Submitter’s Information |  |  |  |
| Name |  | Bill Blevins |  |
| E-mail Address |  | bblevins@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6691 |  |
| Cell Number |  |  |  |
| Market Segment |  | Not applicable |  |

Comments

ERCOT acknowledges the issue that CenterPoint Energy raises in its comments.  However, ERCOT believes that the authority behind a “governmental order” should conform with those entities identified in the Protocol definition of “Governmental Authority.”  In addition, any order or directive issued by a Governmental Authority would also need to be coordinated with both the Transmission Service Provider (TSP) and ERCOT ISO.  While the Department of Energy (DOE) may issue an order for connection, the DOE does not have the situational awareness to determine the impact of its directive on the reliability of the ERCOT Interconnection.  The functional responsibility of Reliability Coordinator has been assigned to ERCOT ISO (as the Control Area Authority).  As a result, it is ERCOT ISO’s duty to coordinate Block Load Transfers (BLTs) in order to ensure that they do not negatively impact the reliability of the ERCOT Grid.

ERCOT also requests that the language proposed by Brazos Electric Power Cooperative be struck.  ERCOT requires that all BLTs be registered whether the BLT is in the Network Operations Model or not, as well as whether the BLT is to be considered in wholesale settlements or not.  The purpose of registration is two-fold: (1) to comply with paragraph (a) of Section 6.5.9.5, Block Load Transfers between ERCOT and Non-ERCOT Control Areas, so that the ISO has information on the BLT in support of issuing clearance to deploy, and (2) to document BLTs for reporting to the North American Electric Reliability Corporation (NERC).

In addition, in the definition of “Block Load Transfer,” ERCOT proposes deleting the reference to transmission to be consistent with other proposed revisions, which recognize that BLTs may occur at the distribution level.

Revised Proposed Protocol Language

2.1	DEFINITIONS

Block Load Transfer (BLT)

A transfer system that isolates a group of Loads from the Control Area in which they normally are served and then connects them to another Control Area.  Such transfer systems involve either transferring Loads normally in the ERCOT Control Area to a non-ERCOT Control Area or transferring Loads normally in non-ERCOT Control Areas to the ERCOT Control Area.

6.5.9.5	Block Load Transfers between ERCOT and Non-ERCOT Control Areas

BLTs are procedures that transfer Loads normally located in the ERCOT Control Area to a non-ERCOT Control Area.  Similarly, when a non-ERCOT Control Area experiences certain transmission contingencies or short-supply conditions, ERCOT may agree to the implementation of BLT procedures that transfer Loads normally located in a non-ERCOT Control Area to the ERCOT Control Area.  BLTs are restricted to the following conditions:

(a)	BLTs shall occur only with approval from ERCOT for Planned or Forced Outages.  In the event an order is issued by a Governmental Authority requiring the BLT, ERCOT shall take into consideration the directives in the order during its coordination of the BLT with the TSP.

(b)	BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time.  Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt In Entity (NOIE) metering points.

(c)	BLTs of Load to the ERCOT Control Area are:

(i)	Treated as non-competitive wholesale Load in the Load Zone containing the ERCOT breaker or switch that initiated the BLT;

(ii)	Registered in accordance with 6.5.9.5.1, Registration and Posting of BLT Points, by the TSP in the ERCOT Control Area responsible for implementing the BLT;

(iii)	Responsible for Unaccounted For Energy (UFE) allocations and Transmission Losses consistent with similarly situated NOIE metering points; and

(iv)	Permitted only if the BLT will not jeopardize the reliability of the ERCOT System.  Under an Emergency Notice, BLTs that have been implemented may be curtailed or terminated by ERCOT to maintain the reliability of the ERCOT System.

(d)	BLTs of Load from the ERCOT Control Area are:

(i) 	Treated as Resources in the ERCOT Settlement system and may only be instructed with the permission of the affected non-ERCOT Control Area.  Under an Emergency Condition, BLTs that have been implemented may be curtailed or terminated by the non-ERCOT Control Area to maintain the reliability of the non-ERCOT system;

(ii)	Registered in accordance with Section 6.5.9.5.1 by the TSP in the ERCOT Control Area responsible for implementing the BLT; and

(iii)	Permitted only if the BLT will not jeopardize the reliability of the ERCOT System.

(e)	BLTs specifically exclude transfers of Load between ERCOT and non-ERCOT Control Areas that occur behind a retail Settlement Meter.

(f)	BLTs may be used in the restoration of service to Customers if the transfers will not jeopardize the reliability of the ERCOT System.

(g)	BLT metering points connected to the ERCOT Transmission Grid and registered according to Section 6.5.9.5.1 and used five or more time per year, as monitored by the TSP, must conform to ERCOT-Polled Settlement (EPS) Metering requirements as defined in Section 10, Metering, and the Settlement Metering Operating Guide.  All other BLT metering points must be revenue quality, four channel bi-directional kWh/kVArh, 15-minute Interval Data Recorder (IDR) metering with remote interrogation.  ERCOT may impose additional metering requirements it considers necessary to ensure ERCOT System reliability and integrity.

(h)	SCADA telemetry on switching devices at BLT points that are deemed necessary by ERCOT to be modeled in the Network Operations Model must be provided by the TSP registering the BLT.

6.5.9.5.1	Registration and Posting of BLT Points

(1)	The necessary Market Participant registration, agreements, metering, and ERCOT Settlement systems, as applicable, must be in place before implementation of any BLT.  At its sole discretion, ERCOT may exclude a BLT of ten MW or less from the Network Operations Model and associated telemetry requirements.

(2)	ERCOT may require any size of BLT that has been deployed in accordance with 6.5.9.5.2, Scheduling and Operation of BLTs, to be in the Network Operations Model with required telemetry if ERCOT determines it is warranted due to the length of time deployed.

(3)	BLTs that transfer Load from the ERCOT Control Area to a non-ERCOT Control Area are treated as a Resource by ERCOT and assigned a Resource ID.  The ERCOT Control Area TSP or DSP associated with the BLT Point has the responsibility for registering the BLT and the creation and maintenance of BLT Resource IDs for Settlement purposes.  For BLTs occurring on NOIE TSP or DSP systems, the NOIE may designate NOIE metering point(s), a Resource Entity, and a QSE for Settlement purposes.  For BLTs occurring on TSP or DSP systems open to Customer Choice, the non-ERCOT Control Area Entity receiving the transferred Load shall designate a registered Resource Entity and acknowledge a QSE for Settlement purposes in accordance with Section 16.5, Registration of a Resource Entity.  The ERCOT Control Area TSP or DSP must complete the applicable BLT registration form.  This BLT registration form along with the metering design and data documentation is the basis for establishing the ERCOT data model of the BLT and associated metering points for Settlement as applicable.

(4)	BLTs that transfer Load from a non-ERCOT Control Area to the ERCOT Control Area are treated as a non-competitive wholesale Load by ERCOT and assigned an ESI ID.  The ERCOT Control Area TSP or DSP associated with the BLT Point has the responsibility for registering the BLT and the creation and maintenance of BLT ESI IDs.  Customers connected to the ERCOT System do not require an ESI ID separated from the assigned BLT ESI ID.  The TSP or DSP that registers the BLT Point shall provide the ESI ID associated with the BLT to ERCOT.  For BLTs occurring on NOIE TSP or DSP systems, the NOIE may designate NOIE metering point(s), an LSE, and a QSE for Settlement purposes.  For BLTs occurring on TSP or DSP systems open to Customer Choice, the non-ERCOT Control Area Entity shall designate a registered ERCOT LSE and acknowledge a QSE for Settlement purposes in accordance with Section 16.3, Registration of Load Serving Entities.

(5)	A “BLT Point” is the metering point for a BLT Resource ID or for a BLT ESI ID.

(6)	ERCOT shall post the registration details of all registered BLTs to the MIS Secure Area.

6.5.9.5.2	Scheduling and Operation of BLTs

(1)	For BLTs that transfer Load to a non-ERCOT Control Area, a verbal instructed Base Point shall be issued to the QSE for Settlement purposes for any energy associated with BLTs modeled in the Network Operations Model and registered as a Resource in accordance with Section 6.5.9.5.1, Registration and Posting of BLT Points. ERCOT shall confirm the BLT’s availability with the non-ERCOT Control Area before any BLT implementation.

(2)	Any energy associated with the non-ERCOT Control Area Load BLT Point is treated as a Load obligation of the QSE representing the LSE with the BLT ESI ID as registered for Settlement purposes in accordance with Section 6.5.9.5.1.

(3)	Generation Resources connected to the portion of the ERCOT Transmission Grid included in the BLT are under no obligation, under these Protocols, to provide Ancillary Services or any other services to ERCOT while that portion of the ERCOT Transmission Grid is connected to a non-ERCOT system other than through a DC Tie.

(4)	ERCOT shall continue to include the BLT Point Load in the Settlement of the LSE Load obligations.