| NOGRR Number | 038 |  |  | NOGRR Title | Synchronization with OGRR243, Disturbance Monitoring Requirements Clarification |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Timeline | Normal |  |  | Recommended Action |  | Approval |  |
| Date of Decision |  |  |  | July 15, 2010 |  |  |  |
| Proposed Effective Date |  |  |  | Upon Texas Nodal Market implementation. |  |  |  |
| Priority and Rank Assigned |  |  |  | Not applicable |  |  |  |
| Guide Section(s) Requiring Revision |  |  |  | 6.1.2.3, Data Recording Requirements 6.1.2.4, Data Retention and Reporting Requirements |  |  |  |
| Revision Description |  |  |  | This Nodal Operating Guide Revision Request (NOGRR) synchronizes the Nodal Operating Guides with OGRR243by changing data recording and reporting requirements for equipment operating at 100kV or above at Facilities where fault recording equipment is required. |  |  |  |
| Reason for Revision |  |  |  | The System Protection Working Group (SPWG) prefers that the fault data recording requirements allow for calculated electrical quantities which are used in modern protection system equipment and can be determined by modern fault analysis software. The SPWG also prefers that recording requirements for autotransformers should allow for monitoring of either high voltage or low voltage terminals and that specification in the fault reporting template of the recorded time standard (such as Central Prevailing Time (CPT) or Coordinated Universal Time (UTC)), replace the requirement of Central Standard Time (CST) recording requirements. |  |  |  |
| Overall Market Benefit |  |  |  | Synchronization of Nodal Operating Guides, clarification of fault recording requirements, and improve the ability of ERCOT, Transmission Service Providers (TSPs), and Resource Entities to determine and implement compliant fault recording equipment. |  |  |  |
| Overall Market Impact |  |  |  | None. |  |  |  |
| Consumer Impact |  |  |  | None. |  |  |  |
| Procedural History |  |  |  | - On 3/26/10, NOGRR038 and the associated CEO Revision Request Review were posted. - On 5/19/10, the Operations Working Group (OWG) considered NOGRR038. - On 6/7/10, an Impact Analysis was posted. - On 6/16/10, OWG considered the 5/19/10 OWG Recommendation Report and Impact Analysis for NOGRR038. - On 7/6/10, ERCOT comments were posted. - On 7/15/10, ROS considered NOGRR038. |  |  |  |
| OWG Decision |  |  |  | On 5/19/10, OWG was in consensus to recommend approval of NOGRR038 as revised by OWG. On 6/16/10, OWG was in consensus to forward the 5/19/10 OWG Recommendation Report as revised by OWG and the Impact Analysis for NOGRR038 to ROS. |  |  |  |
| Summary of OWG Discussion |  |  |  | On 5/19/10, the need to maintain consistency between the Protocols and Operating Guides by using CPT rather than CST in the Operating Guides was discussed. On 6/16/10, it was noted that currently “facility owner” is not a defined term in the Nodal Protocols or Operating Guides and until such definition is developed, the language in NOGRR038 would be clarified to include “facility/equipment owner”. It was also noted that the Nodal Protocol/Reliability Standards Alignment Task Force (NPRSATF) and the Nodal Operating Guide Review and Revision Task Force (NOGRRTF) would address this issue. |  |  |  |
| ROS Decision |  |  |  | On 7/15/10, ROS unanimously voted to recommend approval of NOGRR038 as recommended by OWG in the 6/16/10 OWG Recommendation Report and as revised by the 7/6/10 ERCOT comments. All Market Segments were present for the vote. |  |  |  |
| Summary of ROS Discussion |  |  |  | On 7/15/10, ERCOT Staff reviewed the 7/6/10 ERCOT comments which remove a potential conflict with North American Electric Reliability Corporation (NERC) Reliability Standards. |  |  |  |
| Quantitative Impacts and Benefits |  |  |  |  |  |  |  |
| Assumptions |  | 1 | The new format will help to improve the reliability of transmission protection systems. |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Market Cost |  |  | Impact Area |  |  |  | Monetary Impact |
|  |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Market Benefit |  |  | Impact Area |  |  |  | Monetary Impact |
|  |  | 1 | Improvement of TSPs and Resource Entities ability to successfully comply with listed recording requirements |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Additional Qualitative Information |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |
| Other Comments |  | 1 | None |  |  |  |  |
|  |  | 2 |  |  |  |  |  |
|  |  | 3 |  |  |  |  |  |
|  |  | 4 |  |  |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Glenn Hargrave on behalf of SPWG |
| E-mail Address | grhargrave@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | (210) 353-4215 |
| Cell Number | (210) 394-1313 |
| Market Segment | Municipality |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 070610 | Proposed language changes to remove a potential conflict with NERC Reliability Standards. |

Proposed Guide Language Revision

- 6.1.2.3	Data Recording Requirements

(1)	For facilities operating at 100kV or above where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

(a)	Two sets of voltages for breaker-and-a-half and ring bus substation configurations.  One set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform;

(b)	For all lines, neutral (residual) current waveform;

(c)	Circuit breaker status;

(d)	Circuit breaker trip circuit status; and

(e)	Date and time stamp Central Prevailing Time (CPT).

(2)	For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

(a)	For all autotransformers, high or low voltage terminal current waveform for three phases and either neutral / residual current waveform or current waveform in delta windings;

(b)	For all lines, two phase current waveforms;

(c)	Status – carrier transmitter control (i.e. start, stop, keying); and

(d)	Status – carrier received.

- 6.1.2.4	Data Retention and Reporting Requirements

(1)	The facility/equipment owner shall store all recorded fault data for at least a three year period.  This data shall be stored in the form of a computer file or files.

(2)	Facility/equipment owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five days, along with channel identification and scaling information to allow analysis of the recordings.  Fault recordings shall be shared between facility/equipment owners, upon their request, for the analysis of ERCOT System disturbances.

(3)	When multiple recordings exist for a single event, only report to ERCOT and NERC of data from the best recording, usually the closest recorder is required.

(4)	Data submissions shall be COMTRADE fault recordings, .cfg and .dat files, and one or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel© spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel© spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |
| --- | --- |
|  | From Bus (ERCOT short circuit database bus number) |
|  | To Bus (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Faulted Branch or Bus (kV) |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location. If physical location not found, leave blank) |  |
|  | Date (MM/DD/YYYY) |
|  | Time (HH:MM:SS, 24 hour format) |
|  | Cause Code |
| Fault Recorder Data | Circuit (1, 2, A, B, N, S, etc.) |
|  | From Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |
|  | Nominal Voltage of Monitored Branch (kV) |
|  | Measured Current Magnitude (primary value in RMS amperes) |
|  | Recorded Fault Duration (cycles) |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |
| Optional Comments (40 char. max.) |  |