Texas Renewables Integration Plan (TRIP)

Prepared by the Renewable Technologies Working Group of the ERCOT Technical Advisory Committee

DRAFT version 6

April 20, 2010

Note: This document contains the comments submitted by the following:

- Calpine (Author = Randy Jones or Calpine or RJ)

- PSEG (Author = PDMAW or PSEG)

- Centerpoint (Author = 00010966)

- STEC (Author = STEC)

- Luminant (Author = Luminant or Henry Durrwachter)

Also note that the colors of the changes are tied to the Author name, such that there may be more than one color associated with the changes submitted by a particular company (e.g., Luminant’s comments are two different colors, one for the author “Luminant” and one for the author “Henry Durrwachter”), but all comments submitted by the above parties have been captured in this one document. The pictures shown on the first page have been deleted to reduce file size.

Preface

The combination of several forces has led to a rapid and significant addition of renewable energy generating capacity within the Electric Reliability Council of Texas (ERCOT) in recent years, primarily in the form of large-scale wind generation resources.

The ERCOT Independent System Operator (ISO) and the ERCOT stakeholders embrace the open access network paradigm adopted by the Texas Legislature.  Stakeholders have worked to integrate interconnections of renewable energy resources.  Stakeholders endeavor to allow market forces, to the greatest extent possible, to provide the generation resources, ancillary services, and other technical solutions necessary to ensure adequate system security.  However, those parties responsible for system planning and operational security also recognize that the widespread introduction of variable output renewable generation resources presents significant challenges which must be addressed in order to effectively and efficiently maintain system reliability.

The Texas Legislature’s goal for increasing amounts of installed renewable energy capacity has been successful.  Implementation of the Public Utility Commission of Texas (PUCT or Commission) Competitive Renewable Energy Zones (CREZs) requires a comprehensive review and potentially significant improvements to ERCOT planning models and assumptions, operational capabilities and procedures, and certain elements of the ERCOT Zonal and Nodal market designs and systems.  The Texas Renewables Integration Plan (TRIP) is  one of many reference  documents for this effort.

The TRIP is the work product of the ERCOT Technical Advisory Committee (TAC) by and through its Renewable Technologies Work Group (RTWG).

Table of Contents

| Executive Summary . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  |  | . . . 8 |
| --- | --- | --- | --- | --- | --- |
| 1. | Introduction . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . 10 |
| 2. | Texas Renewables Integration Plan Overview . . . . . . . . . . . . . . . . . . . |  |  |  | . . . 13 |
|  | 2.1. | TRIP Purpose . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . 13 |
|  | 2.2. | TRIP Structure . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . 13 |
|  |  | 2.2.1. | Phases . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 14 |
|  |  | 2.2.2. | Goals . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 14 |
|  |  | 2.2.3. | Recommendations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 15 |
|  |  | 2.2.4 | Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 15 |
|  |  | 2.2.5. | Issues Identification and Prioritization . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 16 |
|  |  | 2.2.6 | Issues Organization . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.7 | Strategies for Resolution and Follow-Up . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.8 | Schedule . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 17 |
|  |  | 2.2.9. | Activities for ERCOT and Market Participants . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.10 | Issues Tracking . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.11. | Quarterly Reports . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 18 |
|  |  | 2.2.12. | RTWG Work Plan . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | 19 |
|  | 2.3. | TRIP Input Process, Change Procedure, and Revision Schedule . . . . . . . |  |  | . . . X |
| 3. | Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 3.1. | Public Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.1.1. | Federal Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | XX |
|  |  |  | 3.1.1.1. | Federal Tax Policy . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.1.2. | Federal Energy and Environmental Policy . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  | 3.1.2. | State Policy Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | XX |
|  |  |  | 3.1.2.1. | Competitive Renewable Energy Zones . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.2. | Energy Efficiency and Advanced Meters . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.3. | Solar Generation Technologies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | XX |
|  |  |  | 3.1.2.4. | Distributed Generation and Energy Storage Technologies . . . . . . . . | XX |
|  |  | 3.1.3. | Policy Issues Raised by Integration of Renewable Technologies . . . . . . . . . . . . . |  | XX |
|  | 3.2. | System Reliability Considerations . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.2.1. | System Planning Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  |  | 3.2.1.1. | Quality of Data and Models . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.2. | Generation Interconnection . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.3. | Transmission Planning . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.4. | System Planning Studies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.1.5. | ERCOT Planning Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  | 3.2.2. | System Operations Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  |  | 3.2.2.1. | Quality of Data, Models, and Systems . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.2. | Dispatchable Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.3. | Generation Ramping Capability and Limitations . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.4. | Frequency Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.5. | Ancillary Services . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.6. | Voltage Control . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.7. | Renewable Generation Forecasting . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  |  |  | 3.2.2.8. | ERCOT Operations Resources . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . | X |
|  | 3.3. | Technical Considerations . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.3.1. | Technical Capabilities and Integration Challenges . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.2. | Technical Approach to Renewable Technologies . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.3. | Technical Challenges to System Planning . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.4. | Technical Challenges to System Operations . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.3.5. | Technical Education and Institutional Knowledge . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 3.4. | Market Design Considerations . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.4.1. | Principles of ERCOT Market Design . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.4.2. | Impacts of Renewable Technologies on ERCOT Markets . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.4.3. | Market Design Approach for Renewable Technologies . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 3.5. | Performance Criteria and Compliance Metrics . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.5.1. | Principles of Performance Criteria and Compliance Metrics . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.5.2. | Application of Performance Criteria to Renewable Technologies . . . . . . . . . . . . |  | X |
|  |  | 3.5.3. | Application of Performance Data to Renewable Technologies Integration . . . . . . |  | X |
|  | 3.6. | Cost Allocation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.6.1. | Principles of Cost Allocation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.6.2. | Cost Allocation Task Forces . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.6.3. | Application of Cost Allocation Principles to Renewable Technologies . . . . . . . . |  | X |
|  | 3.7. | Texas Nodal Market Implementation . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | 3.7.1. | Renewable Technologies Integration Benefits of the Texas Nodal Market . . . . . |  | X |
|  |  | 3.7.2. | Addressing Renewable Technology Issues in Nodal Testing and Start Up . . . . . . |  | X |
|  |  | 3.7.3. | Texas Nodal Market Implementation Schedule and Resource Requirements . . . . |  | X |
|  |  | 3.7.4. | Post-TNMID Evaluation of Wind Operations Issues . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | 3.7.5. | Nodal Parking Deck . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
| 4. | Key Issues and Strategies for Resolution . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 4.1. | System Planning Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | SP-01 | Verify Wind Turbine Technical Data . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-02 | Wind Turbine Computer Models . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-03 | Wind Turbine Fault Tolerance . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-04 | Voltage Transient and Small Signal Stability Study . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-05 | Impact of Wind Turbines on System Inertia . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-06 | Use of Variable Frequency Transformers to Solve Stability Problems . . . . . . . . . |  | X |
|  |  | SP-07 | Voltage Control Process . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-08 | Voltage Ride-Through Study . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-09 | Wind Turbine Model Validation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SP-10 | DOE Long-Term Planning Study . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.2. | System Operations Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | SO-01 | Inventory of Wind Generation Facilities . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-02 | Nodal Tools to Integrate Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-03 | Wind Generation Response and Schedule Control Error (SCE) . . . . . . . . . . . . . . |  | X |
|  |  | SO-04 | Smart Grid Implications for Renewable Resources . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-05 | Operational Studies Related to Wind Integration . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-06 | Testing Reactive Capability of Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-07 | Wind Generation and High System Frequency . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-08 | Wind Generation and System Inertia . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-09 | SCADA Control of Generation Circuit Breakers . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-10 | Voltage Management Practices Applicable to Wind Generators . . . . . . . . . . . . . . |  | X |
|  |  | SO-11 | Technology-Specific Procedures and Protocol Changes . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-12 | Low-Voltage Ride-Through for Wind Generators . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-13 | Performance Metrics for Wind Generation . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-14 | Impact of Transmission Outage Planning on Wind Generation . . . . . . . . . . . . . . |  | X |
|  |  | SO-15 | Communications Between Wind Farms and TSPs . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-16 | Wind Generation Ramp Limits . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-17 | Mid-Term and Short-Term Load Forecast Weather Sensitivity . . . . . . . . . . . . . . |  | X |
|  |  | SO-18 | Evaluate Transmission Line and Wind Power Production Outage Criteria . . . . . . |  | X |
|  |  | SO-19 | Improve Competitively Sensitive Constraint (CSC) Process . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-20 | Dynamic Transmission Line Ratings . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-21 | Evaluate Emergency Electric Curtailment Plan (EECP) Steps . . . . . . . . . . . . . . . |  | X |
|  |  | SO-22 | Open . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-23 | Impact of Advanced Meters on Integration of Renewable Resources . . . . . . . . . . |  | X |
|  |  | SO-24 | Settlement of Advanced Meters in the Nodal Market . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-25 | Generator Governor Response for Wind Generators . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-26 | Impact of Solar Generation on System Operations . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-27 | Manual Curtailment of Wind Generation to Resolve Local Congestion . . . . . . . . |  | X |
|  |  | SO-28 | SPS Actuation for N-0 Conditions . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-29 | Transmission Outage Planning for CREZ . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-30 | Application of Wind Generation Forecast to PASA . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-31 | Tension Monitors on Transmission Lines . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-32 | Real-Time Wind Generation Capacity . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-33 | Real-Time Wind Turbine Availability . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | SO-34 | SCED Line Ratings . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.3. | Market Design Issues . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | MD-01 | Ancillary Services Cost Allocations Applicable to Wind . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-02 | Ancillary Services Procurement Optimization for 2009 . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-03 | Non-Spin Requirements . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-04 | New Ancillary Services Products Needed for Reliability . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-05 | Benefits of Storage Technologies . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-06 | Ancillary Services Procurement Methodology . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-07 | Wind Generating Resources Providing Ancillary Services . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-08 | Reactive and Voltage Requirements Applicable to Wind Generators . . . . . . . . . . |  | X |
|  |  | MD-09 | Wind Generation Dispatch in the Nodal Protocols . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-10 | Wind Generation Performance Metrics in the Nodal Protocols . . . . . . . . . . . . . . . |  | X |
|  |  | MD-11 | Wind Generation and Base Point Deviation in the Nodal Protocols . . . . . . . . . . . |  | X |
|  |  | MD-12 | Wind Generation Resource LSL as a Percentage of HSL . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | MD-13 | Use of State of the Art Wind Forecast . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  | 4.4. | Workshop and Training Issues . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  |  | WT-01 | Resource Plan and Schedule Update Process . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-02 | Wind Workshop III – Summer 2009 . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-03 | Wind Turbine Operator Training . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-04 | Wind in the Nodal Market . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-05 | Wind Workshop IV . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-06 | Solar Workshop . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
|  |  | WT-07 | Energy Storage Workshop . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  | X |
| 5. | 2010-2011 RTWG Work Plan . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . . X |
|  | 5.1. | RTWG Charter . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.2. | RTWG Goals . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.3. | RTWG Activities . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 5.4. | RTWG Work Product . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
| 6. | Summary Tables . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |
|  | 6.1. | Summary Table of TRIP Goals . . . . . . . . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 6.2. | Summary Table of TRIP Recommendations . . . . . . . . . . . . . . . . . |  |  | . . . X |
|  | 6.3. | Summary Table of Recommended ERCOT Activities . . . . . . . . . . . . |  |  | . . . X |
|  | 6.4. | Summary Table of Recommended Market Participant Activities . . . . . . |  |  | . . . X |
|  | 6.5. | Summary Schedule of Major TRIP Activities . . . . . . . . . . . . . . . . . |  |  | . . . X |
| 7. | Appendices . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |
|  | 7.1. | 2009 RTWG White Papers |  |  | . . . X |
|  | 7.2. | 2008-2009 Wind Workshop Presentations |  |  | . . . X |
|  |  | 7.2.1. | Wind Workshop I, March 17, 2008 |  |  |
|  |  |  | 7.2.1.1 | Presentation Title |  |
|  | 7.3. | 2009 RTWG Presentations |  |  | . . . X |
| 8. | References . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . |  |  |  | . . XX |

Executive Summary

Text.

1.	Introduction

In early 2008, ERCOT Staff approached the TAC leadership with a request to hold a workshop focused on operational challenges related to the increasing amount of wind energy production on the ERCOT system.  The workshop, which has since become known as Wind Workshop I, was scheduled for mid-March 2008.  In the intervening period, ERCOT experienced a significant system disturbance on Feb. 26, 2008.  During this event, which had numerous causes and complicating factors, dramatic variations in wind energy output and deviation from wind energy schedules were the proximate causes.  This event added urgency to the scheduled workshop as more and more stakeholders came to realize the near-term importance of addressing operational challenges posed by wind energy production.

Wind Workshop I kicked off a 2-year period of intense focus by ERCOT Staff and stakeholders to address wind integration challenges.  The immediate task was to address the issues raised by ERCOT (PUCT?)Operations Staff at Wind Workshop I because they were viewed by ERCOT Operations to be critical to system security.  The key issues and their resolution are summarized below.

- Develop a common understanding of the impact of wind generation on operations:  ERCOT provided examples of recent operational experiences with wind generation under various scenarios and noted that a lack of understanding on the part of some wind resource owners regarding the details of certain operational procedures  produced inconsistent results in unit responses to instructions and introduced operational challenges.

TAC assigned workshop follow-up items to the Wholesale Market Subcommittee (WMS) and the Reliability and Operations Subcommittee (ROS).  Numerous Protocol Revision Requests flowed from the subcommittee efforts to address the workshop issues raised by ERCOT and other issues which surfaced through the focused follow-up discussions.  The ROS created the Wind Operations Task Force (WOTF) to work closely with ERCOT Operations to quickly focus on the operational issues.  The TAC created the Renewable Technologies Work Group (RTWG) to, in part, maintain a centralized issues list so market-wide education on wind issues could be facilitated.

Focused collaboration between ERCOT and stakeholders led to numerous procedural changes and data collection projects which did not require zonal Protocol Revision Requests (PRRs) or Nodal Protocol Revisions Requests (NPRRs) to implement.  Noteworthy examples of issues addressed identified and resolved in this manner include:

  - Improved communication between Wind Generation Resources (WGRs) and Transmission Service Providers (TSPs) regarding operational practices

  - Clarification and strengthening of voltage support requirements and timelines

  - Improved quality and quantity of ERCOT data on WGR unit designs and capabilities

  - More frequent CSC limit calculations to improve zonal transfers

- Identification of current problems, anticipated future problems, changes to be implemented in the zonal market, and changes to be implemented in the nodal market:  In the weeks following Wind Workshop I, ERCOT and stakeholders identified a range of issues which required Revision Requests to implement.  Resource constraints related to the nodal market transition effort forced parties to reach solutions that minimized systems impacts and maximized ease of implementation.  Many of the PRRs and NPRRs were granted Urgent status.  The full list of approved PRRs and NPRRs stemming from this effort are described below, but some noteworthy examples include:

  - Replace WGR QSE wind schedules with ERCOT wind forecast

  - Impose WGR ramp rate limitations

  - Requirement for WGRs to accelerate implementation of nodal telemetry standards

  - Clarified definitions and performance measures for WGR scheduling practices

  - WGR voltage ride-through requirements

  - WGR Reactive Power Requirements (PRR-830)

  - WGR Primary Frequency Response (PRRs 824 & 833)

- Replace WGR QSE wind schedules with ERCOT wind forecast:  ERCOT observed that the accuracy of WGR Resource Plans varied widely across the market and illustrated the consequences of poor forecasting on Day Ahead and Hour Ahead capacity adequacy studies.  Because ERCOT’s look-ahead studies automatically use Resource Plan data from the Scheduling Pricing Dispatch (SPD) system, any modifications to the software would have significant impacts on ERCOT resources and budget.  A quicker and more cost-effective solution was developed (PRR 763) that required WGR QSEs to make the changes in their own Resource Plans using ERCOT-provided forecast data (i.e., the AWS TrueWind forecast).  ERCOT developed a system project to provide wind operators with the forecast for use in the Resource Plans.  PRR 763 became effective July 1, 2008.

- Establish wind ramp rate requirements:  ERCOT provided examples of wind units with high ramp rates, especially when released from down balancing instructions during windy periods.  The steep ramp rates presented operational challenges to ERCOT, notably in system frequency control.  Due to variations in wind turbine technical capabilities, stakeholders bifurcated the issue into two solutions.  The first (PRR 771), applied a ramp rate limit when responding to or being released from an ERCOT deployment instruction to wind turbines wind facilities with Interconnection Agreements signed Interconnect Agreements executed on or after January 1, 2009. The second (PRR 788), applied to the same standard to most existing wind turbines in ERCOT.  PRRs 771 and 788 were effective Jan. 1, 2009 and Feb. 1, 2009, respectively.

Following Wind Workshop I and the subsequent related work of resolving the identified issues of immediate concern, TAC and the ERCOT Board of Directors (Board) directed ERCOT Staff and the stakeholder process to undertake a variety of efforts to more holistically address the wide array of issues related to integration of renewable technologies with a particular focus in the near term on operational challenges associated with WGRs.  TAC formed the RTWG and charged it to develop a renewable technologies integration plan.

In this plan, the RTWG has endeavored to provide sufficient background discussion and information to give the broader document contextual meaning.  However, this document is not intended to be a primer on general renewable technologies integration issues.  Section 8 of this document provides references to such material.  Rather, this document and its quarterly updates are intended to be regularly used by active ERCOT market policy makers and stakeholders to plan, track, and complete the range of activities and work products recommended to successfully integrate renewable energy technologies into the ERCOT system.

It should also be noted that although the specific directive from the ERCOT Board and TAC was to address the integration of variable renewable generation technologies, the RTWG strongly recommends equal attention be paid to energy storage technologies and certain “smart grid” technologies, either because they may be “renewables-enabling” technologies or because they are likely to have impacts on ERCOT functions, system reliability, processes, and systems potentially similar to those resulting from renewable technologies.

2.	Texas Renewables Integration Plan Overview

The Texas Renewables Integration Plan (TRIP) is a work product of the TAC by and through the RTWG and is one of many reference documents describing the efforts of the ERCOT Independent System Operator and market stakeholders to integrate significant levels of large-scale and distributed renewable generation technologies into the ERCOT system as well as to address issues raised by other emerging technologies associated with or enabling renewable technologies such as storage generation devices.

2.1.	TRIP Purpose

The TRIP serves six key purposes, each of which is stated as a goal of the plan.

| Goal 01 | Identify and communicate issues of interest related to the integration of renewable resources to market participants and industry stakeholders. |
| --- | --- |

| Goal 02 | Develop and recommend strategies that may resolve identified issues. |
| --- | --- |

| Goal 03 | Communicate potential long-term plans of action for ERCOT activities related to renewable technologies integration to market participants and industry stakeholders. |
| --- | --- |

| Goal 04 | Communicate progress on renewable technologies integration and raise issues for consideration to Texas policy makers and ERCOT ISO decision makers. |
| --- | --- |

| Goal 05 | Document the renewable technologies integration activities within the ERCOT Region as a resource for electric power industry stakeholders. |
| --- | --- |

| Goal 06 | Document “lessons learned” through the ERCOT renewable technologies integration effort to preserve institutional memory and better inform ongoing integration activities. |
| --- | --- |

2.2.	TRIP Structure

The TRIP is divided into three phases, each with goals and recommendations for action.  The plan is organized around the specific issues identified to enable renewable technology integration.  The issues are divided into four broad categories – system planning, system operations, market design, and workshops and training.  A consistent set of considerations are applied to each issue to ensure all angles are thoroughly vetted.  Each issue is assigned a priority, a schedule for resolution, and one or more parties responsible for the required work product.  A summary spreadsheet of progress toward issues resolution is provided quarterly to the TAC, ERCOT Board, and PUCT.

2.2.1.	Phases

As discussed in greater detail below, the significance and scope of the Texas Nodal Market implementation project presents a variety of challenges to other efforts to revise ERCOT Zonal  market rules, systems, and procedures.  Accordingly, the TRIP is divided into three distinct phases.

- Phase One:  High priority large-scale wind issues to be resolved in the Zonal Market and those with ERCOT systems changes deemed necessary for the Texas Nodal Market Implementation Date (TNMID).  Phase One began with the March 17, 2008 Wind Workshop I and ends with the “pens down” date for zonal systems changes and TNMID systems changes.

- Phase Two:  Identify post-TNMID large-scale wind issues and strategies for resolution.  Where needed, work with standing TAC Subcommittees to anticipate integration issues associated with other utility- and distributed-scale renewable technologies such as solar generation and storage generation and develop any potential Texas Nodal Market v1.X and/or v2 solutions.  Continue Phase One follow-up activities.

- Phase Three:  Tracking and communicating implementation of Phase Two solutions and follow-up activities.

Due to the large number and urgent nature of challenging wind generation issues to be addressed at the same time the ERCOT stakeholder leadership directed the formation of this long-range plan to address renewable technologies integration issues.  Most Phase One activities described in the plan occurred concurrently with the plan’s development and are shown in this document as completed activities.

2.2.2.	Goals

Goals of the TRIP and the RTWG are included throughout the document.  A summary table of goals is found in Section 6.1.

2.2.3.	Recommendations

The TRIP includes specific recommendations to resolve each identified renewable technologies integration issue.  A summary table of recommendations is found in Section 6.2.

2.2.4.	Considerations

As renewable technologies integration issues are identified, stakeholders must address a wide array of considerations to ensure each issue is vetted from all sides and unintended consequences are minimized.

- Public Policy:  .  Each issue is examined for public policy impacts.  Some issues present policy questions which are forwarded to the appropriate body for resolution.

- System Reliability: Both the system planning function and the system operations function play critical roles in ensuring electric system reliability.  Many renewable technology integration issues present challenges to one or both of these functions.  Each issue is explored from both perspectives to ensure that the integration of renewable technologies does not compromise system reliability.

- Technical: Many of the emerging technologies addressed by the TRIP have very different operating abilities and characteristics than the conventional generation technologies familiar to system planners and operators.  These new technologies may present both opportunities and challenges for ERCOT, market participants, and consumers.

- Market Design:  Sound market design principles canshould address the majority ofall integration issues by aligning requirements and incentives to comply.  In other instances, issues may arise from existing market design elements.  Recommendations must consider market impacts and market design impacts. .

- Performance Criteria and Compliance Metrics:  Some integration issues may be resolved through clarification or creation of performance criteria for renewable generators or other market participants.  In some instances, compliance metrics may also be required to provide regular, transparent reporting on renewable technology adherence to market rules or procedures, both as a dashboard gauge for policy makers and to enable follow-up measurement and analysis for ongoing integration efforts.

- Cost Allocation:  The ERCOT market design utilizes various cost allocation methodologies, some are directly assigned to one or more market participants based on causation principles while others are assigned across a number of market participants on a pro rata basis.

- Texas Nodal Market Implementation:  The recommended solution for any identified renewable technologies integration issue must respect the boundaries resulting from the Texas Nodal Market implementation project and must consider whether solutions should be implemented in the Zonal and/or Nodal markets.

- [Seems like a budgetary criterion should be used as well.  We should show some respect for the intersection of “good ideas for integrating a technology” and “ERCOT’s capital budget constraints”, particularly if the proposed solution to an integration issue involves socializing the cost across the market by requiring ERCOT to install new hardware and/or software specifically for renewable integration (example:  forward facing met towers may be a good idea but can ERCOT afford to install them on its current capital budget and do all stakeholders agree to pay for the continuing upkeep costs?]

2.2.5.	Issues Identification and Prioritization

The heart of the TRIP is the exploration of all likely facets of interaction between renewable technologies and the ERCOT system and markets to identify issues requiring resolution.  Issues may be raised in a variety of ways – through the normal course of business in the stakeholder process, by individual market participants, by ERCOT Staff observations of operational practices, or as directed by policy makers.  To facilitate the identification, coordination and tracking of issues, the RTWG appointed liaisons to the ERCOT Reliability and Operations Subcommittee (ROS), Wholesale Market Subcommittee (WMS), Nodal Advisory Task Force (NATF), and Regional Planning Group (RPG).  Once identified, issues are named, numbered, described, prioritized, analyzed, addressed, and tracked.

Each identified issue is prioritized for resolution.  The four categories of prioritization are Near-Term, Long-Term, Undetermined, and Complete.  The prioritization of issue resolution depends upon several factors including significance to system reliability or market functionality, time required to complete associated tasks, resource availability, and any other identified dependencies.  Prioritization of issues is expected to assist ERCOT and market participants with the allocation of resources to renewable technologies integration efforts in a timely, methodical, coordinated, and cost-effective manner.  Identified issues presenting immediate concerns for system reliability or significant market impacts are escalated for rapid resolution.

2.2.6.	Issues Organization

The TRIP is organized around identified renewable technology integration issues.  These issues are organized by general area of impact as follows:

- System Planning (SP):  Issues which impact or are impacted by the system planning function or require system planning activities to achieve resolution.

- System Operations (SO):  Issues which impact or are impacted by the system operations function or require system operations activities by ERCOT and/or market participants to achieve resolution.

- Market Design (MD):  Issues primarily concerning market activities or market outcomes.

- Workshops and/or Training (WT):  Issues which require stakeholder education and/or brainstorming.  Also, the activities related to effective communication of issues resolutions to market participants and the industry for implementation and operations.

2.2.7.	Strategies for Resolution and Follow-Up

For each identified issue, a strategy is developed to resolve the issue.  Tasks required to resolve the issue are assigned to an RTWG member.  The completion of tasks is tracked and published to promote progress and transparency.  Resolved issues are reported to the ERCOT Board and PUCT in the quarterly updates.  A complete list of resolved and tabled issues is included in the TRIP and the RTWG Issues List to preserve institutional memory.  Where appropriate, the TRIP describes processes for monitoring, evaluating, and reporting on the effectiveness of renewable technology implementation solutions developed through the TRIP which may, in some instances, require follow-up activities after the issue is deemed completed.

2.2.8.	Schedule

For each identified issue, a schedule for resolution is proposed, including timelines for required studies, systems projects implementation, market testing, etc.  The priority assigned to the issue by the RTWG and the resources available to identify and implement a solution are key inputs to the recommended schedule.

2.2.9.	Activities for ERCOT and Market Participants

Some actions will be required of ERCOT and others of the stakeholder process or market participants.  A summary table of recommended activities for ERCOT and market participants is found in Sections 6.3 and 6.4.

2.2.10.	Issues Tracking

Identified integration issues are tracked on the RTWG Issues List, which is an abbreviated and frequently updated version of Section 4 of the TRIP.  The Issues List is updated at least quarterly.  For each identified issue, the Issues List includes:

- the issue identification number;

- a brief description of the issue;

- the volunteer stakeholder  to which the issue is assigned for resolution;

- the issue priority ranking;

- the proposed mechanism for issue resolution, if known (such as PRR, OGRR, etc.);

- the current status of the issue, including keeping track of completed issues to preserve institutional knowledge; and

- cross-references to other ERCOT documents addressing the issue to enable full-spectrum issues tracking.

2.2.11.	Quarterly Reports

In fulfillment of the PUCT Order requiring ERCOT to provide quarterly updates on the resolution of wind integration issues, the RTWG prepares quarterly reports on TRIP progress to the TAC which, in turn, updates the ERCOT Board and PUCT.  Each quarterly report features:

- the amount of installed renewable generation capacity in ERCOT;

- a summary of renewable technology interconnection activities;

- a review of significant events in the previous quarter related to renewable technologies;

- an update on issues completed or new issues identified in the previous quarter;

- the most recent version of the RTWG Issues List; and

- any other relevant information.

2.2.12.	2010-2011 RTWG Work Plan

The monthly meetings of the RTWG provide a forum for market participants to identify, resolve, and track renewable technologies integration issues as well as to share and maintain technical knowledge.  Additionally, the RTWG sponsors workshops featuring in-depth discussion of particular issues to ensure recent changes in technical standards or market rules are communicated to industry participants.  Section 5 describes the RTWG work plan and anticipated work product for the period between the adoption of this plan and the next expected update of the TRIP in the first quarter of 2012.  The RTWG anticipates Phase One activities ending in early 2010 and focusing on Phase Two activities through early 2012.

2.3.	TRIP Input Process, Change Procedure, and Revision Schedule

TAC and the RTWG welcome input to the TRIP from a variety of sources.  All meetings of TAC and its subgroups are public and the meeting locations and agendas are listed on the ERCOT calendar page at least one week in advance of the meeting.  Issues related to the integration of renewable resources may be introduced for inclusion in the TRIP at any meeting of the TAC or its subgroups.  Additionally, TAC seeks the input of the ERCOT Board of Directors and PUCT at least quarterly.  At the direction of TAC, the RTWG maintains the responsibility for incorporating identified issues into the TRIP and the accompanying RTWG Issues List.

All changes or updates to the TRIP are made by the RTWG.  As a working group of the TAC, the RTWG operates on a consensus-based paradigm with reporting to TAC of majority and minority positions when consensus cannot be achieved.  (RTWG does not have a formal voting structure.) The TAC maintains sole authority for the final stakeholder recommendations on all issues in the TRIP.

The next full revision of the TRIP is planned to be presented to the TAC approximately 1 year after the TNMID or earlier if circumstances warrant.

3.	Considerations

Each renewable technology integration issue identified by the RTWG is examined in light of a number of considerations to ensure completeness of thought, coordination with other issues, and to minimize unintended consequences of proposed changes to market rules, technical standards, and procedures.

3.1.	Public Policy Considerations

The ERCOT TAC does not strive to influence public policy regarding any electric power generation technology.  However, the TRIP endeavors to be responsive to public policy directives and provide solutions to the impacts of public policy directives regarding the introduction of new renewable technologies into ERCOT system and markets and the TRIP can serve as an established vehicle for that responsiveness..

3.1.1.	Federal Policy Considerations

Although the ERCOT market is not FERC jurisdictional, federal policy nonetheless can impact the ERCOT grid.   in concert with ERCOT transmission policies numerous large in the span of 4 years

3.1.1.1	Federal Tax Policy

Federal tax policy has perhaps been the most significant single driver for the installation of renewable generation technologies in the past two decades.  Since the passage of the federal Production Tax Credit (PTC) in the Energy Policy Act of 1992, installations of wind have typically surged when the PTC is available.  Likewise, when the credit lapsed, wind farm development ground to a halt.  The PTC was extended through Dec. 31, 2012 by the American Recovery and Reinvestment Act (ARRA) of 2009.  It is anticipated that extended PTC availability during this time period will provide a continued incentive for wind farm development in ERCOT in high-capacity factor areas.

The availability of an Investment Tax Credit (ITC), which was also included in the ARRA and which may be converted to a cash grant, provides further momentum to the likely installation of a significant amount of both large-scale and distributed-scale wind and solar generation technologies in the near-term, possibly even in areas of the state with lower capacity factors since the ITC incentive is not production-based.

3.1.1.2	Federal Environmental and Energy Policy

Federal environmental and energy policy may also play a significant role in either encouraging the installation and use of renewable technologies through mechanisms such as a Renewable Portfolio Standard or limitations of emissions which discourage the use of certain conventional technologies, such as those with higher levels of carbon dioxide (CO2) emissions.  At the direction of the PUCT, ERCOT performed an analysis of possible impacts of proposed legislation to limit CO2 emissions and found that such a policy decision could have significant market and technical impacts on the ERCOT system.

3.1.2.	State Policy Considerations

The State of Texas exercises a high degree of jurisdictional control over most facets of the ERCOT network and markets and has consistently adopted policies to encourage the installation of renewable power generation technologies in ERCOT since the passage of the state’s first 2,000 MW renewable portfolio standard in 1999’s Senate Bill 7.  Additionally, ERCOT transmission policies which currently require load to pay for system upgrade costs have engendered significant interest by resource developers.  To add transparency to the costs borne by loads, the ERCOT System Planning Charter requires Transmission Owners to inform the market when individual interconnection costs exceed $25M.  , which the Region has significantly eclipsed.  For example, by the end of 2010 ERCOT will double the 2015 target and met the meet the 2025 target.

3.1.2.1.	Competitive Renewable Energy Zones

In 2005, the Texas legislature passed Senate Bill 20 which set a goal of 5,880 MW of total installed renewable generating capacity by January 1, 2015, and a target of 10,000 MW by January 1, 2025. The ERCOT Interconnection is very close to meeting the 10,000 MW installation goal, almost 15 years ahead of schedule. ERCOT Staff reported to the ERCOT BOD on April 20, 2010 that the current installed MW of wind was 9,117 MW as of March 31, 2010.  The 9117 MW does not include wind interconnected to SPP in the panhandle of Texas. Thus, it is likely that the total amount of wind already interconnected in Texas exceeds the target set by the Legislature.  The 2005 bill also required the PUCT to

- designate Competitive Renewable Energy Zones (CREZs) throughout the state based on renewable energy resources and developer commitments and

- develop a plan to construct the transmission capacity necessary to deliver this electricity from renewable energy resources to major load centers.

Both of the delegated requirements to the PUCT have been completed.  In PUCT Docket  No. 33672, the Commission designated five geographic areas as CREZs including two in the Texas panhandle, an area normally served by the Southwest Power Pool (SPP).  To interconnect the designated CREZs to the ERCOT system, the Commission also selected ERCOT's "Scenario 2" transmission plan which called for the construction of 2,334 miles of new transmission designed to serve 18,456 MW of wind generation.  The Commission found that certain transmission lines were critical in relieving current transmission congestion in areas with existing wind generation and ordered that those "priority" lines be constructed first.  Certain Transmission Service Providers (TSPs) were ordered to fully implement the CREZ Plan by Dec. 31, 2012.  It is anticipated that the vast majority of “CREZ generators” will be large-scale wind units.

|  | , including design of required Ancillary Service Markets and reliability reuqirements, online and unconstrained as of 12/31/2013. |
| --- | --- |

| Goal 10 | Ensure the ERCOT operations function is prepared for the operating conditions resulting from the significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. |
| --- | --- |

large

3.1.3.	Policy Issues Raised by Integration of Renewable Technologies

It should be noted that the widespread introduction of new technologies often raises policy issues which may or may not be suitable to be addressed by the ERCOT stakeholder process.  The TAC and the RTWG strive to find a balance in such issue discussions.

3.2.	System Reliability Considerations

The primary mission of the ERCOT Independent System Operator is to maintain the reliability of the ERCOT bulk power system at all times through appropriate system planning and operations practices.  The widespread introduction of variable generation technologies, technologies which directly interact with variable generation technologies, and other technologies which directly impact system planning and operations functions in similar fashion as variable generation technologies cause impacts situations which can ERCOT planners and operators.  RTWG strives to identify and discuss these situations.

| Goal 12 | Identify and capture the potential economic impacts and reliability challenges associated with renewable generation technologies and related applications and practices. |
| --- | --- |

3.2.1.	System Planning Considerations

The ERCOT system planning function entails a wide array of activities essential to system security.  The rapidity with which new power generation and load management technologies have been introduced to the system and, in particular, the significant penetration of variable generation technologies creates numerous system planning complications which must be addressed to enable prudent and effective system planning.  Transmission planning challenges related to widespread integration of renewable generation technologies has consumed and continues to consume significant and disproportionate ERCOT transmission planning resources.  Significant, multi-month transmission planning activities devoted largely if not exclusively to integration of renewable generation include development of the $5 billion CREZ transmission plan, analysis and development of a reactive resource plan associated with the $5 billion CREZ transmission plan, analysis of subsynchronous resonance effects of wind generation resources on series capacitive devices (a significant offshoot of the CREZ reactive resource plan), and on-going analysis of low voltage ride-through capability.  Meanwhile, significant ERCOT transmission planning resources are needed for other activities, including resources necessary to modify transmission system modeling practices as part of ERCOT’s nodal implementation plan.

Recommendation 02:  Given the significant and disproportionate amount of transmission planning resources devoted to integration of renewable generation, ERCOT stakeholders should limit the scope and breadth of additional study and modeling proposals to ensure prudent and appropriately prioritized use of transmission planning resources.

3.2.1.1.	Quality of Data and Models

In many respects, ERCOT’s ability to effectively integrate renewable technologies has been hampered by the poor quality of critical information.  Significantthe information relevant to renewable technologies hasis not been consistently provided to ERCOT or TSPs.  Additionally, there is some uncertainty as to the accuracy or completeness of renewable generation technology capability specifications and operations models under a variety of system conditions.

| Goal 13 | Improve the quality of data and accuracy of models used to support the ERCOT system planning function. |
| --- | --- |

| Recommendation 03 | As integration issues are examined, data required for ERCOT and Transmission Owner modeling should be considered and, where possible, improved. Renewable generators should improve ERCOT’s access to quality technical data for all generation technologies, including renewable technologies. |
| --- | --- |

.

3.2.1.4.	System Planning Studies

System planning studies are used to identify areas of near-term and long-term concern and devise and test possible solutions.  In recent years, ERCOT has been required to update assumptions and devise new studies to address the array of issues presented by renewable technologies.  As these technologies continue to evolve and as new technologies enter the market, additional studies may be necessary to ensure reliability.  However, if such additional studies are significant, then the consumption of transmission planning resources necessary to address renewable generation integration issues would become even more disproportionate than is already the caseperformed.  As the market is dynamic and changing, long term system planning studies pose particular challenges with ERCOT’s manpower availability and budget constraints as first considerations.

3.2.1.5.	ERCOT Planning Resources

The ERCOT system planning function is a shared function between the ISO and stakeholders, primarily TSPs.  Much of the regular system planning work is performed by TSPs through the working groups of the ROS and the Regional Planning Group (RPG) under ERCOT supervision.  As ERCOT’s capabilities have increased in recent years, the ISO has assumed a more direct role in system planning activities.  ERCOT system planning resources are still stretched thin to the point that concerns about “study horsepower” have entered the stakeholder lexicon.  Additionally, there is concern about how ERCOT system planning recommendations affect the energy only market design and the overarching goal of balancing system reliability and market needs.

| Goal 14 | Assess and prioritize ERCOT system planning resources in light of the disproportionate use of planning resources devoted to renewable integration issues and other transmission planning resource needs. within ERCOT’s established budgetary constraints.. |
| --- | --- |

| Recommendation 04 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements and priorities for the ISO’s system planning resources to ensure such resources are sufficient and are devoted to the highest priority needs. |
| --- | --- |

3.2.2.	System Operations Considerations

As challenging as variable generation technologies can be for system planning, the task of effectively and efficiently integrating renewable technologies in Real Time system operations is the primary focus of near-term TRIP activities.  The ERCOT system must become more flexible to manage greater inherent variability in generation, load, and net load with an evolving mix of available resources for operational purposes. to the extent allowed by man-machine interface constraints and ERCOT’s budgetary model allows.  The operational decisions made by ERCOT have tremendous impact on system security and the effectiveness of the wholesale market, Real Time and near-term market economics, and long-term market health and sustainability.   It is essential ERCOT be able to posture the system in the Day Ahead and Real Time to mitigate the uncertainty which can accompany high levels of renewable generation penetration.

3.2.2.1.	Quality of Data, Models, and Systems

Just as quality data and models are essential to conduct meaningful system planning activities, system operations must be informed by accurate information from operators of renewable resources that reflect resource availability and technical capabilities.  Where integration issues identify areas of concern or areas for improvement in the data available to system operators, such issues must be timely addressed by renewable generators.

3.2.2.2.	Dispatchable Resources

Maintenance of system security requires ERCOT to dispatch generation resources up and down to follow load and manage transmission system congestion.  L as well as maintain scheduled frequency and voltage profiles.  .  Inherentimitations in the dispatchability of many renewable generation technologies pose several challenges, particularly during conditions in which high renewable energy production is concurrent with low system load and the number and variety of dispatchable generation units may be limited.  ERCOT and stakeholders continue to examine whether existing resources are sufficiently dispatchable and in situations where limited dispatchability poses potential system issues, ERCOT may need to procure additional ancillary services to counterbalance this limited range of dispatchable energy.

3.2.2.3.	Generation Ramping Capabilities and Limitations

The geographical concentration ofconcentrated wind farms in West Texas has subjected the ERCOT network to “ramping events.”  These events are” characterized by rapid, steep increases or decreases in the energy output of multiple renewable generation facilities.  ERCOT must have sufficient dispatchable generation available to address the variability of renewable energy output.  Moreover, the available resources must also be technically capable of meeting the steep ramping needs of the system.  Since combined cycle gas units are typically on the margin in ERCOT.  As these units are displaced by renewable energy production, this concern is being followed closely by market participants. The displacement of this flexible and fast ramping generation precisely when renewable energy production occurs requires continued monitoring to ensure that appropriate ramping capability remains available to ERCOT operations.

The challenge is somewhat unidirectional in nature.  VERs can be constrained in upward response to increasing wind velocity and luminance (solar?) but the withdrawal of “fuel” (wind/sunlight) present a change that may only be offset by storage capability in the future.  Existing resources can generally display and provide normal and emergency ramp rates.  This factor may lead stakeholders to initiatives that might include a tiered ramping service in the form of Regulation Service that recognizes the premium value of faster ramping capability, which also implies more wear and tear on conventional thermal resources.

| Goal 15 | Ensure particular attention is paid to ramping events, including taking steps to mitigate ramp event impacts, improve ramp event forecasting and pre-event system posturing, and devising more effective and/or efficient use of market and operational tools during ramp events. |
| --- | --- |

3.2.2.4.	Frequency Control

The ERCOT ISO is required by NERC standards to maintain system frequency within a specified range and to quickly restore system frequency when deviations occur.  Moreover, .  ERCOT Protocols 5.9.1.1 requires:  “All Generation Resources that have capacity available to either increase output or decrease output in Real Time must provide Primary Frequency Response.” Thus, there is an expectation that all resources will support grid reliability. However,  renewable generation technologies impact system frequency control differently than do conventional resources.  This provides opportunities and challenges to the system.  There is concern that frequency control issues may increase as renewable technology penetration increases. Certain time periods may lack sufficient spinning mass from synchronously connected generators to maintain the system inertia.  Spinning mass can mitigate frequency decline providing time for spinning reserves to ramp sufficiently to arrest the frequency decline.  ERCOT is monitoring the impact  .  Stakeholders will have to be particularly mindful of the relative loss of system inertia as the operational penetration of renewable technologies increases and is evaluating the potential need for further market constructs such as new ancillary services or different amounts of the existing servicessystem’s inertial requirements in low load periods in shoulder months.  VER vendors may develop effective solid state analogs to ensure that sufficient the inertial response needed in the system, but absent the widespread availability of that capability it may be necessary for the ISO to commit out of merit the spinning mass remains available at all times.  ERCOT may require additional Ancillary Services to ensure that sufficient ramp rate equivalent to it.  The current settlement of out of merit machines to provide such a service are inadequate and will only lead to further distortion of market pricing and hamper long term generation adequacy if stakeholders do not execute a change in paradigm in regard to reliability services and response as well as spinning mass is available to meet system security at all timestheir premium values.

| Goal 16 | Identify and address current and anticipated challenges to the maintenance of system frequency control. |
| --- | --- |

3.2.2.5.	Ancillary Services

ERCOT procures ancillary services to provide key system reliability functions.  Capacity, energy, and other services from participating generation and load resources are procured to enable the system to maintain frequency and ride through or recover from recordabledisturbances and capacity shortage conditions.  Large amounts of variable energy output can change the scope, frequency, and duration of ancillary services deployments and have a corresponding impact on the kinds and amounts of ancillary services needed for reliable system operations.

ERCOT continues to review ancillary services-related issues.  This effort began with a study performed by General Electric as part of the PUCT’s CREZ designation process.  The General Electric Study evaluated the likely need for additional Regulation Service to manage wind variability at high penetration levels and suggested that ERCOT explore the possibility of adding a 10-minute Non-Spinning Reserve Service (NSRS).  During 2008 and 2009, ERCOT revised its ancillary services procurement methodology, modifying the amount of NSRS procured and increasing the number of hours during which NSRS is procured.  ERCOT also developed a mechanism to increase the procurement of additional Regulation Service if system control performance falls below a predetermined limit.  ERCOT is presently reviewing the requirements for 2011. Some market participants are supporting evaluation of revisions to the definitions of Ancillary Services to ensure that the required ramp response is available on the systems at all times to ensure reliability.

As discussed in greater detail below, it is anticipated the Texas Nodal Market conversion will necessitate a further evaluation of the necessity and adequacy of the various ancillary services.  The ancillary services procurement methodology will be reviewed and updated in the future as ERCOT gains experience with nodal market operations and increased levels of renewable energy generation.

| Goal 17 | Develop a near-term process by which the range of issues associated with the kinds of ancillary services available to the ERCOT market and the procurement methodologies for those services are evaluated and, if necessary, adjusted, to facilitate the integration of renewable generation technologies. |
| --- | --- |

3.2.2.6.	Voltage Control

A number of issues relating to voltage control practices emerged from Wind Workshop I and were escalated as critical issues resolve early in the TRIP development process.    ERCOT Stakeholders and ultimately the ERCOT Board of Directors exhaustively examined and vetted these issues in the process of approving PRR 830, which has been appealed by renewable generators to the Public Utility Commission.for resolution early in the TRIP process.  VER   ERCOT Protocols Section 6.5.7 requires all Generation Resources greater than 20 MVA (or units connected at the same point of interconnection with an aggregate amount greater than 20 MVA) to provide Voltage Support Service to the grid. Such Generation Resources must maintain a Voltage Profile established by ERCOT at the point of interconnection.

|  | . Determine if market based local procurement of voltage support can be an adjunct approach to maintaining voltage supply where existing and new VERs are present. |
| --- | --- |

3.2.2.7.	Renewable Generation Forecasting

A complicating factor of renewable variable generation technologies on system operations is the uncertain nature of energy output at any given point in time.  As wind penetration increased, variability in resource forecasts provided to ERCOT was addressed by ERCOT developing its own wind forecast.  This lessenedlessen ERCOT’s dependence of individual wind farm forecasts.  ERCOT forecasts expected load and then subtracts expected wind generation from this number.  This forecast is called the “net load” forecast. ERCOT uses the net load forecast for purposes of operational planning. that thisimprove the accuracy of forecasting intermittent resources

Stakeholderstakeholder activities in the forecasting area has resulted in the acceleration to accelerateof nodal market renewable generation forecasting tools ahead of completeof nodal market implementation.  An additional area of near-term focus has been the development of forecasting tools specifically focused on wind ramping events as better situational awareness can mitigate the more significant system reliability challenges posed by such events.

| Goal 19 | Evaluate renewable generation forecasting practices and outcomes. Identify areas of possible improvement and develop solutions. |
| --- | --- |

3.2.2.8.	ERCOT Operations Resources

As the number of significant variables impact system operations.  These variables are increased increases with increasing renewable technologytechnologies penetration. , ERCOT operators may require enhancedenhance situational awareness to adequately and manage system variability.  As the primary users of thesethis new information and tools, ERCOT operators assistinvolved in the development of these products and must be trained in their use.  These development and training activities are in addition to the operators’ core operational duties.  In addition to the human resource impacts of this operational evolution, the financial and technical challenges to hardware and software development must be recognized and addressed. Stakeholders must continually undertake analysis to ensure that the increase of complexity from changing system requirements do not sacrifice the Region’s reliability requirements nor its reasonable and acceptable budgetary constraints.  The Region may at some point be forced to execute a cost-benefit analysis to ensure that  the addition of more low cost VER more than offsets the increase in system complexity, software and hardware O&M, and the resulting increases in consumers’ funding of the ERCOT administrative fee.

| Goal 20 | Assess ERCOT operations capabilities in light of activities required to effectively integrate renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Where operational capabilities are improved, ensure adequate training is performed to maximize benefits. |
| --- | --- |

| Recommendation 04 | The ERCOT Board should focus on the requirements and priorities for the ISO’s system operations resources to ensure such resources are sufficient and are devoted to the highest priority needs ensure that budgets . |
| --- | --- |

3.3.	Technical Considerations

One consequence of the introduction of competitive markets and open access transmission networks in North America is the surge in research and development of grid-connected technologies across the planning and operations spectrum – demand management technologies, distribution system devices, retail products and services, transmission system equipment, and generation and storage technologies.  But while many emerging technologies provide new benefits to the grid, they can also introduce new challenges. and incremental costs.  In many respects, the industry is moving away from the economies of scale of large generationhistoric technologies which provide the full range of grid functionality and toward a more complex system of numerous technologies providing more specialized functionality and, therefore, requiring higher degrees of coordination and integration.

3.3.1.	Technical Capabilities and Integration Challenges

Some renewable technologies, such as biomass-fueled generators, offer many of the technical capabilities of conventional generation resources familiar to system planners and operators while other renewable technologies are fundamentally distinct from the turbine technologies of the past four decades which comprise the majority of resources on the system.  As renewable technologies mature, additional capabilities have been developed to provide grid services and facilitate network integration.  For example, early wind turbines essentially operate in an on or off mode – they have limited operational flexibility, very simple control systems (if any), and are often incapable of providing functionality common to other technologies such as the ability to control unit ramp rate control or to provide primary frequency response.  Newer wind turbines and control systems are equipped with greater functionality and can offer more system support services.

reliable  on both the resources themselves and on the part of the ISO employed.

| Goal 21 | Improve and maintain stakeholder technical understanding of the capabilities and limitations of relevant emerging and evolving grid-connected technologies; their potential benefits and challenges for the system planning and operations functions; and facilitate collaborative stakeholder communications to solve technical integration issues. |
| --- | --- |

3.3.2.	Technical Approach to Renewable Technologies

ERCOT maintains technical requirements and standards for generation resources regardless of the generation technology type. in support of system reliability requirements that remain relatively static due to NERC Reliability Standards..  In other instances, ERCOT market rules recognize the technical limitations of various generation technologies through technology-specific standards which respect the limitations of different equipment types.  This is why many specific rules have been developed over the years applicable to specific resource types– nuclear, hydro, combined cycle, wind, and others.  Generally, to ensure non-discriminatory open access, ERCOT rules are technology neutral except in circumstances where good cause exceptions may be in the public interest which fit compatibly with system reliability requirements, which always trump other considerations.

Presently, there are few, if any, technology-specific market rules and technical standards for several of the emerging technologies which can reasonably be expected to connect to the ERCOT system in the near term such as Concentrating Solar Power (CSP), solar photovoltaic (PV), or various energy storage devices such as batteries or flywheels.  In some areas, the technical issues raised by these newer technologies are similar to those identified for wind resources, such as the lack of contribution to system inertia.  In other areas, these newer technologies may present issues not yet confronted by ERCOT planners or operators, such as the near-instantaneous ramping capability of certain solid-state storage technologies.  However, the RTWG has entertained presentations from several developers of solar and storage resources and few if any barriers to entry have been identified that would prohibit the interconnection of such resources at this time.

A key philosophical issue regarding technical requirements and standards for emerging technologies is whether it is appropriate to modify existing technical requirements that are based on years of reliable system operation to accommodate the unique characteristics of certain technologies or whether maintenance of the non-discriminatory, technology neutral technical standards developed over time to ensure system reliability in a fair and equitable manner to all market participants barriers such standards may create should be maintained.  To   .  System reliability and the extent that good cause exceptions to non-discriminatory requirements potentially harm consumers or other market participants, such impacts will haveof the NERC Reliability Standards in place should always trump in the effort to integrate the various VERs because in the final analysis consumer power quality and security and stability of the network are of paramount importance to be dealt with in some wayinvestments in assets aside from the emerging technologies needs.

| Goal 22 | Strike an appropriate balance which maintains an open access paradigm allowing and encouraging non-discriminatory introduction and integration of beneficialbeneficial technological advances while maintaining interconnection, registration, planning, and operating criteria which protect system security in a fair and equitable manner to consumers and other market participants. |
| --- | --- |

|  | Standards should be clearly defined and enforced. New should be applied prospectivelycreate |
| --- | --- |

for useplannersmust be more robust in their ability to   Additionally, while planning studies are important to identify potential system reliability needs, it is important to remember that the ERCOT market relies on competitive developers to take the risk to build generation.  As a result, the interconnection and the ISO do not engage in “integrated resource planning.”

3.3.4.	Technical Challenges to System Operations

Similar to the system planning function, system operations requirerequires accurate ofinformation about equipment technical specifications.  ERCOT operators also require streams of Real Time information and near-Real Time forecasts to effectively and efficiently position the system to manage significant production from variable generation technologies.

| Goal 25 | Focus on near-term refinement and development of tools providing enhanced operational capabilities for ERCOT management of wind-related issues. In the longer term, evaluate potential tools needed to integrate other renewable technologies as operational issues are identified with an eye to the cost-benefit ratio achieved for the entire system in an overall sense.. |
| --- | --- |

3.3.5.	Technical Education and Institutional Knowledge

As technical knowledge is gained and incorporated into ERCOT market rules, systems, and processes, it is important that knowledge be documented and institutionalized to facilitate industry access to current technical information.  TRIP Goals 01, 05, 06, 13, 21 and 23 address this consideration.

3.4.	Market Design Considerations

Marketmarket design should be used to ensurefrom system reliability to the extent possible in competitive wholesale markets.  ERCOT market participants have limited ability to address many market design issues as they are bound by policy decisions made by legislative and regulatory bodies.  As market design and reliability issues are identified, they are communicated towith policy makers.  Where stakeholders can address market design, a fundamental goal of the market rules process is to align market design elements and incentives with desired market and reliability outcomes.

3.4.1.	Principles of ERCOT market design

In the search for renewable technology integration solutions, certain principals or core elements of the ERCOT market design must be respected as they are required by jurisdictional entities such as the open access network requirement set by the Texas Legislature or the energy-only market design ordered by the PUCT.  Other market design characteristics such as unit dispatch procedures, credit requirements, or settlement formulas are subject to extensive deliberation and modification through the stakeholder process.

3.4.2.	Impacts of Renewable Technologies on ERCOT Markets

At current penetration levels, renewable technologies have already alteredalter ERCOT market outcomes creating downward pressure on energy prices,, the need for ERCOT to procure additional capacity services, and have impacted ERCOT system dispatch actions.  Market impacts have both near-term and/or long-term consequences for overall market efficiency and sustainability, including for example, long term resource adequacy.

.

| Goal 26 | Identify renewable technologies integration market design questions and impacts on market outcomes. Facilitate issues framing for resolution, if desired, by the appropriate stakeholder or policy making body. |
| --- | --- |

3.4.3.	Market Design Approach for Renewable Technologies

There are multiple possible approaches to framing and addressing the market design issues arising from the introduction of new technologies.  New products or services may be defined to facilitate market entry or qualifications for market participation may be modified to accommodate different technical parameters.  On the other hand, the presumption when examining new technologies may be that no modifications are needed to the market design element in question and that new technologies should meet existing qualification or performance criteria in order to participate in the market.  For example, a new generation technology may be able to offer something like the presently defined Regulation Service but may provide the service faster or cheaper but may not meet the qualifications to provide the service as it is currently defined.  However, the ERCOT system may not need a faster Regulation Service, or the market costs of changing systems to utilize a faster Regulation Service may outweigh the potential benefits of such a service.

| Goal 27 | Examine the potential development of market products and/or market design elements which maximize the value to ERCOT consumers of new technologies. |
| --- | --- |

| Recommendation 06 | None at this time. |
| --- | --- |

3.5.	Performance Criteria and Compliance Metrics

All resources are required to comply with the ERCOT Protcols and Operating Guides.

3.5.1.	Principles of Performance Criteria and Compliance Metrics

Compliance is assessed and determined by the Texas Regional Entity, ERCOT or the PUCT as required.

3.5.2.	Application of Performance Criteria to Renewable Technologies

Where appropriate and useful, the TRIP identifies performance criteria and/or compliance metrics for renewable technologies to accomplish one or more of the following purposes:

- inform renewablerenewable technologies manufacturers and project developers of the technical capabilities required for units interconnected to the ERCOT system;

- set uniform performance expectations appropriate for each renewable technology;

- provide data to inform the renewable technologies integration process;

- provide data to gauge the success of renewable technologies integration efforts; and

- provide clear, enforceable measurements to ensure compliance with performance criteria.

.

3.5.3.	Application of Performance Data to Renewable Technologies Integration

Text.

3.6.	Cost Allocation

Text.

3.6.1.	Principles of Cost Allocation

Text.

3.6.2.	Cost Allocation Task Forces

Text.

3.6.3.	Application of Cost Allocation Principles to Renewable Technologies

Text.

3.7.	Texas Nodal Market Implementation

Text.

3.7.1.	Renewable Technologies Integration Benefits of the Texas Nodal Market

Text.

3.7.2.	Addressing Renewables Technologies Issues in Nodal Testing and Start Up

Text.

3.7.3.	Texas Nodal Market Implementation Schedule and Resource Requirements

Text.

3.7.4.	Post-TNMID Evaluation of Wind Operations Issues

Text.

3.7.5.	Nodal Parking Deck

Text.

4.	Key Issues and Strategies for Resolution

4.1.	System Planning Issues

| SP-01 Verify Wind Turbine Technical Data: Wind turbines of various vintages in the ERCOT system possess different technical capabilities. Generally speaking, newer turbine types offer more technically advanced features and control systems than older technologies. It is unclear whether models for wind units provided to ERCOT by wind generators are sufficiently accurate or detailed for system planning and operations purposes. ERCOT has assisted this effort through questionnaires sent to wind generators. |  |
| --- | --- |
| Priority | High. |
| Considerations | Policy: Significant policy impacts. Data quality impacts ERCOT studies and recommendations. |
|  | Reliability: Accurate technical data for use in system planning and operations models is critical to ensuring system reliability. |
|  | Technical: Accurate representation of WGR design, configuration, and technical capabilities and limitations are required inputs for various planning and operation functions. The Resource Asset Registration Form (RARF) for each WGR should reflect all relevant data. |
|  | Market: Significant market impacts. Data quality impacts ERCOT studies reliability assessments. |
|  | Performance/Compliance: No performance criteria are recommended. No compliance metrics are recommended. |
|  | Cost Allocation: There are no costs to allocate. WGRs are responsible for submitting timely, accurate data to ERCOT through the RARF process. |
|  | used |
|  | Rwas sufficiently [what is the status of the follow up?] |

| SP-02 Wind Turbine Computer Models: Computer models used in operations and planning have not always been able to represent all wind-turbine technologies accurately. There are several factors affecting the accuracy of the modeling effort. One is the mutual lack of familiarity and understanding between modelers and WGRs owners leading to misunderstanding of requirements. Another factor is the rapid growth in the WGR capacity making an orderly response to the new technologies’ characteristics difficult. Lastly, there is the rapidly evolving nature of the WGR technology itself, which makes it difficult to keep models current. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This is a key reliability issue. Proper models are needed to accurately perform planning, design, and operational studies. While a variety of approximations are used for all technologies, the degree of approximation for WGRs has seemed excessive. [What is the basis for this assertion? Specific about what characteristics are desired and where the shortfalls are would be helpful.] |
|  | Technical: The modeling issue is partly the result of technical deficiencies in the computer software used to perform the Voltage Ride Through, Subsynchronous Resonance, and other studies. In addition, those designing the software and running the studies have limited experience with WGRs and may require additional education and training. major technical issue for the whole industry is the need to create non proprietary standard models for the many different WGR turbine types. |
|  | Market: Indirectly, lack of confidence in the models used for studies can result in unneeded conservatism on the part of system planners which can increase the cost of facility designs and on the part of system operators which can increase the cost of market operations or lead to inefficient commitment of Resources. |
|  | Performance/Compliance: It is incumbent upon WGRs to provide accurate technical data to TSPs and ERCOT. Existing NERC standards and ERCOT Protocols define responsibilities and time frames. |
|  | Cost Allocation: Entire market absorbs cost of inefficiencies arising from modeling that is not as robust as it could be. WGRs operators absorb costs of providing their data to ERCOT. |
| Strategy | Near-term focus is to identify discrepancies between installed equipment and how that equipment is represented in studies. Two key areas should be addressed – lack of common understanding regarding technical specifications of equipment in the field and the technical capabilities and limitations of the modeling software itself. Recommendation XX: Increase ERCOT and market participant education regarding renewable generation technology and associated modeling issues. Recommendation XX: Encourage stakeholder participation in WGR model improvement efforts in the industry, such as the Electric Power Research Institute (EPRI) Project 17. Recommendation XX: Require WGRs to provide accurate models of their equipment. |
| Activities |  |
|  | MP XX: WGRs need to work with equipment suppliers to insure that the vendors provide complete, detailed, and accurate technical data for their equipment as needed to support all required studies. WGRs must update entities that need their technical data promptly and completely as their plans and actual facilities change. |
| Follow-Up | Insure that the Voltage Ride Through findings relative to WGR modeling needs as well as the modeling data itself is captured and documented. Initiate revisions to procedures and Protocols to establish a common data collection system and data base for all generators with appropriate modifications to ensure that ERCOT documentation of the actual characteristics of each facility’s technology. |
| Schedule | Wind Workshop One, March 17, 2008 Wind Workshop Two, August 22, 2008 Wind Workshop Three, June 26, 2009 Wind Workshop Four; ERCOT requirements and Vendor solutions; July 2010 Voltage Ride Through Study phase 2; WGR data and model verification; June 2010 Data Repository; modify data collection and establish data base; after nodal go live |

| SP-03 Wind Turbine Fault Tolerance: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. As more WGRs were added to the ERCOT system, it became necessary to evaluate WGR fault tolerance capabilities as well as to establish fault tolerance standards for new WGRs. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Yes—not requiring VRT from renewable facilities created inequity on the grid between those resources and other resources on the grid. |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. However, existing WGRs may not be easily modified to meet new fault tolerance . In most cases, new WGRs can meet fault tolerance requirement by buying certain options in the wind-powered turbines. In most cases, those options cannot be retrofit onto existing wind-powered turbines; [is this a technical or a financial limitation?] thus, the actual ability to meet new requirements may provide a significant technical challenge. |
|  | Market: New requirements would cause certain wind-powered turbines to no longer be able to be supplied for WGRs in ERCOT. However, other interconnections require fault ride through capability and this is not anticipated to create supply disruption on a wide scale. There will not typically be any significant change in operating costs for new WGRs. There is little expected change in the competitive landscape for new WGRs that comply with new fault tolerance standards. For existing WGRs the possible expense of retrofitting existing equipment could be significant. Compliance by the WGR may require the addition of dynamic reactive devices in the WGR substation. The expense could cause some WGRs to be retired rather than be upgraded. For all WGRs there is likely to be both increased capital cost and operating cost as a result of complying with new standards. There are also commercial issues with inability to control single source prices and with warranty terms and conditions as well as warranty cost. These technical, cost, and commercial issues raise compliance with new standards by existing generators to a policy level. See SP-08 for additional details pertaining to existing WGRs. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: There is no cost allocation issues associated with new WGRs, costs will be borne by the new WGR. For existing WGRs see the discussion for SP-08. |
| Strategy | Establish new requirements for new WGRs that balance WGR capabilities and transmission system design requirements. For existing WGRs, evaluate need. Recommendation. Adopt an Operating Guide Revision Request establishing new standards for WGR Voltage Ride Through to provide WGR fault tolerance capability. Perform detailed studies using well groomed data to evaluate exiting WGRs capability to ride through system faults. |
| Activities | ERCOT (E X): Participate in the process of establishing new standards. Specify scope and contract for studies to evaluate the need for system design changes related to faults affecting existing WGRs. |
|  | Market Participants (MP X): TSPs, generators and all market participants actively participate in the development of new standards for WGRs. |
| Follow-Up | Codify new standards in protocols (see SO-12). Require needed studies for existing WGRs to be completed by a specific date (see SP-08). |
| Schedule | 11/17/2008 Operating Guide Revision Request 208 approved establishing new Voltage Ride Through standards for WGRs (see SO-12). Studies for existing WGRs are underway with results required by June 2010 (see SP-08). |

| SP-04 Voltage Transient and Small Signal Stability Study: The West-to-North Transfer study is performed annually by ERCOT Operations, with input from ERCOT Planning and review by the Dynamics Working Group. The purpose is to calculate how much power can safely be transferred from West to North while maintaining a safe small signal stability margin. The DWG assembles the dynamic data set necessary for ERCOT staff to do the study. |  |
| --- | --- |
| Priority | Medium or Medium-High |
| Considerations | Policy: Yes. Thousands of MW of turbines that are susceptible to Subsynchronous Resonance (SSR) are interconnected to the ERCOT Grid. The issue was not identified until late November 2009 when an SSR issue was experienced on the grid. There is a policy question of whether additional standards should be required for interconnection of this type of machine. |
|  | Reliability: Yes. The results of the study inform ERCOT Operations how much transfer they can allow reliably in the real time operation. Without this information they must operate more conservatively to maintain the system reliability. |
|  | Technical: The technical challenge is to allow as much power transfer as possible without risking a system separation due to the undesired system oscillation. The solution is to do the study every year and limit the west to north power transfer based on small signal stability criteria. |
|  | Market: The market consideration is to maximize the wind-to-load transfer based on security constraints. |
|  | Performance/Compliance: Each renewable generation resource owner must provide good dynamic models. ‘Good’ in this context means (1) compatible with the version of software being used, and (2) accurately describing the electrical characteristics of the equipment. Re-using old models for old facilities is not always good enough. |
|  | Cost Allocation: None |
| Strategy | Recommendation. WGRs will provide good dynamic models to ERCOT to create the dynamic data set. |
| Activities |  |
|  | Market Participants: TSPs – Maintain database of dynamic models of all transmission and generation facilities. Provide to DWG when requested. Insist on adequate generator models from developers before allowing energization. Resource Owners – Provide complete dynamic model of generator and provide to TSP and ERCOT staff. |

| SP-05 Impact of Wind Turbines on System Inertia: Determine the potential impact on system reliability of large amounts of wind turbine generating capacity on ERCOT’s system inertia requirements. This is the second of two entries on this topic. The first one was SO-08 which was resolved in October 2008 by a PDCWG (Performance, Disturbance, Compliance Working Group) presentation to ROS. SP-05 is looking to the future problem of maintaining system frequency as installed wind power capacity approaches the system minimum load. |  |
| --- | --- |
| Priority | MediumHigh |
| Considerations | Policy: This is an issue where performance deficiency would negatively impact consumers, other market participants, or both. Setting aside financial considerations to mitigate such negative consequences, there are technical limitations upon other resource owners to maintain ERCOT frequency fluctuations associated with intermittent resources, particularly if a lower percentage of such other resources are dispatched as a larger percentage of renewable generation is connected and dispatched. |
|  | Reliability: The reliability concern is that wind plants do not automatically respond to frequency deviations in the same way synchronous generators do. As the proportion of synchronous generation decreases, maintaining frequency will require more operator action, or additional under-frequency load-shed relay settings, or in real-time reaction by the operators at the Frequency Desk Statement regarding the key issue to stabilize system frequency. |
|  | Technical: The technical challenge is how to operate the grid reliably with fewer synchronous generators available to respond automatically to frequency deviations. |
|  | Market Design: There is a long-term question whether units which provide spinning mass or stabilize system frequency will continue to be installed in the ERCOT system and whether such units will be able to remain online during periods of high wind production and correspondingly low prices. Additionally, a new Ancillary Service that provides quick ramp response to the grid during frequency deviations may be required. |
|  | Performance/Compliance: ERCOT: NERC CPS1 and DCS criteria and Balancing Authority ACE limit QSEs with synchronous generators: Correct SCE bias settings Wind-only QSEs: None now |
|  | Cost Allocation: To be determined. |
| Strategy | ERCOT Planning staff will study the problem. Recommendation: The recommendations will not be known until the study has been done. |
| Activities | ERCOT: ERCOT Planning staff will study the problem. ERCOT Operations to evaluate whether a targeted fast ramping AS would aid operators in more reliably integrating WGRs. |
|  | Market Participants: Work with ERCOT to develop fast ramping AS that will support system security and frequency response. |
| Follow-Up | This will be a periodically recurring study as the percentage of wind as compared to all ERCOT generation increases. |
| Schedule | ERCOT already provided data to NERC. When the NERC study is completed it will inform ERCOT’s study. ERCOT staff will start this study when the VRT study is done (June 2010). |
| SP-06 Use of Variable Frequency Transformers to Solve Stability Problems: Text. |  |
| Priority | Text. |
| Considerations | Policy: Text. |
|  | Reliability: Text. |
|  | Technical: Text. |
|  | Market Design: Text. |
|  | Performance/Compliance: Text. |
|  | Cost Allocation: Text. |
| Strategy | Text. Recommendation X: Text. |
| Activities | ERCOT (XX): Text. |
|  | Market Participants (MP XX): Text. |
| Follow-Up | Text. |
| Schedule | Text. |
| Status | Text. |

| SP-07 Voltage Control Process: This issue has been raised in recognition of the fact that the West Texas / Panhandle will have many different transmission providers serving a large concentration of wind-powered generation. Voltage has been coordinated by Resources, TSPs, and ERCOT in response to daily load and generation variations. Transmission Service Providers (TSPs) have designed, installed, and operated some reactive devices for their systems. Historically ERCOT has conducted seasonal studies to establish required voltage profiles at the point of generator interconnection. Then the Transmission Service Providers (TSPs) manage the day to day and hour to hour variations by calling on Generators to increase or decrease output to maintain their voltage profiles. However, such day to day interaction has not typically been the case for WGRs operators. Moreover, many WGRs were interconnected without sufficient study as to their voltage impacts on the system when they are offline and not generating. The eight TSPs involved in the CREZ projects must coordinate voltage control expectations. One TSPs voltage control efforts could have a large impact on anther TSP’s facilities and on other generators. The large concentration of wind-power served by eight different TSPs requires a detailed and coordinated design effort and operating strategy. Thus this issue has both a planning and operations component. |  |
| --- | --- |
| Priority | High for the design component |
| Considerations | Policy: Significant |
|  | Reliability: Voltage control is a key reliability issue. The coordinated reactive design effort will determine a holistic solution. |
|  | Technical: Currently available technology will provide the needed reactive components. |
|  | Market: Potentially. If WGRs are not providing reactive capability, other generators will be asked to make up the difference creating inequities in expectation about generator performance across different types of generators and imposing opportunity costs on one class of generators asked to make up the difference while simultaneously providing benefit to the other types of generators not required to meet the standard. Could potentially be ameliorated by development of a VAR compensation Ancillary Service. |
|  | Performance/Compliance: Existing performance and compliance should be adequate to direct the design effort. However, it is not clear that the existing Protocol requirements have been consistently applied to all interconnecting entities. |
|  | Cost Allocation: ERCOT Protocols 6.5.7.1 requires generators to maintain a set voltage profile. All costs of complying with the required voltage profile fall to the generator. |
| Strategy | Recommendation. Initiate a reactive design study involving all TSPs in West Texas / Panhandle coordinated by ERCOT. Develop a VAR Ancillary Service to allow resources that do not have the capability to comply with the Protocols to “provide services in kind” by buying from the market or bilaterally. |
| Activities | ERCOT (E X): ERCOT assist in developing a study scope and procuring study resources. |
|  | Market Participants (MP X): Develop a VAR Ancillary Service to allow resources that do not have the capability to comply with the Protocols to “provide services in kind” by buying from the market or bilaterally. TSPs actively participate in developing the study scope, providing data, funding, managing the study and implementing the study design requirements. |
| Follow-Up | Normal planning, design, and certification processes provide the needed follow up procedures for the design effort. Additional work is needed by ROS and WMS to define the new Ancillary Service. Additional follow up is needed for the operations component of this issue (see SO-10) |
| Schedule | The reactive design study is currently underway. May 2010 – reactive device requirements portion of the study completed. 2010-2013 TSPs specify, purchase, and install needed reactive devices. |

| SP-08 Voltage Ride-Through (VRT) Study: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. As more WGRs were added to the ERCOT system, a process was initiated to establish fault tolerance standards for new WGRs. The process was expanded to include a study of system needs for existing WGRs during fault conditions. SP-03 identifies the VRT issue for WGRs. The issue was divided into two parts for follow through; SO-12 dealing with establishing new standards for new WGRs and SP-08 dealing with studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Yes. The rest of the United States has a specific requirement for VRT in FERC 661-A. ERCOT was not subject to this requirement because it was not FERC jurisdictional. The question of how existing and new equipment in ERCOT should be treated is an issue that is not yet resolved. |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. The studies needed to evaluate fault tolerance of existing WGRs require extremely detailed modeling of the WGRs. The software and data needed are generally available but the technical challenge results from the volume of data needed from many different organizations. Consistency in interpreting the data needs of the software and fidelity of the representation will require intense, centralized data review efforts. In some cases, existing WGRs are not easily modified to meet new fault tolerance requirements. In most cases, new WGRs can meet fault tolerance requirement by buying certain options in the wind-powered turbine equipment. In most cases, options available for new resources cannot be retrofit onto existing wind-powered turbines; thus, the ability of existing resources to meet new requirements may provide significant technical challenges. |
|  | Market: For existing WGRs the possible expense of retrofitting existing equipment could be significant. Compliance may require the addition of very expensive dynamic reactive devices in the WGR substation to make up for the lack of capability of the generation equipment itself. The expense could cause some WGRs to be retired rather than be upgraded. For all WGRs could be increased capital cost and operating cost as a result of complying with new standards. There are also commercial issues with inability to control single source prices and with warranty terms and conditions as well as warranty cost. These technical, cost, and commercial issues raise compliance with new standards by existing generators to a policy level. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: The cost of any new equipment to resolve any issues associated with existing WGRs must be determined from the results of the VRT study. The study results may indicate that equipment changes at some WGRs will resolve any system problems for all WGRs. Transmission system changes might provide the needed solution to any problems. If this is the case, there may be questions from loads about whether they should pay for this equipment. The study results are thus needed to identify cost allocation issues, if any. |
| Strategy | For existing WGRs, evaluate need for any VRT related design changes. Recommendation. Perform detailed studies using validated data to evaluate exiting WGR capability to ride through system faults. The study scope shall include detailed modeling. A major effort to collect consistent and correct detailed data needs to be a part of the study effort. |
| Activities | ERCOT (E X): Specify scope and contract for studies to evaluate the need for system design changes related to faults affecting existing WGRs. Provide staff to oversee the study. |
|  | Market Participants (MP X): Respond to ERCOT/contractor data requests to support study efforts. WGRs gather needed detailed data from vendors and cooperate with ERCOT in insuring consistency and fidelity of the modeling. |
| Follow-Up | ERCOT manage the study effort. Study results need to be communicated to market participants. The Regional Planning Group and the Reliability and Operations Subcommittee must review the study results and establish required equipment changes. A follow up protocol revision may be required to designate the parties required to implement the required equipment changes. |
| Schedule | Studies for existing WGRs are due by June 2010. Study results should be reviewed by October 2010 with any follow up protocol revisions initiated in November 2010. |

|  | Could be If appropriate and complete data are not available to ERCOT, ERCOT’s studies are necessarily impacted. |
| --- | --- |
|  | for ERCOT potentially include |
|  | Market: : Could be a market issue. If appropriate and complete data are not available to ERCOT, ERCOT’s studies are necessarily impacted. Thus, operational information is not as complete as it could be and this could potentially lead to out of market actions to resolve unanticipated issues. |

| SP-10 DOE Long-Term Planning Study: Text. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: As part of the study effort, all participants must be mindful of existing PUCT policy regarding the energy only market and transmission cost of service. |
|  | Reliability: ERCOT shall evaluate reliability outcomes in the scenarios studied. |
|  | Technical: |
|  | Market Design: The ERCOT Study should include, for each scenario, the expected “peaker net margin” benchmark for the ERCOT Energy Only market. This will help to ensure that potential transmission solutions are developed with an eye toward supporting a robust energy – only market. |
|  | Performance/Compliance: Text. |
|  | Cost Allocation: ERCOT Admin fee supplemented with Federal Department of Energy (DOE) funding. |
| Strategy | Text. Recommendation X: Ensure that scenarios are vetted through ROS and WMS. |
| Activities | ERCOT (XX): Text. |
|  | Market Participants (MP XX): Participate in scenario development. |
| Follow-Up | Text. |
| Schedule | Text. |
| Status | Text. |

4.2.	System Operations Issues

| SO-01 Inventory of Wind Generation Facilities: As wind-power was added to the ERCOT system it became apparent that there were inconstancies in the communications and understanding between WGRs, ERCOT, and Transmission Service Providers. ERCOT launched a number of initiatives to address the communication and interpretation inconsistencies. The Inventory of Wind Generation Facilities was initiated by ERCOT to insure that ERCOT and the WGRs were communicating correctly about voltage control capability, reactive devices, and operating procedures. ERCOT staff engaged in an effort to contact each WGR in writing and by phone to answer specific questions about the WGR’s voltage control equipment and procedures. Written responses from the WGRs were all followed up with site visits and/or phone calls by ERCOT staff to insure there was a common understanding and interpretation of the questions and responses. The inventory process led to many follow up initiatives including changes in data collection forms and procedures (SP-01, SP-02, SP-09), workshops (WT-02, WT-05), and better coordination with Transmission Service Providers (TSPs)(SO-15). The actual inventory has been completed but follow up activities are still ongoing; thus this issue remains open. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: Yes. Inconsistent understanding led to existing disputes about various Protocol requirements –for example those around requirement to supply reactive power. |
|  | Reliability: Consistent interpretation of requirements and communications is fundamental to reliable operations. The lack of familiarity with ERCOT by the new WGRs and the lack of familiarity with wind-power by ERCOT and TSPs can result in miscommunication. |
|  | Technical: No |
|  | Market: Yes. ERCOT Protocols anticipate that interconnected resources provide similar types of services to the grid. When it is identified that differences in the ability to provide various services exists it creates opportunities for market solutions. Without market solutions to these issues, if some providers are unable to provide specific services, it could result in impacts to other providers who may be called upon to make up the difference. Without appropriate compensation to the entities called to provide the additional services cross subsidization occurs. Cross subsidies unfairly advantage some while requiring action on the part of another. To the extent possible, cross subsidies should be avoided to ensure that market incentives ensure the desired outcomes. |
|  | Performance/Compliance: No new compliance considerations, but better understanding and communications will result in a higher standard of compliance. |
|  | Cost Allocation: No |
| Strategy | The basic issue that was identified was the need for more communication and common understanding of ERCOT requirements and WGR characteristics. Recommendation: Develop a common understanding of ERCOT requirements and procedures and WGR equipment characteristics through direct verbal communication between ERCOT and WGRs. |
| Activities | ERCOT (E X): Directly communicate in person or by phone with each WGR to establish a common understanding of the WGRs chacteristics. |
|  | Market Participants (MP X): WGRs proactively communicate with ERCOT to insure information is understood. |
| Follow-Up | SP-01 Verify Wind Turbine Technical Data SP-02 Wind Turbine Computer Models SP-09 Wind Turbine Model Validation WT-02 and WT-05 Wind-power Workshops SO-15 Communications Between Wind Farms and TSPs |
| Schedule | The inventory process is complete. Follow up activity is ongoing (see respective issues) A project to create a common generator data base for use by ERCOT planning, ERCOT operations, ERCOT dispatch software, and TSPs is scheduled to start soon after the Nodal go live date. |

Comment--SO-02 is nearly the same as the Planning one. Recommend combining them in the Planning section or copying changes I proposed in planning section into this one.  Duplication makes document less user friendly than it might otherwise be.

| SO-02 Wind Turbine Computer Models: Computer models used in operations and planning have not always been able to represent all wind-turbine technologies accurately. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This is a key reliability issue. Proper models are needed to accurately perform operational studies. While a variety of approximations are used for all technologies, the degree of approximation for WGRs has seemed excessive (what is the basis for this assertion?). |
|  | Technical: The modeling issue is partly the result of technical deficiencies in the computer software used to perform the needed studies. In addition, those designing the software and running the studies have limited experience with WGRs and require additional education and training. One major technical issue for the whole industry is the need to create non proprietary standard models for the many different WGR turbine types. |
|  | Market: Indirectly, lack of confidence in the models used for studies can result in unneeded conservatism which increases the cost of designs and operations. |
|  | Performance/Compliance: It is incumbent upon the WGRs to provide accurate technical data to Transmission Service Providers and to ERCOT in a timely way. There are existing NERC standards AND ERCOT Protocols that define that responsibility and required time frames. |
|  | Cost Allocation: No |
| Strategy | The focus needs to be on identifying disconnects between equipment on the ground and the representation in studies. There are two main aspects to be addressed; lack of understanding leading to miscommunication, and the technical capability of the software. Recommendation. Increase education of all parties about the technology and the modeling issues. Add resources to ERCOT planning staff to address all study related issues. Lead and participate in industry wide WGR model improvement efforts. |
| Activities | ERCOT (E X): Hold workshops for Market Participants and ERCOT staff to allow WGRs, equipment vendors, Transmission Service Providers, and ERCOT to present their information and issues to each other. Take advantage of study efforts to verify WGR data, to develop more appropriate models, and to initiate software changes. ERCOT and the Transmission Service Providers need to rework all forms and modeling processes to be appropriate for WGRs and use a common database for all studies. |
|  | Market Participants (MP X): WGRs need to work with equipment suppliers to insure that the vendors provide complete, detailed, and accurate technical data for their equipment as needed to support all required studies. WGRs must update those that need their technical data promptly and completely as their plans and actual facilities change. |
| Follow-Up | Insure that the Voltage Ride Through findings relative to WGR modeling needs as well as the modeling data itself is captured and documented. Initiate revisions to procedures and Protocols to establish a common data collection system and data base for all generators with appropriate modifications to insure there is clear documentation of the actual characteristics of each technology’s facilities. |
| Schedule | Wind Workshop One; Title; Date Wind Workshop Two; Title; Date Wind Workshop Three; Title; Date Wind Workshop Four; ERCOT requirements and Vendor solutions; July 2010 Voltage Ride Through Study phase 2; WGR data and model verification; June 2010 Data Repository; modify data collection and establish data base; after nodal go live |

| SO-03 : Wind-powered Generation Response to Down Balancing Instructions It is difficult for ERCOT to determine compliance with a Down Balancing instruction because there is confusion about whether the instruction is based off of real time output level or the Resource Plan value. This problem is a result of the zonal market design and specific software limitations that do not exist in the nodal market. A process has been completed requiring all WGRs to update their resource plan every hour and to use the best forecast available. AWS TrueWind provides a forecast to ERCOT for use in operations. At the present time, some WGRs have forecasting methods with good track records which are better than the ERCOT/AWST forecast for their facility. During this transition process (how long is the transition supposed to last?), the WGR is allowed to use its own forecast unless the ERCOT forecast is better (who determines ‘better’ and what is the basis for the determination?). Thus the new procedures will improve ERCOT’s ability to calculate the effect of their down balancing instructions in the zonal market without the need for substantial zonal software changes. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: Every 15 minutes ERCOT operations calculates a Balancing Energy Offset amount to account for the differences between what the software thinks WGRs are doing and what they are actually doing. Extreme errors in calculating the offset can lead to reliability issues, but this happens rarely. |
|  | Technical: There is no real technical issue. Existing processes appear adequate for the present time. The nodal software completely resolves this issue. |
|  | Market: Market impacts arise from inaccurate forecasts and from the offset process. Effectively Balancing Energy and Regulation Ancillary Service makes up the differences between forecast and actual output. In special circumstances, out of merit instructions are employed by ERCOT to mitigate potential reliability issues. ERCOT can also deploy Responsive Reserve and NonSpin if conditions warrant. |
|  | Performance/Compliance: This new process imposes new requirements on WGRs. The requirements are clear and enforceable. |
|  | Cost Allocation: No cost allocation issues. |
| Strategy | Develop a workable solution and wait for the nodal market for the full resolution of the issue. Recommendation : Require all WGRs to update their resource plan every hour using the best available forecast. |
| Activities | ERCOT (E X): Monitor the accuracy of WGR forecasts as needed. |
|  | Market Participants (MP X): WGRs change procedures to insure hourly updates and to insure that the most accurate forecast is being used. |
| Follow-Up | None |
| Schedule | 9/15/2009 Protocol Revision Request 812 was approved |
| SO-04 – Smart Grid Implications for Renewable Resources – Determine how development of a "smart grid" might benefit and improve integration of renewable resources into the ERCOT grid. Specifically, determine if there are new technical capabilities associated with electronic metering and monitoring systems that would allow higher penetration of renewable resources, particularly at the customer (i.e., distribution) level. |  |
| Priority | Low |
| Considerations | Policy: This issue might involve policy considerations depending on the type and level of “smart grid” deployment. |
|  | Reliability: This issue involves reliability considerations, particularly if it encourages deployment of additional renewable resources at or near a customer’s premises. |
|  | Technical: This issue involves the technical feasibility considerations associated with deployment of a “smart grid” and its associated hardware and software. |
|  | Market Design: This issue impacts market design because as the penetration of renewables and smart technologies change the composition of the market changes. This could lead to changes in market design, including changes to the structure of the Ancillary Service markets. |
|  | Performance/Compliance: This issue includes performance or compliance considerations, particularly if new generation resources are connected at the distribution level. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Examine hardware and software capabilities of electronic metering equipment and other electronically-controlled devices associated with a “smart grid” deployment to determine if they will benefit integration of additional renewable generation resources, particularly at the distribution voltage level. |
| Activities | ERCOT (XX): Assist market participants in the preparation of a whitepaper examining the various technologies associated with deployment of “smart grid” technology in ERCOT. |
|  | Market Participants (MP XX): Prepare a whitepaper examining the various technologies associated with deployment of a “smart grid” and assess the capability of such technologies to improve or enhance integration of additional renewable generation technologies. |
| Follow-Up | If the concepts presented in the final whitepaper gain market acceptance, then individual market participants should follow-up with appropriate changes in the ERCOT Protocols and/or Operating Guides to facilitate the deployment of “smart grid” technology in the ERCOT market. |
| Schedule | Topics for whitepaper are under discussion at RTWG; a draft whitepaper should be available for review by the end of 2010. |
| SO-05 Operational Studies Related to Wind-powered Generation: This issue is essentially a follow up to the GE Ancillary Services study. ERCOT now has a growing data base of actual wind-power operations at a significant level of penetration. Using that data base, a new study should use actual data rather than assumed data to evaluate the need for new ancillary services or procedures. Key areas for further study might include evaluation of actual WGR ramping history, and evaluation of low load high wind-power scenarios. The objective of the study is to further refine operational tools as we increase WGR installed capacity above 15,000 MW. |  |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: As additional wind-power is added to ERCOT, there may be new and unfamiliar operating situations. Anticipating and studying those situations can prepare ERCOT staff to handle the situations reliably. |
|  | Technical: There may be some issues in how WGRs can provide reliability services. |
|  | Market: There could be a large market impact if operational needs are not investigated ahead of time to determine the most effective methods of ensuring system reliability. |
|  | Performance/Compliance: There may be new operational requirements or new services that are defined which need follow up to establish Performance/Compliance requirements. |
|  | Cost Allocation: No |
| Strategy | ERCOT has initiated a variety of much needed studies having to do with stability, voltage control, ancillary services, and voltage ride through. It is critical that ERCOT continue to anticipate and study future operational issues in order to avoid entering an unfamiliar operating situation unprepared. Recommendation: Perform an update of the ancillary service study using actual WGR data with an emphasis on fleshing out any operational procedure and resource changes that may be needed. |
| Activities | ERCOT (E X): ERCOT needs to lead the effort to determine the study scope and acquire the study resources. |
|  | Market Participants (MP X): All market participants should assist in determining the study scope. |
| Follow-Up | The results of the study will dictate any follow up that is needed. Possible outcomes include new procedures, mechanisms for WGRs to provide regulation, or modifications to ancillary service market design. |
| Schedule | The need for this update is not immediate. Operational data from the Nodal market may be required for a meaningful study. The updated study and some of the follow up should be completed before 2013 at which time it can be anticipated that WGR capacity will exceed 15,000 MW. |

|  | Policy: This issue impacts all interconnected resources. Resources that provide reactive capability are not compensated for provision of this service. Thus, resources that do not provide this service may be experiencing benefit from not having to provide the service. |
| --- | --- |
|  | impacts An VAR Ancillary Service should be designed so that entities that cannot meet the existing requirements can buy the service through markets operated at ERCOT or from the bilateral market. |
|  | includes bothand. |
|  | Potentially |
|  | and Ancillary Service constructs and Ancillary Services |
|  | Develop summary of reactive ancillary services from other markets. Provide draft proposal for consideration by ERCOT stakeholders. |
|  | Required. |

| SO-07 Wind Generation and High System Frequency: Wind turbines in ERCOT do not provide primary frequency control through “governor-like” mechanisms . Energy production from wind generation can impact system frequency during periods of increasing wind speeds, in particular during periods when frequency exceeds 60 Hertz. This issue seeks to address the types of controls and/or requirements available or necessary for wind turbines to provide the required governor-like response during periods of high system frequency. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue has broad impacts across all resources and the market. |
|  | Reliability: This issue addresses maintaining adequate system reliability during periods when system frequency is higher than normal. |
|  | Technical: Some types of wind turbines can provide primary frequency response, others cannot. This issue assesses possible alternative methods available to provide primary frequency response. |
|  | Market: Is primary frequency response better provided by imposing technical requirements on WGRs or by devising a market mechanism to provide the service? |
|  | Performance/Compliance: Performance criteria are to be specified in the PRR / NPRR. Compliance will be done on a spot-check (event-driven) basis. |
|  | Cost Allocation: If primary frequency response capability is required of WGRs, each WGRs will bear the cost of such capability. |
| Strategy | Recommendation X: Develop a Protocol Revision Request to require wind generator control systems to be programmed to respond to frequency deviations by controlling WGR real power output in a way that is similar to governor response for conventional steam generators. Develop fast ramping Ancillary Service that would act to ramp down to offset wind output. |
| Activities | ERCOT (E X): None |
|  | Market Participants (MP X): The Wind Operations Task Force of the ERCOT Reliability and Operations Subcommittee (ROS) developed a Protocol Revision Request (PRR) 824 – Primary Frequency Response to add a requirement for wind generator control systems to be programmed to respond to frequency deviations by controlling WGR real power output in a way that is similar to governor response for conventional steam generators. This PRR was approved by the ERCOT Board of Directors in December, 2009 and it applies to new wind generators with Standard Generation Interconnection Agreements signed after January 1, 2010. Another PRR, PRR 833 – Primary Frequency Response from Existing WGRs is currently under review in the ERCOT PRR process. |
| Follow-Up | It is expected that normal and ongoing PDCWG review of system frequency disturbances will reveal if there is still a concern regarding the adequacy of primary frequency response on the ERCOT system. |
| Schedule | PRR 833 is tabled at TAC. |

| SO-08 Impact of Wind Turbines on System Inertia: Determine the potential impact on system interia and develop possible solutions. This is the first of two entries on this topic. The other one is SP-05 which will be done by ERCOT Planning staff after the VRT study is done (June 2010). SO-08 was resolved in October 2008 by a PDCWG (Performance, Disturbance, Compliance Working Group) presentation to ROS. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: No policy considerations |
|  | Reliability: The reliability concern is that wind plants do not automatically respond to frequency deviations in the same way synchronous generators do. As the proportion of synchronous generation decreases, maintaining frequency may require more operator action. |
|  | Technical: The technical challenge is how to operate the grid reliably with fewer synchronous generators available to respond automatically to frequency deviations. |
|  | Market Design: The challenge is to ensure the appropriate mix of Resources is available in Real Time to respond to frequency variations and that market rules reflect proper compensation for those services out of merit that represent premium “must have” unit committments. . |
|  | Performance/Compliance: ERCOT: NERC CPS1 and DCS criteria and Balancing Authority ACE limit QSEs with synchronous generators: Correct SCE and fleet bias settings Wind-only QSEs: Stakeholders must begin to examine analog sources of inertial response and/or market incentives to ensure that an adequate amount is available, particularly at low load periods, to protect the other resources on line from poor system power quality conditions. |
|  | Cost Allocation: None. |
| Strategy | PDCWG reported by to ROS in October 2008 without making a recommendation, which is not an indication of an exhaustive examination of the issue.. |
| Activities | ERCOT XX: ERCOT Operations staff to study the problem. |
|  | Market Participants: None |
| Follow-Up | This will be a recurring study for ERCOT Planning staff as the wind percentage of all ERCOT generation increases. Recommend that this issue be revisited as it has not been actively discussed for nearly two years. |
| Schedule | PDCWG reported by to ROS in October 2008. |

| SO-09 SCADA Control of Generator Circuit Breakers: Unlike conventional generation resources WGR technology and operating characteristics allow for considerable automation and operation from remote sites. As a result, there is often no staff at the WGR site. Transmission Service Provider (TSP) and ERCOT operators assume people are available on site to perform certain operations. The lack of onsite staff can be accommodated as long as the needed operations can be handled remotely. Not all WGRs have the same level of remote control and/or automation. A task force of TSP, ERCOT, and WGR operators was formed to identify the required operations and the standard for compliance. The task was expanded to include all generators since the newly specified requirements were appropriate for all technologies. This issue has been addressed and is now complete. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Limited impact on reliability but certain local situations could lead to out of tolerance operation if the issue were not addressed. |
|  | Technical: None |
|  | Market: Some increase in cost for WGRs. |
|  | Performance/Compliance: Clearly establishes uniform performance requirements. |
|  | Cost Allocation: None |
| Strategy | Specifying requirements that are generally assumed to be in place provides a clear and uniform compliance regime. Recommendation : Develop clear written specifications for operational needs heretofore simply assumed to be in place. |
| Activities | ERCOT (E X): Participate in establishing the operational requirements. |
|  | Market Participants (MP X): All market participants, but especially generators and TSPs participate with ERCOT to establish the requirements. |
| Follow-Up | None |
| Schedule | Operating Guide Revision Request 226 was approved December 2009 |

| SO-10 Voltage Control Process: This issue has been raised in recognition of the fact that the West Texas / Panhandle will have many different transmission providers serving a large concentration of wind-powered generation. Voltage has beencoordinated by Resources, TSPs, and ERCOT in response to daily load and generation variations. Transmission Service Providers (TSPs) have designed, installed, and operated some reactive devices for their systems. Historically, ERCOT has conducted seasonal studies to establish required voltage profiles at the point of generator interconnection. Then the Transmission Service Providers (TSPs) manage the day to day and hour to hour variations by calling on generators to increase or decrease output to maintain their voltage profiles. However, such day to day interaction has not typically been the case for WGRs operators. Moreover, many WGRs were interconnected without sufficient study as to their voltage impacts on the system when they are offline and not generating. The eight individual TSPs systems involved in the CREZ projects must coordinate voltage control expectations. One TSPs voltage control efforts could have a large impact on anther TSPs facilities and on other generators. The large concentration of wind-power served by eight different TSPs requires a detailed and coordinated design effort and operating strategy. Thus this issue has both a planning and operations component. |  |
| --- | --- |
| Priority | Medium for the operations component |
| Considerations | Policy: Significant. |
|  | Reliability: Voltage control is a key reliability issue. |
|  | Technical: Currently available technology will provide the needed reactive components. However new operating practices and requiring new coordination strategies may be needed. |
|  | Market: Potentially. If WGRs are not providing reactive capability, other generators will be asked to make up the difference creating inequities in expectation about generator performance across different types of generators and imposing opportunity costs on one class of generators asked to make up the difference while simultaneously providing benefit to the other types of generators not required to meet the standard. Could potentially be ameliorated by development of a VAR compensation Ancillary Service. |
|  | Performance/Compliance: Existing performance and compliance should be adequate unless radically different operating procedures are developed. However, it is not clear that the existing Protocol requirements have been consistently applied to all interconnecting entities. |
|  | Cost Allocation: ERCOT Protocols 6.5.7.1 requires generators to maintain a set voltage profile. All costs of complying with the required voltage profile fall to the generator. |
| Strategy | Recommendation. Include an operational analysis in the reactive design study to evaluate the level of coordination needed to respond to load and generation changes in West Texas / Panhandle. Evaluate the adequacy of current voltage control procedures and establish a VAR Ancillary Service similar to those provided for in other markets to ensure that the grid has sufficient reactive capability online at all times. |
| Activities | ERCOT (E X): ERCOT assist in developing a study scope and procuring study resources. Develop summary of VAR compensation methodologies in other markets (for example, PJM). ERCOT lead the effort to assess the adequacy of standard voltage control procedures when operating the CREZ system. |
|  | Market Participants (MP X): Assist ERCOT in developing summary of VAR compensation methodologies used in other markets. TSPs, generators, and all other market participants actively participate in the evaluation of voltage control procedures for the CREZ system. |
| Follow-Up | The Reliability and Operations Subcommittee needs to review ERCOT and TSP plans for voltage control of the CREZ system. WMS needs to create subgroup to develop information for ERCOT on the VAR services in place in other markets. |
| Schedule | The reactive design study is currently underway. Work still outstanding on summary of VAR Ancillary Services in other markets. June 2010 – reactive operational review portion of the study completed. June 2011 – ERCOT and TSPs establish any needed new procedures. |

Struck SO-11.

| SO-12 Low Voltage Ride Through (VRT) for Wind Generators: System reliability requires that during short circuit conditions (transmission system faults) that generators stay on line during the short circuit and after it clears. As more WGRs were added to the ERCOT system, a process to establish fault tolerance standards for new WGRs was initiated. This process has been completed. SP-03 identifies the VRT issue for WGRs. SP-08 looks at the Low Voltage Ride Through Study. The issue was divided into three parts for follow through; SO-12 deals with establishing new standards for new WGRs and SP-08 looks at studies related to existing WGRs. A portion of the discussion is repeated in these three issue write-ups to allow each to be complete. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Not for new WGRs. A policy issue did develop for existing WGRs (see Sp-03 and SP-08). |
|  | Reliability: The ability of generators to have a reasonable level of fault tolerance is critical to system reliability. During system fault conditions, voltages electrically close to the fault are depressed and generators may come off line if the depressed voltages last too long. The fault tolerance requirements can be met by designing the transmission system to clear faults quickly and by designing generators to remain on line for certain low voltage situations. WGR fault tolerance must be evaluated / designed to function for typical transmission fault clearing times. |
|  | Technical: There is no significant technical challenge to designing new WGRs to meet fault tolerance requirements. |
|  | Market: New requirements would cause certain wind-powered turbines to no longer be able to be supplied for WGRs in ERCOT. However, as these turbines are not likely to meet the standards already in place elsewhere in the United States this is not anticipated to create major issues. The provision of fault tolerance for new WGRs from other wind-power turbine suppliers will increase WGR capital costs when compared with the turbines that do not perform this service. However, as the rest of the United States already has requirements for low voltage ride through, this is not a new issue. There will not typically be any significant change in operating costs for new WGRs. There is little expected change in the competitive landscape for new WGRs that comply with new fault tolerance standards. |
|  | Performance/Compliance: New standards will require routine compliance requirements. |
|  | Cost Allocation: There is no cost allocation issues associated with new WGRs, costs will be borne by the new WGR. |
| Strategy | Establish new requirements for new WGRs that balance WGR capabilities and transmission system design requirements. Recommendation. Adopt an Operating Guide Revision Request establishing new standards for WGR Voltage Ride Through to provide WGR fault tolerance capability. |
| Activities | ERCOT (E X): Participate in the process of establishing new standards. |
|  | Market Participants (MP X): TSPs, generators and all market participants actively participate in the development of new standards for WGRs. |
| Follow-Up | None |
| Schedule | 11/17/2008 Operating Guide Revision Request 208 approved establishing new Voltage Ride Through standards for WGRs (see SO-12). |

| SO-13 Performance Metrics for Wind Generation: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-14 Impact of Transmission Outage Planning on Wind-powered Generation: Transmission outages can affect all generators at one time or another. In ERCOT, it is common practice of TSPs to schedule outages in the spring and the fall so as to avoid high load seasons. This period is when WGRs produce much of their power. Concentrating outages at these times increases the potential market impact on WGRs. Discussions were initiated in the Regional Planning Group to address these two issues. The basic idea is to provide TSPs sufficient information to know when extra ordinary measures to mitigate market impacts are warranted. ERCOT staff did an excellent job of bringing forward possible methods of including market impacts when considering transmission outage scheduling issues. It was noted that the software needed to estimate market impacts was part of the nodal package. These discussions resulted in the identification of additional transmission issues that needed attention (SO-20, SO-29, SO-31, and SO-34). The discussions also focused on CRR study assumption stability. Despite significant discussion, no progress has been made on identifying market impacts that justify mitigation. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: Yes, there are a number of policy issues raised in the discussion that most likely need to be addressed to allow the issue to be resolved. Is it appropriate to consider such a construct solely for a certain class of generators? Will TSPs be allowed to recover the cost of extra ordinary mitigation efforts? What will be the standard of accuracy required of the market impact estimation process? |
|  | Reliability: This is primarily an efficiency issue and properly done, there are no reliability impacts. There is some fear that once the market cost of transmission outages is known there will be pressure on TSPs to defer maintenance or delay inspections. |
|  | Technical: Market impact estimation processes exist but increasing the accuracy could be a challenge. Mitigation measures do exist but developing better ways to work on energized facilities and doing more predictive maintenance may require new technology. |
|  | Market: This is a major market issue. Transmission outages have always had a huge impact on production costs. |
|  | Performance/Compliance: There could be new performance requirements for TOs and compliance measures to implement any change in transmission outage scheduling. |
|  | Cost Allocation: There may be ways to identify generation resources that would benefit from the mitigation and assign the cost of mitigation to them. This would raise many issues since identifying what level of mitigation is “normal” will be subjective. |
| Strategy | Now that TSPs and generators are unbundled it seems appropriate to determine the effects of transmission operations on the market. (How would this work for entities that are not unbundled—like the munis?) Recommendation: Resolve policy issues prior to taking action. |
| Activities | ERCOT (E X): |
|  | Market Participants (MP X): TSPs need to identify policy and regulatory roadblocks to their ability to use transmission outage market cost information as a basis for extraordinary mitigation efforts. |
| Follow-Up | This issue needs routine follow up by the Regional Planning Group (RPG) after nodal go live. |
| Schedule | The RPG should discuss preliminary results of market cost calculations in March 2011. |

| SO-15 Communication Between Wind-power Ranches and Transmission Service Providers (TSPs): The newness of the WGR technology and the lack of familiarity with ERCOT and TSP procedures have led to multiple communication issues. A portion of the needed resolution focused on more complete and clear written requirements (see SO-09). In addition, a key component was familiarizing all parties with the procedures and issues of the other parties. A series of management level meetings between TSPs and WGRs developed strategies to increase communication effectiveness. The result was a series of workshops and proactive efforts to become more familiar with WGRs were another way to address the lack of knowledge. As an example one TSP, ONCOR, sent all of their transmission operators to WGR sites with specific learning objectives so that the TSP and WGR operators could improve their working relationship. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: Poor understanding of each other can lead to incorrect results when operating the ERCOT system. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Better understanding and working relationships can result in better performance. |
|  | Cost Allocation: None |
| Strategy | Continue with ERCOT's long history of face to face contact between various operating groups. Recommendation: Recognize that WGRs represent a new technology not familiar to electric system operators. Take proactive steps to remove barriers to effective communication. |
| Activities | ERCOT (E X): Schedule workshops to communicate specific information but to also provide an opportunity for contact between system operators and WGR operators. |
|  | Market Participants (MP X): WGRs proactively seek opportunities to understand TSP and ERCOT procedures and issues. Provide familiarization opportunities at WGR sites. |
| Follow-Up | None |
| Schedule | Immediate action has been taken and completed. |

| SO-16 Wind Generation Ramp Limits: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: All interconnected WGRs should provide ramping Control for ramping up and down upon instruction provided fuel source is available. |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-17 – Mid-Term and Short-Term Load Forecast Weather Sensitivity – Determine if sensitivity of the ERCOT mid-term and short-term weather forecasts were a major reason for the February 26, 2008 wind event that caused ERCOT to interrupt load due to a drop in system frequency resulting from a rapid reduction in wind generation while customer loads were rapidly increasing. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue does not involve policy considerations. |
|  | Reliability: This issue involves reliability considerations related to operation, voltage control, reactive capability, frequency response, and power production forecasting for wind generation resources. |
|  | Technical: This issue involves the technical capabilities of ERCOT to accurately forecast load and of WGR market participants to accurately forecast wind generation output. |
|  | Market Design: Ramping considerations have market impacts. ERCOT stakeholders should considering new Ancillary Services to create a fast ramping Ancillary Service as part of or in concert with a specific ancillary service to respond to frequency issues. |
|  | Performance/Compliance: This issue does include performance or compliance considerations applicable to all wind generation facilities regarding scheduling and operations. |
|  | Cost Allocation: Potentially if new AS is developed. |
| Strategy | Analyze the circumstances surrounding the February 26, 2008 wind event to determine if ERCOT’s weather forecast, which impacts both the load forecast and the wind generation output, was a contributing factor. |
| Activities | ERCOT (XX): Provide forecast and operational data related to the February 26, 2008 wind event to market participants. |
|  | Market Participants (MP XX): Analyze data provided by ERCOT related to the weather, load and wind production forecasts for the February 26, 2008 wind event and make any necessary recommendations for changes to prevent a reoccurrence. |
| Follow-Up | None necessary |
| Schedule | ISSUE COMPLETE: The Wind Operations Task Force (WOTF) analyzed data provided by ERCOT related to the February 26, 2008 wind event and determined that weather forecast sensitivity was not a major factor. The WOTF recommended to the ERCOT Reliability and Operations Subcommittee (ROS) that no changes were necessary and ROS concurred. |

| SO-18 Evaluate Transmission Line and Wind Power Production Outage Criteria: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-19 Improve Competitively Sensitive Constraint (CSC) Process: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-20 Dynamic Transmission Line Ratings: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-21 Evaluate Emergency Electric Curtailment Plan (EECP) Steps: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-22 Performance Metrics for Wind Generation: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-24 Settlement of Advanced Meters in the Nodal Market: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-25 Generator Governor Response for Wind-powered Generators: When system frequency deviates from the planned frequency of 60 Hz, then conventional, synchronous generators and loads automatically respond. If frequency goes up motors run faster so load goes up. When frequency goes up, all generators tend to reduce their output to bring frequency back down. Both of these automatic actions have the effect of reducing the high frequency and getting the system headed back to 60 Hz. The opposite occurs when frequency goes below 60 Hz. These automatic responses to frequency are called primary frequency response. Presently generators provide this service to the grid without compensation. However, as not all new generators provide the service, there is opportunity for these generators to provide this service by buying this Ancillary Service Product from ERCOT. Sufficient primary frequency response is needed to keep the ERCOT system stable, especially when generators or loads trip off suddenly. WGRs are not synchronously connected to the transmission system. There is no automatic response to frequency unless it is created artificially. For some WGR turbine technologies, there is no way to create a response to frequency at all (except tripping them off line). As the installed capacity of WGRs grows above 15,000 MW there will be many hours when a substantial amount of the generation on line will be WGRs. At these times, it will be efficient for WGRs to provide a portion of the needed primary frequency response or to purchase this service from an Ancillary Service Market conducted by ERCOT. If the WGRs do not provide the needed response, then WGRs may have their production curtailed to allow more conventional units to be on line or to increase their output in order to insure the response is available. A process has been completed to require all new WGRs to provide primary frequency response which culminated in the adoption of Protocol Revision Request 824. The newer technology WGRs can modify their control systems to provide what is expected to be excellent primary frequency response. On a going forward basis, the cost and commercial issues are quite manageable and no study is needed to justify the change in requirements. |  |
| --- | --- |
| Priority | High. |
| Considerations | Policy: No policy issue is raised on establishing a new requirement for new WGRs. An issue does arise if a new technical requirement is placed upon existing WGRs. However, it is consistent with market design principles to allow entities that do not provide specific services to purchase them through the market. |
|  | Reliability: Reliability could be an issue if sufficient frequency response is not available when needed |
|  | Technical: The newest WGR technologies can provide primary frequency response capability. Existing WGRs could provide a “service in kind” by procuring the needed volume of services from the ERCOT Ancillary Service Markets if a Primary Frequency Response Ancillary Service is developed. |
|  | Market: The development of new Ancillary Service Markets to meet reliability needs of the grid is an opportunity to demonstrates the close link between using market constructs to ensure reliability outcomes. |
|  | Performance/Compliance: New performance standards and compliance metrics will be required. |
|  | Cost Allocation: None, the costs will be borne by the WGRs. |
| Strategy | Maximize WGR production by providing needed system reliability services from WGRs when possible and by requiring WGRs to provide a service in kind by purchasing services from the competitive markets where available. Recommendation: Establish a new requirement for new WGRs to provide primary frequency response similar to conventional generator “governor response”. Develop proposal for new Frequency Response Ancillary Service. |
| Activities | ERCOT (E X): Participate in developing the new requirement and performance standards. |
|  | Market Participants (MP X): WGRs and all market participants assist in developing the new requirement and performance standards. Comply with the new standards as they are adopted. |
| Follow-Up | Monitor system performance and WGR performance to frequency deviations. |
| Schedule | December 2009 -Adopted Protocol revision 824 establishing new primary frequency response requirements for new WGRs Operating Guide revisions to establish performance requirements are in the approval process Protocol revision 833 establishing new primary frequency response requirements for existing WGRs is in the approval process. Work still to be done on design of new Frequency Response Ancillary Service. |

| SO-26 – Impact of Solar Generation on System Operations – Determine potential impact of new solar generation on ERCOT system operations and reliability through appropriate studies of solar ramp rate capabilities, forecasting of solar energy production, and voltage and reactive control capabilities of both solar photovoltaic and solar thermal technologies. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: This issue does not involve policy considerations. |
|  | Reliability: This issue does involve reliability considerations because of the potential impact of significant additions of solar PV and solar thermal generating resources on ERCOT system reliability and operations. |
|  | Technical: This issue involves technical considerations of two very different types of solar technology (PV and solar thermal) and their capability to provide necessary reliability services, such as voltage and frequency control, reactive control, ramp rates, etc. |
|  | Market Design: This issue could impact market design considerations since solar generation resources might be able to participate in ERCOT ancillary services markets. |
|  | Performance/Compliance: This issue does include performance or compliance considerations because of the inherent differences between solar PV, solar thermal and conventional generating technologies. |
|  | Cost Allocation: This issue does not directly involve cost allocation considerations. |
| Strategy | Develop a whitepaper to examine the capabilities and technical issues applicable to solar PV and solar thermal technologies. |
| Activities | ERCOT (XX): Assist market participants in the preparation of a whitepaper examining the various solar technologies and their potential impacts on ERCOT operations and reliability. |
|  | Market Participants (MP XX): Through the work of the RTWG, prepare a whitepaper examining the various solar technologies associated and assess the capability of such technologies to improve or enhance integration of additional renewable generation without compromising operations flexibility and system reliability. |
| Follow-Up | None necessary |
| Schedule | A draft whitepaper should be available for review by the end of 2010. |

| SO-27 Manual Curtailment of Wind Generation to Resolve Local Congestion: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-28 SPS actuation for N-0 Conditions: A SPS is a Special Protection Scheme which is an automatic system designed to trip a generator off line when needed to protect the transmission system. If an SPS is actuated for an N-0 condition that means it is tripping the generator off even though there has been no transmission contingency. This can occur when a new generator is connected to a transmission system that can handle some of its output all of the time and all of its output only some of the time. Since line flows are determined by more than that generator’s output, a SPS is employed to take the generator off line when the total flow, which the generator is not allowed to know, is reaching the transmission lines limit. The initial issue is that generation capability that the system could not fully support was interconnected to the grid. A secondary problem arose with coordinating ERCOT operations directions to the generator with the generators actions to avoid being tripped. The SPS warning signal, before the trip, was being used by the generator to cut production to avoid the trip. All parties agreed that this was appropriate; however it was unclear whether a complete SPS investigation and report to the Regional NERC Reliability Entity was needed when the warning signal activated but the SPS never tripped the unit. The investigation and reporting was a considerable burden on the Transmission Service Provider (TSP), ERCOT, and the Texas Reliability Entity (TRE). All parties agreed that the investigation and report were needed only if the SPS actually tripped the unit and the Operating Guides were modified to clarify the requirements. This issue affects WGRs almost exclusively since several WGRs have been connected to the transmission system ahead of the needed improvements. While this is normally a temporary situation, the design and construction of CREZ has become part of the solution for many of the WGRS. Other, timelier transmission upgrades are not being pursued since they would become redundant once CREZ construction is complete. The reporting issue has been resolved through procedural changes. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Fundamentally, this issue is associated with compliance procedures. |
|  | Cost Allocation: None |
| Strategy | Recommendation: Insure that there are no reliability issues associated with the N-) SPS operating procedures and modify the Operating Guides to clarify requirements. |
| Activities | ERCOT (E X): Assist in review and resolution of the issue. |
|  | Market Participants (MP X): Generators, TRE, and TSPs assist in review and resolution of the issue. |
| Follow-Up | None needed |
| Schedule | September 2009 Operating Guide Revision Request 224 clarifying SPS reporting requirements was approved |

| SO-29 Transmission Outage Planning for CREZ: This is a specific issue under the broader issue of transmission outage planning (see SO-14). This issue has been raised due to the fact there will be many transmission outages needed to construct the CREZ lines. CREZ construction outages are unique because of number of outages needed and the number of different entities involved in the construction. The issue is further exacerbated by the short time frame to complete all of the construction. No outages will be taken until construction which will be after regulatory approvals and designs are completed. The CREZ build out has a deadline of 2013. The front end time required and the quick build out will concentrate the bulk of the outages into 2011 and 2013. The outages are further concentrated by the practice of scheduling transmission outages only in the spring and fall months. These are the very times when WGRs are able to produce the most power. Originally market participants sought to have ERCOT provide the market impact of outages to the Transmission Service Providers (TSPs) in order to allow them to evaluate the need for extraordinary mitigation. One particular project was selected for such review, but any further market impact evaluation was put on hold pending the resolution of the general issue (SO-14). ERCOT Planning staff has identified the likely outages needed and they are very numerous. The focus now is to coordinate the outages needed by the various parties doing the construction. Normal procedures allow the TSPs to start scheduling their outages no sooner than 90 days after the granting of regulatory approval since the outages will be somewhat dependent on the specifics of the route. There is no practical way to get better information sooner, thus ERCOT must await scheduling information from the TSPs to start any coordination of the schedules. Altering procedures and beginning a coordination process with less than perfect information may be needed to insure that transmission construction is not delayed due to limitations on outages. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Is it appropriate for the TOs to be coordinating only a subset of outages that advantage or disadvantage only a single class of generators? How does this comport with open access policies? What is the burden of proof required for TSPs to allow extra ordinary mitigation costs to be recovered by the TSPs? |
|  | Reliability: Planned outage cannot be allowed to affect reliability. |
|  | Technical: There is no technical issue, |
|  | Market: The construction outages associated with CREZ will have a significant market impact. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Given the tight schedule and the limitations on available outage information the focus needs to be on coordinating outages in order to avoid construction delays. There does not seem to be any practical way to “optimize” the outages to reduce market impacts. |
| Activities | ERCOT (E X): Insure that staff and systems are available to coordinate CREZ transmission outages as information from the TSPs becomes available. Explore techniques for anticipating possible outage needs to identify possible conflicts ahead of time. |
|  | Market Participants (MP X): TSPs consider providing a planning estimate of the outages needed. |
| Follow-Up | ERCOT and the TSPs, together with other market participants, need to move forward on developing a mechanism for evaluating market impacts of transmission outages (SO-14) |
| Schedule | This is an ongoing issue until the completion of the CREZ construction. |

| SO-30 Application of Wind Generator Forecasts to PASA: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| SO-31 Tension Monitors on Transmission Lines: The rating of a transmission line, that is to say, the amount of current it can carry is very dependent upon the environmental conditions at the moment. Three major factors affect the current carrying capability: wind, ambient temperature, and sun. Many Transmission Service Providers (TSPs) vary their transmission line ratings used by ERCOT based upon temperature. Wind can have a much larger impact on line ratings than temperature. However, it is much more difficult to estimate line ratings for different wind conditions since the wind varies along the line due to topography and wind direction. One possible way to consider all the effects on the transmission line is to use real-time measurements on the condition of the line itself to determine how much current it can carry. Several vendors provide a way of measuring the tension on the line which is directly related to the cumulative effects of all environmental conditions along the length of the line and the current loading of the line. The vendor’s equipment then can provide the TSP with the instantaneous rating of the monitored section of the line. However, the effects of the environmental factors will not be captured by unmonitored lines, so the approach is not fool-proof. Two transmission lines in ERCOT are equipped with such devices. There is potentially a particular value for this technology when a WGR’s output is being limited by a nearby line. When the wind is strong enough for the WGR to increase its output it is very likely that the wind will also be cooling the nearby transmission line increasing its ability to handle the WGR’s increased output. However, the extent to which the WGR output correlates to cooling of the transmission line conductor depends upon the geographic prevalence of the amount of wind (is it windy across the entire length of the line, or just in the vicinity of the WGR) and the direction of the wind relative to the transmission line conductor (is the wind blowing across the conductor or is it blowing in parallel to the conductor). This second factor (direction of the wind relative to the conductor) can be different for different line sections as the transmission line turns or if the wind direction is variable. The purpose of this initiative is to have ERCOT and the TSPs consider using the tension monitoring technology when economically justified. Current planning processes do not specifically evaluate this solution to curtailment issues. The tension monitor system can be expensive to install and maintain and is not fool-proof. The equipment is not a standard part of a TSP’s inventory thus requiring special training and procedures. However the potential value in reduced production costs may justify overcoming these obstacles. |  |
| --- | --- |
| Priority | Low unless you are the WGR being curtailed |
| Considerations | Policy: What policy issues are raised by use of advanced technical equipment in some parts of the grid and not others? Are there policy issues around “grid equity”? The CREZ lines will be built with the latest technologies. How will generators situated in other parts of the grid be provided with similar access and optimization such as that potentially provided by tension monitors? |
|  | Reliability: The use of sophisticated specialized equipment can introduce additional complexity and uncertainty to system operations. |
|  | Technical: Tension monitors are available but increasing reliability of the devices and simplicity of operation may require additional development. |
|  | Market: This could have value to the market, but the policy implications of providing only a subset of the market with the advanced equipment is an open question. |
|  | Performance/Compliance: None |
|  | Cost Allocation: Potentially. It is possible that this equipment once installed would be rolled into Transmission Cost of Service. |
| Strategy | Recommendation: Identify policy issues raised by proposing advanced equipment for only part of the grid and raise in appropriate bodies. Identify WGRs that are being curtailed due to local transmission constraints and evaluate the possible value of using a tension monitor to increase the transmission line rating. |
| Activities | ERCOT (E X): Develop a screening process to identify possible candidates for use of tension monitors and submit Operating Guide Revision Request to document process. Evaluate candidates identified under the approved OGRR process. |
|  | Market Participants (MP X): ERCOT Planning will identify and prioritize candidate applications and work with TSPs to evaluate additional applications and work to resolve compliance responsibilities in the event that impacts to unmonitored line segments contributes to violation of vegetation management or other reliability and safety requirements. |
| Follow-Up |  |
| Schedule |  |

| SO-32 Real Time Wind-powered Generation Capacity: At certain times it will be necessary to estimate the potential output capability of WGRs when they are being curtailed. Experience using an estimation process that possibly includes the effects of wind velocity, direction, losses, and wind-powered turbine production efficiencies could be useful in developing the final estimation process needed. Estimating WGR output from wind measurements is not straight forward. The results are dependent upon many different factors and the experience in the industry is limited and inconsistent. Requiring all WGRs to estimate their output when not curtailed using the same process as would be used when curtailed allows the process to be compared with actual meter readings when curtailed. The comparison process will allow the WGRs to evaluate alternative algorithms and data sources in order to provide the best estimate. The process to require all WGRs to supply real time production potential telemetry has been completed. The data sent to ERCOT has some immediate, limited operational value in the Zonal system but is not needed in the nodal system. This is essentially a process to gain experience with estimating techniques and has little value once the techniques are perfected. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Providing a reasonable estimate of WGR potential capability when the WGR is curtailed is needed to allow ERCOT to reschedule the WGR when it is no longer curtailed. |
|  | Technical: There are many issues about measurement processes, averaging times, and data sources that need to be explored. |
|  | Market: None |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Develop a protocol revision requiring WGRs to telemeter an estimate of production potential to ERCOT using a consistent averaging time for the data. |
| Activities | ERCOT (E X): Develop procedures and systems to capture the new data and analyze as needed. |
|  | Market Participants (MP X): WGRs develop systems needed to telemeter the new estimate of production potential to ERCOT. Compare the estimates with meter readings and experiment with alternative data sources, averaging times and algorithms to develop the best estimate. |
| Follow-Up | Share experience of WGRs in developing reasonable estimation methods. |
| Schedule | January 2010 Protocol revision 811 requiring estimated Real Time Production Potential to be telemetered to ERCOT was adopted. |

| SO-33 Real Time Wind-powered Turbine Availability: WGRs are comprised of many, sometimes hundreds, of individual wind-powered turbines. At any given time some of the wind-powered turbines may be out of service on a planned or a forced outage basis. The maximum output of the WGR is dependent upon the available wind and the number of wind-powered turbines currently in operation. In addition, the reactive control capability of the WGR is dependent upon the number of wind-powered turbines in service. This initiative is intended to provide ERCOT with real time information about the actual number of wind-powered turbines available for service, out of service, and whose status is uncertain. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: Provides additional detail to improve modeling and thus will have some positive effect on reliability. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: New telemetry requirements will require additional compliance by WGRs with existing telemetry standards |
|  | Cost Allocation: None |
| Strategy | Recommendation: ERCOT develop needed protocol changes defining the new requirement. |
| Activities | ERCOT (E X): ERCOT develop needed protocol changes defining the new requirement. |
|  | Market Participants (MP X): WGRs comply with the new requirements. |
| Follow-Up | None |
| Schedule | November 2009 - Protocol Revision 830 establishing reactive standards and including wind-turbine availability telemetry requirements was adopted |

| SO-34 SCED Line Ratings: The Security Constrained Economic Dispatch (SCED) software determines the allowed output level of all generators in ERCOT respecting transmission line limits. The transmission line limits are provided by the Transmission Service Providers (TSPs) and in many cases are periodically modified based on expected temperatures. The temperatures used must be the highest temperature reasonably possible during the time period and for the region of the estimate. It is possible to provide actual temperatures in local geographic areas on a real-time basis. The use of the higher temperature estimate insures that the rating of the line will be conservative since a high temperature limits the current carrying capability of the line. If the more local real-time temperatures can be used to give SCED updated line ratings then it may be possible to increase the use of the transmission system reliably since a more realistic line rating will be used. Increased use of existing facilities is a benefit to all parties. Implementation in the new nodal software is possible but new procedures, monitoring systems, telemetry, and software will be needed. |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: This could impact production costs. |
|  | Performance/Compliance: Should require TSPs to publish line rating methodologies. |
|  | Cost Allocation: None |
| Strategy | Get the most out of existing transmission assets. Recommendation: Establish procedures and systems to allow TSPs to update line ratings near to real time and to publish rating methodologies so that differences in practices across TSPs can be identified. |
| Activities | ERCOT (E X): After nodal go live, commit resources to evaluate the cost and the schedule to implement real time updating of transmission line ratings. |
|  | Market Participants (MP X): TSPs assist in specifying procedures and systems to allow real-time updating of transmission line ratings and provide ERCOT with the necessary information to implement the system. |
| Follow-Up | Encourage ERCOT to require TSPs to share their ratings methodologies. Create NPRR if required. |
| Schedule | After nodal go live and no later than July 2011 have the scope, schedule, and cost of updating line ratings near real time defined. PRR and NPRR on ratings methodology could be developed now. |

4.3.	Market Design Issues

| MD-01 – Ancillary Services Cost Allocations Applicable to Wind: Many Market Participants as well as ERCOT Operations Staff (see John Dumas’ presentation to TAC on this issue at TAC’s 4/08/2010 regular monthly meeting) believe that integration of large amounts of variable wind generation have increased ERCOT’s need for certain Ancillary Services. These parties believe that such increased costs should be allocated to the party responsible for the increased need for Ancillary Services. This issue will evaluate alternative methods of cost allocations for Ancillary Services for possible application to Wind Generation Resources. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue examines the potential change in the existing ERCOT policy of assigning costs of Ancillary Services to loads (based on load ratio share) to allocate costs of Ancillary Service costs to all components of the system Net Load summation. |
|  | Reliability: This issue does not directly impact system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market Design: Presently AS costs are borne by loads. Changes to this construct would impact market design. Additionally, it may be cost effective for entities to provide “services in kind” by purchasing and supplying services such as Reactive Ancillary Service from ERCOT rather than retrofitting old equipment to provide the service. |
|  | Performance/Compliance: This issue does not involve any performance or compliance considerations. |
|  | Cost Allocation: Primary consideration of this issue. |
| Strategy | Recommendation XX: Develop one or more methodologies with supporting rationales for allocating the cost of Ancillary Services to Intermittent Renewable Resources, specifically, Wind Generation Resources (WGRs) , with further expansion to other components to the Net Load summation such as new intermittent renewable resources.. |
| Activities | ERCOT XX: None |
|  | MP XX: The Wind Cost Allocation Task Force (WCATF) of the ERCOT Wholesale Markets Subcommittee (WMS) was created in November 2009 to examine this issue and develop a cost allocation methodology with supporting rationale. The WCATF is meeting monthly in 2010. |
| Follow-Up | Awaiting final report from the WCATF. |
| Schedule | WCATF is to complete their work by _____, 2010. |

| MD-02 – Ancillary Services Procurement Optimization for 2009 – Annually, ERCOT produces its plan for procuring Ancillary Services for the coming calendar year. With the increasing influx of variable wind generation, the amounts and types of Ancillary Services needed to maintain system reliability may change. This issue examines potential impact of wind generation on ERCOT’s plan for Ancillary Service procurements for 2009. |  |
| --- | --- |
| Priority | Complete |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: The amounts and types of Ancillary Services procured by ERCOT do impact system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. |
|  | Performance/Compliance: This issue does not directly involve any performance or compliance considerations. |
|  | Cost Allocation: Whether or not to change Ancillary Cost allocations is a consideration of this issue. |
| Strategy | Recommendation XX: The Wind Operations Task Force (WOTF) of the ERCOT Reliability and Operations Subcommittee (ROS) reviewed ERCOT’s proposed Ancillary Services Procurement Plan for 2009 to ensure that it maintains adequate reliability while ensuring optimum market participation. . Future year efforts should also include ensuring that any and all out of merit dispatches necessary for controlling system security, such as Fleet OOMs, are included in the requirements algorithm for Regulation Services. |
| Activities | ERCOT XX: Prepare 2009 proposed Ancillary Service Procurement Plan |
|  | MP XX: WOTF reviewed ERCOT’s proposed 2009 Ancillary Services Procurement plan and made recommendation to ROS. |
| Follow-Up | None. |
| Schedule | WOTF completed its review of the proposed 2009 Ancillary Services Procurement Plan in December of 2008 and was approved by ROS, TAC and the ERCOT Board of Directors in February, 2009. |

| MD-03 – Non-Spin Requirements: Determine if additional amounts of Non-Spin Service procurements by ERCOT are necessary to reliably accommodate increased amounts of wind generation in ERCOT. Historical events indicate that there is increased risk to reliability due to the variable output of wind generation and the difficulties in predicting when such variations will occur. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by ensuring that adequate amounts of Non-Spin Service are procured by ERCOT to deal with increased risk from variable output wind generation. |
|  | Technical: This issue does involve some technical issues related to revisions of the Non-Spin Service procurement methodology |
|  | Market Design: The interrelated issue of AS inherently impacts market design. |
|  | Performance/Compliance: This issue does impact performance or compliance. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Examine methods to ensure that adequate Non-Spin capacity is available to ERCOT from the market to deal with increasing amounts of variable wind generation. |
| Activities | ERCOT (XX): Analyze and recommend revisions to the Ancillary Service Procurement methodology, specifically focusing on Non-Spin Service procurements to address concerns about increased amounts of variable wind generation entering the ERCOT market. |
|  | Market Participants (MP XX): Review and provide guidance to ERCOT on its analysis of Ancillary Service procurements. |
| Follow-Up | Periodically review historical Non-Spin Service procurements and deployments to ensure that reliability is maintained at the lowest possible cost to the market. |
| Schedule | ISSUE COMPLETE: In December, 2009, the ERCOT Board approved the proposed 2010 Ancillary Services Procurement methodology which was revised from the previous year’s methodology to specifically increase Non-Spin Service procurements to deal with the increased risk posed by increasing amounts of variable wind generation in the ERCOT market. |

| MD-04 New Ancillary Services Products for Reliability: . |  |
| --- | --- |
| Priority | .High |
| Considerations | Policy: Potentially |
|  | Reliability: Enhanced through assurance that needed services would be available. |
|  | Technical: |
|  | Market Design: Frequency Response and Fast Ramp Ancillary Services would facilitate reliability through market constructs. The value of these services is presently not fully accounted for as entities supplying them are paid solely for energy deployed. Development of ancillary service products would encourage this type of capability to be available when ERCOT believes it is necessary. |
|  | Performance/Compliance: Would be developed along wit the design of the AS. |
|  | Cost Allocation: Could be accommodated according to existing principles. |
| Strategy | . Recommendation XX: ERCOT should consider addition of these services as part of the 2011 AS Procurement Guidelines. Additionally, these services should be evaluated in the next round of AS needed for reliable integration of renewables. |
| Activities | ERCOT (XX): ERCOT should consider addition of these services as part of the 2011 AS Procurement Guidelines |
|  | Market Participants (MP XX): Should develop proposals for discussion. |
| Follow-Up | Services to be discussed for 2011 AS Procurement Guidelines and beyond as appropriate. |
| Schedule | 2010 discussions |
| Status | Services need specific definition and discussion in stakeholder bodies. |

| MD-05 – Benefits of Storage Technologies – The infusion of Federal Subsidies through the ARRA may increase the range of technologies that can be applied to improving grid stability and reliability at both the transmission and distribution level, and aid in the integration of renewable resources. |  |
| --- | --- |
| Priority |  |
| Considerations | Policy: Optimal utilization of storage technologies may require modifying ancillary services requirements and interconnection rules. |
|  | Reliability: Storage has the potential to increase reliability due to rapid and highly controllable response to dispatch instructions. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. As storage technologies are similar to demand side resources existing market constructs could be modified to accommodate their market participation. |
|  | Performance/Compliance: As market participation evolves, compliance metrics should be developed. |
|  | Cost Allocation: Storage technologies are not inherently different than existing generation that uses energy from the grid while it starts and then later generates energy. Cost allocation is not anticipated to be an issue. |
| Strategy | Recommendation X_: Continue to monitor development. Explore protocol revisions as required. |
| Activities | ERCOT (E X): Storage workshop is the first step in identifying the barriers to integration of storage, if any, into the ERCOT market. |
|  | Market Participants (MP X): Storage is a priority item for both TAC and WMS for 2010. (when was this decided?) |
| Follow-Up |  |
| Schedule |  |
| Status | Complete |

| MD-06 – Ancillary Services Procurement Methodology – Determine impact and possible changes in amounts of ancillary services to be procured by ERCOT on a daily and hourly basis to ensure reliability with increasing amounts of wind generation planned to be installed in the ERCOT market within the next few years. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: The amounts and types of Ancillary Services procured by ERCOT impact system reliability. The variable and relatively unpredictable nature of wind generation output will likely require ERCOT to procure additional amounts of Ancillary Services to maintain adequate system reliability. |
|  | Technical: This issue does not entail any technical considerations. |
|  | Market: Since all Ancillary Services involve markets in one way or another, market impacts are considerations. New Ancillary Services may be needed to fully optimize value of resources on the grid and to continue to reliably integrate renewables. |
|  | Performance/Compliance: As new AS are developed, performance and compliance requirements will also be developed.. |
|  | Cost Allocation: Whether or not to change Ancillary Cost allocations is a side issue but is related to this issue. |
| Strategy | Recommendation XX: ERCOT and stakeholders should continue to evaluate the AS needed to reliably operate the grid. |
| Activities | ERCOT XX: Consider new ancillary services, specifically, the potential reliability and market impacts of a Frequency Service, A Fast Ramp Service and a VAR service should be discussed. |
|  | MP XX: Develop revised AS definitions for discussion and consideration. |
| Follow-Up | Ongoing |
| Schedule | Ongoing |

| MD-07 Wind-powered Generation Resources Providing Ancillary Services: AS definitions are technology independent. All qualified resources can compete to supply them through the ERCOT managed AS markets. Thus, WGRs like other resources can compete to provide Ancillary Services. The latest technology WGRs have the technical capability to provide regulation services when there is enough wind. The following issues need to be explored: - What if any changes are needed to the nodal protocols to allow WGRs to provide ancillary services? - What if any changes are needed in WGR operating procedures or capabilities to provide ancillary services to ERCOT? |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: None |
|  | Reliability: Proper procedures need to be put in place to insure that reliability is maintained. |
|  | Technical: None, modern WGRs can provide excellent services if wind conditions are right. |
|  | Market: There are always market impacts from new entrants or revised product definitions. |
|  | Performance/Compliance: There may be new performance measures needed to ensure that WGRs are providing the needed service. |
|  | Cost Allocation: None forseen |
| Strategy | Anticipate issues to provide sufficient time to analyze, resolve, and implement as needed. Recommendation: Start a process of reviewing and discussing the mechanisms for WGRs to provide ancillary services. |
| Activities | ERCOT (E X): Review AS proposals. |
|  | Market Participants (MP X): WGRs assist in evaluating system operations alternatives. Make any needed modifications deemed commercially expedient to participate in providing ancillary services. |
| Follow-Up | May need protocol revisions depending on the results of the analysis |
| Schedule | This is primarily a market issue that will likely be important when more than 15,000 MW of WGR capacity is on the system. Discussion of the issue needs to be started soon and implementation will could be beneficial by 2013. |

| MD-08 – Reactive and Voltage Requirements Applicable to Wind: Review current ERCOT Protocols and Operating Guides to ensure reactive and voltage control requirements specified therein are applicable to all generating technologies, including wind generation. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue involves the policy of ensuring that each type of generating technology provides the proper amount of reactive and voltage control capability to ensure adequate reliability of the ERCOT system. |
|  | Reliability: This issue will ensure adequate ERCOT reliability by requiring all types of generating technologies, including wind turbines, to provide the appropriate amount of reactive and voltage control capability. |
|  | Technical: This issue involves technical issues related to the specific technical capability of a unconventional generation technology (e.g., wind turbine) to provide reactive and voltage control capability similar to that of conventional generation. |
|  | Market Design: This issue may impact market design if it is determined that a unconventional generation technology is allowed to purchase reactive or voltage control capability from a third-party provider through an ERCOT markets. |
|  | Performance/Compliance: This issue does impact performance or compliance of any generating technology. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Examine ERCOT Protocols and Operating Guides to determine if reactive and voltage control requirements are clearly applicable to all generating technologies. Develop AS product definitions for Reactive (VAR) Ancillary Service. |
| Activities | ERCOT (XX): Review and comment on any proposed changes in existing ERCOT Protocols or Operating Guides related to reactive and voltage control capability of generation resources. |
|  | Market Participants (MP XX): Review existing ERCOT Protocols and Operating Guides and recommend changes, if necessary, to ensure that all generating technologies are required to provide proper reactive and voltage control capability either directly or via a market solution. Develop AS product definitions for Reactive (VAR) Ancillary Service. |
| Follow-Up | Develop AS product definitions for Reactive (VAR) Ancillary Service. |
| Schedule | ISSUE Ongoing: PRR 830 "Reactive Power Capability Requirement" was approved by the ERCOT Board in November, 2009. However, this PRR has been appealed to the Public Utility Commission of Texas in Docket Nos. 37817, 37818, 37819, 37823, 37824and 37827, so it is not clear if this issue is really complete. Market still to consider Reactive AS as discussed in SP-07, SO-01, SO-06, SO-10, SO-17, MD-01. |

| MD-09 Wind Generation Dispatch in the Nodal Protocols: The current nodal protocols call for WGRs to follow ERCOT Base Point instructions when the Security Constrained Economic Dispatch (SCED) calculation indicate they must be curtailed below their High Sustained Limit (HSL)to maintain system reliability. The trigger to indicate that the WGR must curtail its output is when the Base Point it receives from SCED is more than 2 MW below the HSL used by SCED. The HSL for a WGR is dependent upon wind conditions and could change routinely. The current nodal protocols call for WGRs to routinely update their HSL by real-time telemetry to ERCOT. The WGRs does not know which HSL update to use. One solution is to have SCED send out a curtailment flag to signal to the WGR when it must curtail. While this could be the best resolution for the issue it would require software changes and would not be available until after nodal go live. In the interim, a change in the WGR telemetry procedure has been developed to ensure that the WGR and SCED are using the same HSL for their curtailment trigger. This requires a temporary software change in all of the WGRs control centers. The process requiring all WGRs to modify their software is in progress. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: None |
|  | Reliability: This modified procedure maintains the synchronization between SCED and the WGRs in order to maintain reliable operations. |
|  | Technical: None |
|  | Market: None |
|  | Performance/Compliance: Clarifies the performance requirement for the WGR. |
|  | Cost Allocation: None |
| Strategy | Recommendation: Develop a nodal protocol revision to temporarily resolve the issue by changing the WGR HSL telemetry procedure. Develop an additional nodal protocol revision, to be implemented after go live, for SCED to send a curtailment flag when needed; coordinate with other WGR related nodal revisions requiring software changes (MD-10, MD-11). |
| Activities | ERCOT (E X): Assist in analyzing and resolving the issue. Implement the needed changes. |
|  | Market Participants (MP X): WGRs implement the temporary fix in their software and procedures. Assist in analyzing and resolving the issue. |
| Follow-Up | None |
| Schedule | Nodal Protocol Revision Request 214 specifying a revised WGR HSL update process is in the approval process. By July 2010 Submit a nodal protocol revision request requiring a change in the nodal software creating a curtailment flag when needed by SCED (coordinate with MD-10 and MD-11) |

| MD-10 – VER Generation Performance Metrics in the Nodal Protocols – This issue relates to a review of the ERCOT Nodal Protocols to ensure proper treatment of wind generation in regard to performance metrics. VER Resource generators may be different from conventional generation in many ways. Because of these differences, it may be appropriate to develop special performance metrics for VER Resource generators that recognize the technological capability (or lack thereof) inherent to the various VERs and to the extent that system performance requirements are shifted to other technologies the stakeholders must determine and assign the cost offsets to the VERs as appropriate with the cost-causation principle |  |
| --- | --- |
| Priority | Medium |
| Considerations | Policy: This issue includes policy considerations on whether or not to impose the same performance standards on all generation technologies. |
|  | Reliability: Proper operation of wind generation resources can impact system reliability. Measurement of performance of wind generation, like that of conventional generation, is necessary to ensure adequate system reliability. |
|  | Technical: There are some technical considerations related to how wind turbines can or cannot respond to system disturbances. |
|  | Market: Inherently, exemptions or rules that provide differing incentives for different types of generators affect the market. Impacts cannot be judged until proposals for performance standards are drafted. |
|  | Performance/Compliance: This issue directly involves performance and compliance considerations. |
|  | Cost Allocation: This issue does not include any cost allocation considerations. |
| Strategy | Recommendation X_: Review the ERCOT Nodal Protocols to determine what performance measures and metrics currently apply to wind resources and make recommendations for any changes to better measure wind resource generation operations and responses during reliability events. |
| Activities | ERCOT (E X): Provide operational and performance data for wind resources for evaluation of various performance metrics applicable to wind generation. |
|  | Market Participants (MP X): This issue was assigned to the ERCOT Wholesale Market Subcommittee (WMS), which in turn, assigned the issue to its QSE Managers Working Group (QMWG), which is currently reviewing the performance metrics applicable to wind generation in the existing ERCOT Nodal Protocols. Upon completion of this review, the QMWG may make recommendations to the WMS for changes in the Nodal Protocols to recognize any inherent technological differences between wind turbine generators and conventional generators in regard to generator performance metrics. |
| Follow-Up | None at this time. |
| Schedule | The QMWG will complete its review of the Nodal Protocols and provide any recommendations to ROS by _______, 2010. |

| MD-11 Wind-powered Generation and Base Point Deviation in the Nodal Protocols: The nodal protocols specify that WGRs shall be held accountable for deviations from their base point when the Security Constrained Economic Dispatch (SCED) calculations must curtail them below the High Sustained Limit (HSL) used by SCED. The need to curtail is signaled by the fact that the base point received by the WGR is 2 MW or more below the HSL sent to ERCOT by the WGR. Ensuring that the HSL used by the WGR and that used by SCED is the subject of issue MD-09. This issue has resulted from the fact that the settlement equations use the HSL from the current operating plan and not the HSL used by SCED to trigger base point settlement charge calculations. The settlement trigger needs to be changed to use the HSL used by SCED. Since a software change is required to fix this issue, resolution will have to wait for nodal revisions implemented after go live. The possible effect of this error is inappropriate charges to WGRs that must be resolved by a routine dispute process. Dispute processes for settlement issues may be considered routine, but they do take up market participant and ERCOT staff time. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: None |
|  | Reliability: None |
|  | Technical: None |
|  | Market: Can expose WGRs to higher costs if not resolved. |
|  | Performance/Compliance: None |
|  | Cost Allocation: None |
| Strategy | Recommendation: Prepare a nodal revision request fixing this and other WGR related issues requiring a software change (see MD-09, MD-10) |
| Activities | ERCOT (E X): Assist with analyzing and resolving the issue. Implement needed changes. |
|  | Market Participants (MP X): WGRs assist with analyzing and resolving the issue. |
| Follow-Up | None |
| Schedule | Initiate the nodal revision request by July 2010. |

| MD-12 – Wind Generation Resource LSL as a Percentage of HSL – Determine the appropriate minimum percentage for the Low Sustained Limit (LSL) of the High Sustained Limit (HSL) for a wind generation resource and incorporate those values in the ERCOT Protocols. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: Currently non-wind resources must provide accurate LSL and HSL representations in their Resource Plans and in nodal in their COP. The issue is whether all resources should be treated similarly. |
|  | Reliability: This issue impacts reliability because ERCOT systems use the LSL and HSL to determine resource capability on the system. |
|  | Technical: This issue involves the technical feasibility of a wind generation facility to determine the appropriate minimum and maximum level of generation capability. |
|  | Market Design: Inherently, exemptions or rules that provide differing incentives for different types of generators affect the market. The fact that wind resources have the capability to prevent ERCOT systems from moving their units (by showing their LSL as 90% of the HSL) over the full range of output inherently affects market outcomes and creates an incentive for these resources to comply with this requirement because there is an economic incentive to do so. |
|  | Performance/Compliance: This issue does impact performance or compliance of any generating technology to meet its LSL and HSL. LSL as percent of HSL is an enforceable protocol condition for resources installed after 1/1/2003. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Determine the appropriate levels of LSL and HSL for wind generation facilities. |
| Activities | ERCOT (XX): Review and comment on any proposed changes in existing ERCOT Protocols or Operating Guides related to LSL and HSL for wind generation resources. |
|  | Market Participants (MP XX): Review existing ERCOT Protocols and Operating Guides and recommend the appropriate LSL and HSL standards for wind generation facilities. |
| Follow-Up | None necessary since the performance metric associated with the percentage of LSL to HSL will cease to exist when the ERCOT Nodal Market is implemented in December, 2010. |
| Schedule | ISSUE COMPLETE: PRR 773 "Setting the LSL Requirement for WGRs " was approved by the ERCOT Board in December, 2008. This PRR sets the LSL as a percentage of HSL at 10% for all wind generators installed on or after January 1, 2003. Wind generators installed prior to that date are excluded from the measure. |

| MD-13 – Use of State-of-the-Art Wind Forecast – An accurate wind power generation forecast is essential to the reliable and efficient integration of wind generation into the ERCOT grid. It is important for ERCOT and wind resources to be able to accurately forecast wind energy production on a day-ahead up to an hour-ahead timeframe to reliably and efficiently dispatch its resources to serve load. However, state-of-the-art forecasts require significant amounts of meteorological (site-specific and region-wide) and operating data (i.e., wind turbine availability) in order to accurately forecast energy production from wind generators. Such data is only available from Wind Generation Resource (WGR) owners. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not include any policy considerations. |
|  | Reliability: Proper forecasting of wind generation output can impact system reliability. This new requirement will allow ERCOT to perform its Day Ahead Replacement Reserve Service (RPRS) procurement using a consistent state-of-the-art forecast of the output from WGRs rather than relying on forecasts from varying sources (i.e., individual wind farms) with varying degrees of sophistication and accuracy. |
|  | Technical: There are some technical considerations related to the inputs necessary to populate the data required for a state-of-the art wind power production forecast. |
|  | Market: Wind forecasts inherently affect ERCOT markets as ERCOT bases its net load with the exception of the socialization of inaccurate forecast outcomes and the costs of the centralized forecasting functions coupled with any hardware and software procurement and O&M support on the wind forecast.ERCOT’s central systems. |
|  | Performance/Compliance: This issue directly involves compliance considerations. |
|  | Cost Allocation: This issue does not include any direct cost allocation considerations. Indirectly wind forecasting affects AS procurement requirements. considerations with the exception of the socialization considerations noted in the section above (Market:). . |
| Strategy | Recommendation: Establish a requirement in the ERCOT Protocols for a Qualified Scheduling Entity (QSE) representing Wind Generation Resources (WGRs) to use a state-of-the-art wind production forecast provided by ERCOT in their daily resource plan submittals unless their own forecasts are consistently more accurate. . |
| Activities | ERCOT (E X): Develop a state-of-the-art wind power production forecast through collaboration with a recognized forecast provider. File a Protocol Revision Request (PRR) to establish data reporting requirements for QSEs representing WGRs to populate the state-of-the-art wind forecast model. |
|  | Market Participants (MP X): Establish processes to collect and transmit required meteorological data to ERCOT to feed into the state-of-the-art wind power production forecast. |
| Follow-Up | None at this time. |
| Schedule | Protocol Revision Request 763 - Use of WGRPP as Planned Operating Level in Day-Ahead Resource Plan for WGRs was submitted by ERCOT staff in May of 2008 and approved by the ERCOT Board of Directors in July of 2008. |

4.4.	Workshop and/or Training Issues

| WT-01 – Resource Plan and Schedule Update Process: Determine potential improvements to the existing Resource Plan and Resource Schedule update process to improve performance and reliability. Because of the pending implementation of the Nodal market design, this issue should be addressed after the Nodal Market implementation as a topic for a future workshop. |  |
| --- | --- |
| Priority | Low |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by providing ERCOT with more timely and accurate information regarding the status and operation of wind generation resources. |
|  | Technical: This issue does involve some technical issues related to implementation within the Nodal market design as planned. |
|  | Market Design: This issue does not impact market design. |
|  | Performance/Compliance: This issue does impact performance or compliance. |
|  | Cost Allocation: This issue does not directly impact cost allocation. |
| Strategy | Solicit input and ideas from Market Participants and ERCOT staff through a workshop. |
| Activities | ERCOT (XX): Host a workshop dealing with potential improvements to the scheduling of both conventional and variable renewable resources that could be implemented into the Nodal market design after initial Go-Live (i.e., after December, 2010) |
|  | Market Participants (MP XX): Provide speakers and/or suggested improvements for discussion at the workshop. |
| Follow-Up | None at this time. |
| Schedule | Hold workshop after Nodal Go-Live (2011 or beyond). |

| WT-02 – Wind Workshop III (Summer 2009): Develop list of topics and speakers for the ERCOT Wind Workshop III to be held in the summer of 2009. |  |
| --- | --- |
| Priority | High |
| Considerations | Policy: This issue does not directly involve policy. |
|  | Reliability: This issue will improve ERCOT reliability by providing ERCOT with better tools to address issues being experienced as the penetration of variable wind generation on the ERCOT system continues to increase. |
|  | Technical: This issue does involve some technical issues related to various types of wind turbine designs. |
|  | Market Design: This issue could result in development of new market-based tools to help ERCOT deal with increased penetration of variable wind generation. |
|  | Performance/Compliance: Any tools developed as a result of this issue could impact performance or compliance. |
|  | Cost Allocation: This issue could impact cost allocation if certain costs are incurred due to increased penetration of variable wind generation |
| Strategy | Make the market participants aware of issues that ERCOT has experienced as variable wind generation penetration has increased to stimulate new ideas and methods of reliably integrating such resources into the ERCOT system. |
| Activities | ERCOT (XX): Host a workshop for interested parties to discuss methods of improving system operations and reliability in an environment of ever-increasing use of variable wind generation resources. |
|  | Market Participants (MP XX): Provide speakers and/or suggested improvements for discussion at the workshop. |
| Follow-Up | None at this time. |
| Schedule | ISSUE COMPLETE: The workshop was held on June 29, 2009 and was well-attended. |

| WT-03 Wind Turbine Operator Training: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-04 Wind in the Nodal Market: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-05 Wind Workshop IV: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-06 Storage Workshop I: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

| WT-07 Energy Storage Workshop I: . |  |
| --- | --- |
| Priority | . |
| Considerations | Policy: . |
|  | Reliability: . |
|  | Technical: . |
|  | Market Design: . |
|  | Performance/Compliance: . |
|  | Cost Allocation: . |
| Strategy | . Recommendation XX: . |
| Activities | ERCOT (XX): . |
|  | Market Participants (MP XX): . |
| Follow-Up | . |
| Schedule | . |
| Status | . |

5.	2010-2011 RTWG Work Plan

The RTWG Work Plan for 2010-2011 is guided by its charter and goals as approved by TAC.  The work plan describes the activities and work product planned for the period through the first year of nodal market operations.

5.1.	RTWG Charter

The RTWG Charter was approved by TAC on Nov. 6, 2008.

The ERCOT Technical Advisory Committee creates the Renewable Technologies Work Group to coordinate and track stakeholder efforts to capture the benefits and address the challenges associated with the introduction of renewable energy generating technologies interconnected to the ERCOT grid.

Created as a Work Group, rather than a Subcommittee, the RTWG does not have a formal voting structure, but rather strives to achieve consensus on the issues raised during the conduct of its duties.  Where applicable, the RTWG will report the consensus, majority, and / or minority views of participants on each issue.

The Chair and Vice Chair of the RTWG will be appointed by the TAC Chair and confirmed by the TAC.  The RTWG shall meet not less than quarterly and shall continue in the conduct of its duties until such time as TAC decides to dissolve the work group.

The RTWG is charged with the following duties:

- Identify issues related to renewable energy generation on the ERCOT system – either benefits not realized or challenges which need to be addressed.  This activity does not preclude WMS or ROS from identifying and resolving wind integration issues within their traditional purview.

- Define, frame, and prioritize the identified issues for resolution

- Refer issues to the appropriate TAC subcommittees for further development and resolution

- Gather input as provided from TAC subcommittees and RTWG activities and develop recommendations and / or frame issues for resolution by TAC

- Provide monthly status reports to TAC

- Maintain an issues tracking system

- Organize and host technical workshops as needed to ensure ERCOT Staff and market participants stay abreast of new technologies deployed on the ERCOT system, emerging technologies offering solutions to renewable generation technology challenges, and industry best practices

- Organize training seminars as needed to ensure ERCOT Staff and affected market participants effectively coordinate practices and procedures adopted to reliably integrate renewable generation technologies into the ERCOT grid

- Draft quarterly reports to TAC to support the ERCOT process to provide quarterly reports to the PUCT regarding reliability and grid integration issues related to renewable resources

5.2.	RTWG Goals

Text.

Goals.

5.3.	RTWG Activities

Regular Meetings

Workshops

Liaisons

Reports

Phase One Activities

Completed Phase One Activities

Summary Table of Major Phase One Activities

-PRRs

-NPRRs

-OGRRs

-NOGRRs

-Process/Procedure Changes

-Issues Not To Be Addressed

-Open Phase One Activities

--PRR 833

--Wind Workshop IV

Phase Two Activities

Solar Workshop I

Storage Workshop I

Wind Workshop V

Storage White Paper

Wind Ramp Event Simulation Tool

Phase Three Activities

No Phase Three Activities are yet defined or scheduled.

5.4.	RTWG Work Product

Text.

Regular Meetings, Workshops, Issues Communication, Issues Tracking, Work Product

Issues Communication

To ensure transparency and broad communication of all renewable technologies integration issues with market participants and policymakers, the following activities are performed on a regular basis:

- Designated RTWG member reports relevant RTWG activities to the WMS and ROS monthly;

- Designated RTWG member reports relevant WMS and ROS activities to the RTWG monthly;

- The RTWG Chair (or designate) reports RTWG activities to TAC monthly;

- The TAC Chair (or designate) reports on the TRIP to the ERCOT Board of Directors and to the PUCT quarterly; and

- The current version of the RTWG issues list is available in the public  area of the ERCOT web site.

- An archived list of all parties’ comments to the TRIP shall be maintained on the RTWG ERCOT web page with adequate detail to provide transparency to how the RTWG dealt with each set of comments in detail.

The RTWG in coordination with ERCOT staff, will facilitate periodic workshops and training seminars on renewable technology issues for industry stakeholders and interested parties.

6.	Summary Tables

6.1.	Summary Table of TRIP Goals

| Goal 01 | Identify and communicate issues of interest related to the integration of renewable resources to market participants and industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| --- | --- | --- |
| Goal 02 | Develop strategies to resolve identified issues. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 03 | Communicate the long-term plan for ERCOT activities related to renewable technologies integration to market participants and industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 04 | Communicate progress on renewable technologies integration and raise issues for resolution to Texas policy makers and ERCOT ISO decision makers. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 05 | Document the renewable technologies integration activities within the ERCOT Region as a resource for electric power industry stakeholders. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 06 | Document “lessons learned” through the ERCOT renewable technologies integration effort to preserve institutional memory and better inform ongoing integration activities. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 12 |
| Goal 07 | Remain informed of federal policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 20 |
| Goal 08 | Guide and track stakeholder efforts to facilitate implementation of and adaptation to the PUCT’s CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 09 | Ensure the ERCOT planning function addresses the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 10 | Ensure the ERCOT operations function is prepared for the operating conditions resulting from the likely significant increase in installed renewable generation capacity associated with the PUCT CREZ Plan. Supported by Recommendations 01, XX, XX, XX, and XX. | p. 23 |
| Goal 11 | Remain informed of state policy initiatives likely to promote significant changes affecting the ERCOT system and consider whether such policies require stakeholder action to prepare ERCOT for the anticipated changes. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 23 |
| Goal 12 | Identify and capture the economic benefits and reliability enhancements offered by renewable generation technologies and related applications and practices while maintaining ERCOT system reliability. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 24 |
| Goal 13 | Improve the quality of data and accuracy of models used to support the ERCOT system planning function. Supported by Recommendations 02, XX, XX, XX, and XX. | p. 25 |
| Goal 14 | Assess ERCOT system planning capabilities in light of activities required to effectively plan for further integration of renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 26 |
| Goal 15 | Ensure particular attention is paid to ramping events, including taking steps to mitigate ramp event impacts, improve ramp event forecasting and pre-event system posturing, and devising more effective and/or efficient use of market and operational tools during ramp events. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 28 |
| Goal 16 | Identify and address current and anticipated challenges to the maintenance of system frequency control. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 28 |
| Goal 17 | Develop a near-term process by which the range of issues associated with the kinds of ancillary services available to the ERCOT market and the procurement methodologies for those services are evaluated and, if necessary, adjusted to facilitate the integration of renewable generation technologies. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 29 |
| Goal 18 | Assess voltage control requirements, capabilities, and areas of possible clarification or improvement in current procedures and technical standards. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 30 |
| Goal 19 | Evaluate renewable generation forecasting practices and outcomes. Identify areas of possible improvement and develop solutions. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 31 |
| Goal 20 | Assess ERCOT operations capabilities in light of activities required to effectively integrate renewable technologies and identify areas of possible capabilities enhancements through the application of internal and external resources. Where operational capabilities are improved, ensure adequate training is performed to maximize benefits. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 31 |
| Goal 21 | Improve and maintain stakeholder technical understanding of the capabilities and limitations of relevant emerging and evolving grid-connected technologies; their potential benefits and challenges for the system planning and operations functions; and facilitate collaborative stakeholder communications to solve technical integration issues. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 32 |
| Goal 22 | Strike an appropriate balance which maintains an open access paradigm allowing and encouraging introduction and integration of benficial technological advances while maintaining interconnection, registration, planning, and operating criteria which protect system security. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 23 | As renewable generation and related technologies mature and enhanced capabilities become available, ensure technical standards are periodically evaluated to ensure best available technologies and practices are utilized where necessary and cost-effective. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 24 | Contribute to ERCOT’s development of longer-term system planning studies which include reasonable assumptions regarding the installation and capabilities of emerging renewable generation and related technologies. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 33 |
| Goal 25 | Focus on near-term refinement and development of tools providing enhanced operational capabilities for ERCOT management of wind-related issues. In the longer term, evaluate potential tools needed to integrate other renewable technologies as operational issues are identified. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 34 |
| Goal 26 | Identify renewable technologies integration market design questions and impacts on market outcomes. Facilitate issues framing for resolution, if desired, by the appropriate stakeholder or policy making body. Supported by Recommendations XX, XX, XX, XX, and XX. | p. 36 |
| Goal 27 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 28 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 29 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |
| Goal 30 | Goal text. Supported by Recommendations XX, XX, XX, XX, and XX. | p. XX |

6.2.	Summary Table of TRIP Recommendations

| Recommendation 01 | For system planning purposes and operational readiness activities, ERCOT should assume full implementation of the PUCT CREZ Plan by Dec. 31, 2013. Studies and preparations should assume at least 19,000 MW of installed wind generation capacity. Supports Goals Nos. 08, 09, 10. | p. 23 |
| --- | --- | --- |
| Recommendation 02 | As integration issues are examined, data and model quality should be considered and, where possible, improved. ERCOT and stakeholders should collaborate in specific activities to improve ERCOT’s access to quality technical data related to renewable generation technologies. Supports Goals Nos. 13, XX, XX, and XX. | p. 25 |
| Recommendation 03 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system planning resources to keep pace with rapidly evolving grid-connected technologies. Supports Goals Nos. 14, XX, XX, and XX. | p. 27 |
| Recommendation 04 | As a component of the annual budgeting process, the ERCOT Board should include a special focus on the requirements for the ISO’s system operations resources, including operator training opportunities, to keep pace with rapidly evolving grid-connected emerging technologies. Supports Goals Nos. XX, XX, XX, and XX. | p. 31 |
| Recommendation 05 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 06 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 07 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 08 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 09 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 10 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 11 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 12 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 13 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 14 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 15 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 16 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 17 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 18 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 19 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 20 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 21 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 22 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 23 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 24 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 25 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 26 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 27 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 28 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 29 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 30 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |
| Recommendation 31 | Recommendation text. Supports Goals Nos. XX, XX, XX, and XX. | p. XX |

6.3.	Summary Table of Recommended ERCOT TRIP Activities

| ERCOT 01 | Activity description. Schedule. | p. XX |
| --- | --- | --- |
| ERCOT 02 | Activity description. Schedule. | p. XX |
| ERCOT 03 | Activity description. Schedule. | p. XX |
| ERCOT 04 | Activity description. Schedule. | p. XX |
| ERCOT 05 | Activity description. Schedule. | p. XX |
| ERCOT 06 | Activity description. Schedule. | p. XX |
| ERCOT 07 | Activity description. Schedule. | p. XX |
| ERCOT 08 | Activity description. Schedule. | p. XX |
| ERCOT 09 | Activity description. Schedule. | p. XX |
| ERCOT 10 | Activity description. Schedule. | p. XX |

6.4.	Summary Table of Recommended Market Participant TRIP Activities

| MP 01 | Activity description. Schedule. | p. XX |
| --- | --- | --- |
| MP 02 | Activity description. Schedule. | p. XX |
| MP 03 | Activity description. Schedule. | p. XX |
| MP 04 | Activity description. Schedule. | p. XX |
| MP 05 | Activity description. Schedule. | p. XX |
| MP 06 | Activity description. Schedule. | p. XX |
| MP 07 | Activity description. Schedule. | p. XX |
| MP 08 | Activity description. Schedule. | p. XX |
| MP 09 | Activity description. Schedule. | p. XX |
| MP 10 | Activity description. Schedule. | p. XX |

6.5.	Summary Schedule of Major TRIP Activities 2010-2012

| Date | Wind Workshop IV | reference |
| --- | --- | --- |
| Date | Solar Workshop I | reference |
| Date | Storage Workshop I | reference |
| Date | ERCOT Operations Training | reference |
| Date | Wind Workshop V | reference |
| Date | Activity | reference |
| Date | Activity | reference |

6.5.	Summary TRIP Schedule

7.	 Appendices

7.1.	March 2010 RTWG Issues List

7.2.	2009 RTWG White Papers

7.3.	2008-2009 Wind Workshop Presentations

7.4	2009 Presentations Made to the RTWG

8.	References

The presentations made at WInd Workshop I are located in Section 7.2.1.

PUCT Docket No. 33672 Final Order, paragraph 7

cite PUCT project where quarterly reports are filed

cite

cite

cite ERCOT CO2 study May 2009

cite SB7, 75R

cite SB7, 75R

http://www.ercot.com/content/meetings/board/keydocs/2010/0420/Item_08_-_Grid_Operations_and_Planning_Report.pdf

cite SB20, 78 first or second called

PUCT Docket No. 33672 Final Order, Paragraph 1

PUCT Docket No. 33672 Final Order, Paragraph 3

Cite(HD Comment: I can’t find such a date in the Final Order of Docket No. 33672 or Docket No. 36801)

PURA 39.XXX, etc.

brief recitation of criteria and cite NERC standards.

defined ancillary services in the zonal market may be found in Protocols Sec. X.X-X.XX and link to doc. defined ancillary services in the nodal market may be found in Nodal Protocols Sec. X.X-X.XX and link to doc.

cite GE study and point to ancillary services discussion, impacts, recommendations.

brief summary of 2008 and 2009 methodology changes and links to methodology documents

ERCOT Protocols 6.5.7 Voltage Support Service,

ERCOT Protocols 6.5.7.1 Installed Reactive Power Capability Requirement for Generation Resources Required to Provide VSS.

The ERCOT 2008 State of the Market Report produced by Potomac Economics indicates that the implied heat rate in the ERCOT West Zone dropped by approximately 24% between 2005 and 2008. (See chart entitled “Monthly Average implied Marginal Heat Rate” on page v.)

cite url