ERCOT Operating Guides

Section 7:  Disturbance Monitoring and System Protection

August 1, 2010

Contents

7	0BDisturbance Monitoring and System Protection	7-3

1B7.1	Disturbance Monitoring Requirements	7-3

4B7.1.1	Introduction	7-3

5B7.1.2	Fault Recording Equipment	7-3

6B7.1.3	Dynamic Disturbance Recording Equipment	7-6

7B7.1.4	Equipment Reporting Requirements	7-6

8B7.1.5	Review Process	7-6

2B7.2	System Protective Relaying	7-7

9B7.2.1	Introduction	7-7

10B7.2.2	Design and Operating Requirements for ERCOT System Facilities	7-7

11B7.2.3	Performance Analysis Requirements for ERCOT System Facilities	7-11

12B7.2.4	Maintenance and Testing Requirements for ERCOT System Facilities	7-13

13B7.2.5	Requirements and Recommendations for ERCOT System Facilities	7-13

3B7.3	Document Control	7-24

# 0BDisturbance Monitoring and System Protection

## 1B7.1	Disturbance Monitoring Requirements

### 4B7.1.1	Introduction

Disturbance monitoring is necessary to determine:

- The performance of the ERCOT system,

- The effectiveness of protective relaying systems,

- Verify ERCOT system models, and

- Determine the causes of ERCOT system disturbances (unwanted trips, faults, and protective relay system actions).

To ensure that adequate data is available for these activities, the disturbance monitoring requirements and procedures discussed in this document have been established by ERCOT for Facility Owners in the ERCOT system.

Disturbance monitoring equipment includes digital fault recorders (DFRs), certain protective relays with fault recording capability, and dynamic disturbance recorders (DDRs). Sequence-of-event recorders (SERs), although considered equipment to monitor disturbances, are not preferred devices, as they provide limited information.  SERs have been replaced by digital fault recorders and microprocessor-based protective relays.

### 5B7.1.2	Fault Recording Equipment

Fault recording equipment includes digital fault recorders (DFRs) and protective relays with fault recording capability that meet the triggering requirements below.  Fault recording equipment required by these Operating Guides shall be time synchronized with a Global Positioning System-based clock, or ERCOT-approved alternative, with sub-cycle (17 millisecond) timing accuracy and performance.

#### 14B7.1.2.1	Triggering Requirements

Fault recording equipment triggering must occur for system voltage magnitude and current magnitude disturbances (delta V and delta I) without requiring any circuit breaker operations or trip outputs from protective relay systems. Triggering by additional methods is acceptable. Triggering shall be adjusted to operate for faults in the area to be monitored, which should overlap into the area of coverage of adjacent fault recorders.

#### 15B7.1.2.2	Location Requirements

The location criteria below shall apply to equipment operated at or above 100 kV. The Facility Owner, whether registered as a TDSP or Resource Entity, shall install fault recording equipment at the following facilities, at a minimum:

- Interconnections to other Regions (i.e. outside ERCOT).

- Switching stations where electrical transfers of equipment can be made between ERCOT and another Region.

- Switching stations having three or more non-radial 345 kV line terminals.  If a switching station is one bus removed from a station with a larger number of line terminals, then the fault recorder shall be located at the larger station and not required at the smaller station.

- Switching stations that are more than one circuit breaker-controlled bus away from a fault recorder and have five or more non-radial line terminals.

- For the purpose of evaluating #c. and #d. in this section, autotransformer or generating capacity totaling 150 MVA or greater (based upon minimum nameplate rating upon which transformer impedance is stated, i.e., base rating) shall constitute a non-radial line terminal at the highest voltage level to which it is directly connected.

- All generating station switchyards connected to the ERCOT System with an aggregated generating capacity above 100 MVA or the remote line terminals of each generating station switchyard.

All fault recording equipment shall be either DFR’s or fault recording protective relays

#### 16B7.1.2.3	Data Recording Requirements

For Facilities operating at 100kV or above where fault recording equipment is required, recorded electrical quantities shall be sufficient to determine the following:

- Two (2) sets of voltages for breaker-and-a-half and ring bus substation configurations.  One (1) set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform.

- For all lines, neutral (residual) current waveform.

- Circuit breaker status.

- Circuit breaker trip circuit status.

- Date and time stamp.

For all new or upgraded fault recorder installations, recorded electrical quantities shall be sufficient to determine the following additional items:

- For all autotransformers, high or low voltage terminal current waveform for three (3) phases and either neutral/residual current waveform or current waveform in delta windings.

- For all lines, two (2) phase current waveforms.

- Status – carrier transmitter control (i.e. start, stop, keying).

- Status – carrier received.

#### 17B7.1.2.4	Data Retention and Reporting Requirements

The Facility owner shall store all recorded fault data for at least a three (3)-year period.  This data shall be stored in the form of a computer file or files.

Facility owners shall provide fault recordings to ERCOT or the North American Electric Reliability Corporation (NERC) upon their request, within five (5) Business Days, along with channel identification and scaling information to allow analysis of the recordings.  Fault recordings shall be shared between Facility owners, upon their request, for the analysis of ERCOT System disturbances.

Data submissions shall be COMTRADE fault recordings (.cfg and .dat files) and one (1) or more identification files that associate the COMTRADE recordings with ERCOT System disturbances and ERCOT short circuit database bus numbers.  The identification file shall be a Microsoft Excel © spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel © spreadsheet.  For this file, the data fields to be reported for each record, in the following order, are:

#### 18BReporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |  |
| --- | --- | --- |
| From Bus (ERCOT short circuit database bus number) |  |  |
|  | To Bus (ERCOT short circuit database bus number) |  |
| Nominal Voltage of Faulted Branch or Bus (kV) |  |  |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location) |  |  |
| Time Zone (Central Prevailing Time (CPT), Coordinated Universal Time (UTC), etc.) |  | Date (MM/DD/YYYY) |
|  |  | Time (HH:MM:SS, twenty-four (24) hour format) |
|  |  | Cause Code |
| Fault Recorder Data |  | Circuit (1, 2, A, B, N, S, etc.) |
| From Bus – Recorder Location (ERCOT short circuit database bus number) |  |  |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |  |
|  | Nominal Voltage of Monitored Branch (kV) |  |
|  | Measured Current Magnitude (primary value in RMS amperes) |  |
|  | Recorded Fault Duration (cycles) |  |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |  |
| Optional Comments (40 char. max.) |  |  |

When multiple recordings exist for a single event, data from the best recording (usually the closest recorder) is required.

#### 19B7.1.2.5	Maintenance and Testing Requirements

Facility Owners shall maintain and test their Fault recording equipment as follows:

- In accordance with the manufacturer’s recommendations.

- Calibration of the analog (waveform) channels shall be performed at installation and when records from the equipment indicate a calibration problem.  Calibration can be monitored through the analysis and correlation of fault records with system models and the records of other fault recorders in the area.

- Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record (remotely or at the device), or automatic record production due to a power system disturbance.

### 6B7.1.3	Dynamic Disturbance Recording Equipment

Reserved

### 7B7.1.4	Equipment Reporting Requirements

Facility Owners shall maintain a current database summarizing their disturbance monitoring equipment installations.

The database shall include installation location, type of equipment, make and model of equipment, operational status, a listing of the major equipment being monitored and the date the equipment was last tested.  This database shall be submitted to ERCOT annually, by October 31.  Additionally, a complete list of all monitored points at each installation shall be maintained by Facility Owners and provided, when requested specifically by ERCOT or NERC, within 30 days.

ERCOT shall maintain a comprehensive database of all Facility Owner’s disturbance monitor equipment submittals, updated annually.

### 8B7.1.5	Review Process

ERCOT shall review fault recorder and disturbance recorder locations for compliance and adequacy when significant changes are made to the ERCOT system or at least every five years.

## 2B7.2	System Protective Relaying

### 9B7.2.1	Introduction

The satisfactory operation of the ERCOT System (equipment operated above 60 kV), especially under abnormal conditions, is greatly influenced by protective relay system.

Protective relay systems are defined as the total combination of:

- The protective relays,

- Associated communications system,

- Voltage and current sensing devices, and,

- The dc system up to the terminals in the circuit breaker.

Although relaying of tie points between Facility Owners is of primary concern to the ERCOT System, internal protective relay system often directly, or indirectly, affects the adjacent area also.  Facility Owners are those entities owning facilities in the ERCOT System.  Facility Owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  Protective relay system of individual Facility Owners shall not adversely affect the stability of ERCOT System interconnections.  Additional minimum protective relay system requirements are outlined in North American Electric Reliability Corporation (NERC) Planning and Reliability Standards.

#### 20B7.2.1.1	Applicability

These objectives and design practices shall apply to all new protective relay system applied at 60 kV and above unless otherwise specified.  It is recognized that there may be portions of the existing ERCOT System that do not meet these objectives.  It is the responsibility of individual Facility Owners to assess the protective relay system at these locations and to make any modifications that they deem necessary.  Similar assessment and judgment should be used with respect to protective relay system existing at the time of revisions to this guide.  Special local conditions or considerations may necessitate the use of more stringent design criteria and practices.

### 10B7.2.2	Design and Operating Requirements for ERCOT System Facilities

- Protective relay systems shall be designed to provide reliability, a combination of dependability and security, so that protective relay systems will perform correctly to remove faulted equipment from the ERCOT System.

- For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one (1) location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in other sections of the Operating Guides.

- Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

- The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

- Applicable Institute of Electrical and Electronic Engineers (IEEE)/ American National Standards Institute (ANSI) guides shall be considered when applying the protective relay system on the ERCOT System.

- The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility Owners affected shall negotiate a solution.

- All Facility owners shall give sufficient advance notice to ERCOT of any changes to their Facilities that could require changes in the protective relay system of neighboring Facility owners.

- Facility owners’ operations personnel shall be familiar with the purposes and limitations of the protective relay system.

- The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused Direct Current (DC) control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within thirty (30) days.  This documentation shall be reviewed by ERCOT for verification of implementation.

- Upon ERCOT’s request, within thirty (30) days, Power Generation Companies (PGCs) shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

- Upon ERCOT’s request, within thirty (30) days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

- Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by Generation Entities, to ERCOT upon their request within thirty (30) days.

- Special Protection Systems (SPSs) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in Demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include under-frequency or under-voltage Load shedding.  A “Type 1 SPS” is any SPS that has wide-area impact and specifically includes any SPS that a) is designed to alter generation output or otherwise constrain generation or imports over DC Ties, or b) is designed to open 345 kV transmission lines or other lines that interconnect Transmission and/or Distribution Service Providers (TDSPs) and impact transfer limits.  Any SPS that has only local-area impact and involves only the Facilities of the owner-TDSP is a “Type 2 SPS.”  The determination of whether an SPS is Type 1 or Type 2 will be made by ERCOT upon receipt of a description of the SPS from the SPS owner.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of NERC Standards relating to SPSs, and shall additionally meet the following ERCOT requirements:

- The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources and High Voltage Direct Current (HVDC) ties.

- The SPS shall be automatically armed when appropriate.

- The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a Real-Time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one (1) or more of the SPS’s monitored Facilities exceeds ninety-percent (90%) of the flow necessary to arm the SPS.  The cost necessary to provide such status indication shall be allocated as agreed by the SPS owner and the Generation Resource owner.

- The status indication of any automatic or manual arming/activation or operation of the SPS shall be provided as Supervisory Control and Data Acquisition (SCADA) alarm inputs to the owners of any Facility(ies) controlled by the SPS.

- When a Transmission Operator (TO) removes an SPS from service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the market via Market Information System (MIS).  When an SPS is returned to service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

- The status indication of the following items shall be provided by SCADA telemetry provided by the owner of the SPS equipment to ERCOT for incorporation into ERCOT systems:

- a.		Any automatic or manual arming/activation or operation of the SPS;

- b.		The in-service/out-of-service status of the SPS; and

- c.	Any additional related telemetry that already exists pertinent to the monitoring of the SPS (e.g. status indication of communications links between associated SPS equipment and Transmission Service Provider (TSP) control center, arming limits of associated SPS equipment).

- The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS every five (5) years, or sooner as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and posted on the ERCOT website.

- For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Service Request to ERCOT.

- For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a Service Request.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one (1) review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, and approval of ERCOT before completion of the required ERCOT review.

- The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of any Facility(ies) controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

- An ERCOT SPS review shall verify that the SPS complies with ERCOT and NERC criteria, guides, and Reliability Standards.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within thirty (30) days.

- As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the appropriate Reliability and Operations Subcommittee (ROS) working groups such as the Steady State Working Group (SSWG), the Dynamics Working Group (DWG), and/or the System Protection Working Group (SPWG) shall review the SPS and report any comments, questions, or issues to ERCOT for resolution.  ERCOT may work with the owner(s) of Facilities controlled by the SPS as necessary to address all issues.

- ERCOT shall develop a methodology to include the SPS in the Commercially Significant Constraint (CSC) limit calculations, if appropriate.

- ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

- SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 6.1.2, Relay Misoperation Report.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

- ERCOT shall report all SPS operations and misoperations to the Texas Regional Entity (TRE) for review.  SPS arming or activation that ramps generation back is not considered an operation or misoperation with respect to reporting requirements to TRE.  An operation and misoperation of an SPS with respect to reporting requirements to TRE occurs when changes to the transmission system occur, including but not limited to circuit breaker operation.  Owners of SPSs will provide a monthly report to ERCOT by the 15th of each month, for the previous month, describing each instance an SPS armed/activated and reset.  The report will include the date and time of arming/activation and reset.  ERCOT shall consolidate the monthly reports and forward to TRE.

- If an SPS which removes generation from service operates more than two (2) times within a six (6) month period and the operations are not a direct result of an ERCOT System disturbance or a contingency operation, ERCOT may require the Generation Resource owner(s) to decrease the available capability on the affected Generation Resource(s).  The amount of available capacity to be decreased shall be determined by ERCOT.  The decreased available capacity on the Generation Resource(s) shall remain until the Generation Resource owner(s) provides documentation that demonstrates the Generation Resource(s) can properly control output in a pre-contingency or normal ERCOT System condition.

- For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the ERCOT MIS.  Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a Service Request, whenever the SPS is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all Facilities controlled by the SPS.

### 11B7.2.3	Performance Analysis Requirements for ERCOT System Facilities

- All ERCOT System disturbances (unwanted trips, faults, and protective relay system operations) shall be analyzed by the affected Facility Owner promptly and any deficiencies investigated and corrected.

- All protective relay system misoperations in systems 100 kV and above shall be documented, including corrective actions and the documentation supplied by the affected Facility Owner to ERCOT or NERC upon their request within five business days.  All protective relay system misoperations shall be documented using Section 6.1.2, Relay Misoperation Report.  Any of the following events constitute a reportable protective relay system misoperation:

- Failure to Trip – Any failure of a protective relay system to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device.

- Slow Trip – A correct operation of a protective relay system for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intends.

- Unnecessary Trip During a Fault – Any relay initiated operation of a circuit breaker during a fault when the fault is outside the intended zone of protection.

- Unnecessary Trip Other Than Fault – The unintentional operation of a protective relay system, which causes a circuit breaker to trip when no system fault is present.  May be due to vibration, improper settings; load swing, defective relays, or SCADA system malfunction.

- Employee action that directly initiates a trip is not included in this category. It is the intent of this reporting process to identify misoperations of the relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the relay system. With this in mind, if an individual directly initiates an operation, it is not counted as a misoperation (i.e., unintentional operation during tests). On the other hand, if a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a relay system misoperation

- Failure to Reclose – Any failure of a protective relay system to automatically reclose following a fault if that is the design intent.

- All SPS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five business days.  All SPS misoperations shall be documented using Section 6.1.2, Relay Misoperation Report.  Any of the following events constitute a reportable SPS misoperation:

- Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occur.

- Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed.

- Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s).

- Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s).

- Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the design intent.

- Facility Owners shall document the performance of their protective relay system utilizing the method described in the paper “Transmission Protective Relay System Performance Measuring Methodology”, IEEE/PSRC Working Group 13 September 16, 1999. Facility Owners shall report the performance of their 138 kV and 345 kV protective relay system for the previous twelve months to ERCOT on an annual basis.  The reporting period shall be from May 1 of the previous year through April 30 of the present year. The performance data reported shall include the total number of protective relay system misoperations, the total number of events, and the factor “k”.

- At least annually, ERCOT shall review the protective relay system misoperation reports and 345 kV performance data of Facility Owners for analysis of protective relay system performance and compliance.

- All Facility owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in Section 7.1.2.3, Data Recording Requirements.

- Facility owners shall provide an assessment of the system performance results of simulation tests of the contingencies in Table I of the NERC Planning Standard I.A.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Planning Standard I.A. and the associated Table I.  All non-compliance findings shall be documented, including a plan for achieving compliance.  These assessments shall be provided to NERC or ERCOT on their request within 30 days.

### 12B7.2.4	Maintenance and Testing Requirements for ERCOT System Facilities

- The Facility Owner shall test and verify the proper operation of each new or modified protective relay system and associated communications channels prior to placing the equipment in its zone(s) of protection in service.  For protective relay systems that utilize a propagation-delay-sensitive operating principle and a communication channel with potentially significant propagation delay, time-synchronized “end-to-end” testing of the protective relay system shall be performed to verify that communication channel performance (including alternate routes) is adequate for proper operation.

- Facility Owners shall have documented protective relay system maintenance and testing programs in place.  Documentation shall include identification of protective relay system, a summary of testing procedures including requirements for frequency of tests, and the date last tested.

- The Facility Owner shall periodically test and inspect all components of the protective relay system to assure continued reliability.  Identified deficiencies shall be corrected.  Documentation demonstrating compliance with the Facility Owner’s maintenance and testing programs shall be supplied to ERCOT or NERC upon their request within thirty (30) days.

### 13B7.2.5	Requirements and Recommendations for ERCOT System Facilities

#### 21B7.2.5.1	General Protection Criteria

24BDependability

- Except as noted in items 4 and 5 below, all elements of the ERCOT System operated at 100 kV and above (i.e., lines, buses, transformers, generators, breakers, capacitor banks, etc.) shall be protected by two (2) protective relay systems.  Each protective relay system shall be independently capable of detecting and isolating all faults thereon.

- The protective relay system design should avoid the use of components common to the two (2) protective relay systems.  Areas of common exposure should be kept to a minimum to reduce the possibility of both protective relay systems being disabled by a single contingency.

- The use of two (2) identical protective relay systems is not generally recommended, due to the risk of simultaneous failure of both protective relay systems because of design deficiencies or equipment problems.

- Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.  This protection need not be duplicated.

- On installations where freestanding or column-type Current Transformers (CTs) are provided on one (1) side of the breaker only, the protective relay system should be provided to detect a fault on the primaries of such CTs.  This protection need not be duplicated.  Application of freestanding CTs requires extra care to ensure that the relaying is proper and that the schemes overlap.

25BSecurity

The protective relay system should be designed to isolate only the faulted element, except in those circumstances where additional elements should be tripped intentionally to preserve system integrity.  For faults external to the protected zone, each protective relay system should be designed to either not operate, or to operate selectively with other systems, including breaker failure.  (In this context, the limits of the protected zone are defined by the circuit breakers.)

26BDependability and Security

- The protective relay system should be no more complex than required for any given application.

- To the maximum degree practicable, the components used in the protective relay system should be of proven quality, as demonstrated either by actual experience or by stringent tests under simulated operating conditions, to ensure that the reliability of the protective relay system is not degraded by the components.

- The protective relay system shall be designed to minimize the possibility of component failure or malfunction due to electrical transients and electromagnetic interference or external effects such as vibration, shock and temperature.

- Critical features associated with protective relay system and circuit breaker operation shall be annunciated or monitored.

- The protective relay system circuitry and physical arrangements shall be carefully designed so as to minimize the possibility of incorrect operations due to personnel error.

- Computerized fault studies shall be used during the planning or design stages to analyze the effects of an addition or modification to the ERCOT System and to determine proper protective relay system coordination.

- To the extent dynamic or transient analysis shows that a protection system, designed within the guidelines contained in these Operating Guides, is unable to operate in a manner that maintains continuity of service and/or system stability in accordance with NERC Reliability Standards and the Operating Guides, additional measures shall be considered for improvement to the operation of the protection system.  Additional measures may include redundant CTs, Voltage Transformers (VTs), power supplies and communication paths.

27BOperating Time

The objective of the protective relay system is to take corrective action in the shortest practical time with due regard to selectivity, dependability and security.  In cases where clearing times are deliberately extended, consideration should be given to the following:

- Effect on ERCOT System stability or reduction of stability margins.

- Possibility of causing or increasing damage to equipment and subsequent extended repair and/or outage time.

- Effect of disturbances on service to customers and neighboring Facility Owners.

28BTesting and Maintenance

- The design of the protective relay system both in terms of circuitry and physical arrangement shall facilitate periodic testing and maintenance.  Test devices or switches should be provided to eliminate the necessity for removing or disconnecting wires during periodic testing.  Protective relays for transmission lines shall be designed to support periodic testing and maintenance while the transmission line remains in service.

- Commissioning of new equipment should consist of the following steps:

- Relay installation wiring diagrams cross-checked against schematics

- After completion of construction, physical check of wiring and relay installation

- Check and testing before energizing of all equipment in the zone of protection, including relay testing.  It is desirable to test the relays at the setting the relay will have in service

- Check of supporting paperwork, such as relay test reports

- Check that the relay settings when received from the manufacturer concur with the intended manufacturer’s specifications

- Calibrate and check that proper utility’s settings have been made

- Maintain a record of trip check and energizing procedure performance

- Maintain a record of in-service measurement of voltage, current magnitudes, phase angles, and a comparison to expected values and to other instrumentation

- Release to Facility owner for service

29BAnalysis of System Performance and Associated Protection Systems

- Relay operation and settings shall be reviewed periodically and whenever significant changes in generating sources, transmission facilities, or operating conditions are anticipated.

- Naturally occurring faults and other system disturbances should be analyzed as a source of information as to the health of relay schemes in the system.  Sources of information usually available are:

- Short circuit study for the exact conditions of the fault

- Fault recorder traces

- Sequence of events data recording the opening and closing of contacts in the protective relay scheme and associated communication equipment

- Fault locator data

- SCADA logger output of breaker operation and alarms

- Interviews with operating personnel and/or other witnesses

- Field report of relay flags and breaker counter changes

- Field report of the fault location, if found

- Records of relay setting, relay testing, trip check and energize procedures as carried out, in-service measurements, relay wiring diagrams and schematics, manufacturers' information

- Other coworkers and SPWG members

- Manufacturers’ application and design engineers

- Steps one can follow in analyzing a disturbance are:

- Gather data

- Create a time line consisting of events and periods between events

- Compare actual and calculated values of current and voltage during the periods between events

- Compare actual and expected breaker operations and flags

- Choose the least complicated explanation for contradictory information and to fill in missing information

- Gather additional information as indicated to prove or disprove explanations

- Iterate

- Document by issuing a report of all findings, changes, and recommendations

- After a reasonable time, check back to see if the recommendations have been carried out

#### 22B7.2.5.2	Equipment and Design Considerations

30BCurrent Transformers

- CTs associated with the protective relay system shall have adequate steady state and transient characteristics for their intended function.

- The output of each CT shall remain within acceptable limits for the connected burdens under all anticipated fault currents to ensure correct operation of the protective relay system.

- CTs or their secondary windings shall be located so that adjacent protection zones overlap.

- CT secondary wiring shall be grounded at only one (1) point. When multiple CTs are interconnected, the combination shall have only one (1) ground.

- For all newly installed protective relay systems, the two (2) protective relay systems protecting a zone shall utilize isolated and separate CTs, or isolated and separate secondary windings in the case of free-standing CTs.

- Other considerations:

- Internal bushing CTs are preferred over external slip-over CTs

- 10L800 (C800) class CTs are preferred for relaying

- Breakers and free-standing CTs with four or more sets of CTs are preferred

- Over-the-bushing external CTs can sometimes solve problems when there aren't enough CTs.  Note that there may be an unprotected region between the external CT and the bushing CT.

- Shorting type terminal blocks should be provided for all CTs

31BVoltage Transformers and Potential Devices

- VTs and potential devices associated with the protective relay system shall have adequate steady state and transient characteristics for their intended functions.

- VTs and potential devices shall have adequate volt-ampere capacity to supply the connected burden while maintaining their relay accuracy over their specified primary voltage range.

- Usually one (1) set of VTs (with two separate secondary windings per VT) per bus (i.e. single bus substation configuration) or per power system element (i.e. ring bus and breaker-and-a-half substation configurations) is sufficient.

- The two protective relay systems protecting ERCOT System Facilities may use separate secondary windings of the VTs or one (1) of the secondary windings may be dedicated to supplying the polarizing potential and the other winding used to supply other protection and monitoring functions.  For all newly installed protective systems, if the two (2) protective relay systems protecting a zone each require a VT input for protection functions, they shall utilize isolated and separate VT secondary windings unless ERCOT determines that one of the secondary windings must be dedicated to metering applications.

- VT and potential device secondary wiring shall be grounded at only (1) one point.  (ANSI/IEEE C57 recommends grounding at the panel.)

- VT installations shall be designed with due regard to ferroresonance due to capacitance across the interrupter at 138 kV and above.

- Other considerations

- Special attention should be given to the physical properties of secondary circuit fuses

- Capacitor coupled VT are suitable for relaying and SCADA telemetry

- Report loss of VT voltage (VT fuse failure) over SCADA

32BBatteries and Direct Current (DC) Supply

- DC batteries associated with the protective relay system shall have a high degree of reliability.

- Two (2) batteries each with its own charger should be provided at each location.  An acceptable alternative is one (1) battery with two (2) separately protected branches.  The two (2) protective relay systems protecting a zone shall be supplied from the separate batteries or branches.  For a new transmission Facilities at 100 kV and above, two (2) batteries shall be required in locations that remote backup clearing of lines and substation faults is not achieved.  For new or upgraded transmission Facilities at 200 kV and above with two (2) or more transmission voltage circuit breakers, two (2) batteries each with its own charger, are required.

- Each battery shall have sufficient capacity to permit operation of the station, in the event of a loss of its battery charger or the AC supply source, for the period of time necessary to transfer the load to the other battery or to re-establish the supply source.  Each battery and its associated charger shall have sufficient capacity to supply its share of the DC Load of the station.

- A fault at the battery terminals can only be interrupted by a mid-bank protective device.  If a mid-bank protective device is not used, then the connections between the battery terminals and the main protective devices shall possess the highest possible degree of reliability.

- Battery chargers and all associated circuits shall be protected against short circuits.  All protective devices shall be coordinated to minimize the number of DC circuits interrupted.

- The regulation of DC voltage shall be designed such that, under all possible loading conditions, voltage within acceptable limits will be supplied to all devices.

- DC systems shall be monitored to detect abnormal voltage levels, both high and low, DC grounds, and loss of AC to the battery chargers.  Loss of DC to relay schemes shall be alarmed.  Also, where possible the loss of AC to the battery chargers and loss of DC should be provided as SCADA alarm inputs.

- DC systems shall be designed to minimize AC ripple and voltage transients.

- The DC circuit protective devices used shall have published DC interrupting ratings suitable for the required circuit duty.

33BAC Auxiliary Power

- There should be two (2) sources of station service AC supply, each capable of carrying all the critical loads associated with the protective relay system.

- Failure of station service AC supply should be alarmed over SCADA.

34BCircuit Breakers

- Two (2) trip coils, one (1) associated with each protection system, shall be provided for each operating mechanism.  The failure of one (1) coil shall not damage or impair the operation of the other coil.

- The design shall be such that the breaker will operate if either both trip coils are energized simultaneously, or either trip coil alone, and verified by tests.

- Circuit breaker auxiliary switches used in protection systems should be highly reliable with a positive make-break action and good contact wipe.  Multiplier contacts simulating breaker auxiliary switches should be used with caution in protection systems.

- A three-phase and line-to-ground interrupting study to validate or indicate breaker interrupting rating shall be performed.

35BCommunications Channels

- Where communication channels are required for the protective relay system purposes, the communication facilities shall have a degree of reliability no less than that of the other protective relay system components.  For extra security, the output contacts from two (2) independent channels may be wired in series.

- Where communication channels are required in each of the two (2) protective relay systems, the channels shall be separated physically and designed to minimize the risk of both channels being disabled simultaneously by a single contingency.

- Communication channels shall be provided with means to verify signal performance.

- Other considerations

- Report loss of channel over SCADA

- Automatic testing of power line carrier (PLC) is desirable to reduce false trips from failure to block

- Split up PLC Loads between DC sources so that loss of one (1) fuse does not disable all the carrier sets.  If all the carrier sets were to be disabled, then multiple false trips during a fault could result.

- See also Section 8.3.4, TDSP and QSE Supplied Communications.

36BControl Cables and Wiring

- Control cables, wiring and auxiliary control devices should be such as to assure high reliability with due consideration to published codes and standards, fire hazards, current-carrying capacity, voltage drop, insulation level, mechanical strength, routing, shielding, grounding and environment.

- Other considerations

- AC or DC go-and-return functions should be implemented in the same cable to avoid induction loops

- Individual wires in cables should have colored jackets, not black jackets with a "color" printed on the jacket

- Standardization of the relationship between wire colors and functions is desirable

- No splice in any wire or cable

- All cables terminated on terminal blocks

- Shielded cable should be installed in locations where electric fields, magnetic fields, or electromagnetic interference is sufficient to disrupt the reliable operation of the control cable and it cannot be mitigated by other means.

37BEnvironment

- Means shall be employed to maintain environmental conditions that are favorable to the correct performance of the protective relay system.  Particular attention should be given to solid-state equipment installations.

- Other environmental hazards to look out for:

| - Fire ants | - Rats |
| --- | --- |
| - Snakes | - Dust, dirt, grime |
| - Trash and leftover hardware | - Water |
| - Gunfire | - Theft of substation and transmission grounds |
| - Hand-held radio keyed near solid-state relays | - Batteries located in same room as relays (battery fires) |
| - Severe cold weather conditions can impact operation of circuit breakers, DC battery, and carrier signals. |  |

#### 23B7.2.5.3	Specific Application Considerations

38BTransmission Line Protection

- 1.	Each of the two (2) independent protective relay systems shall detect and initiate action to clear any line fault without undue system disturbance.  The protective relay system shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme, a widespread disturbance will not result.  A protective relay system, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other protective relay system, including breaker failure.

- 2.	For newly installed transmission line protective relay systems:

- Fuses shall not be used in the 3Vo polarizing supply for ground relays.

- Loss-of-potential function shall be used for schemes dependent on voltage for correct operations.  SCADA alarms shall be provided for Loss-of-potential conditions.

- Dual communication-aided protection over dual communications channels shall be used where dynamic and/or voltage stability studies indicate non-pilot protection operating times are inadequate.

- 3.	Transmission line protection should include:

- One independent protective relay system of phase and ground protection over a communications channel.

- A second independent protective relay system of at least two (2) zones of phase protection and at least two (2) zones of ground protection or ground directional overcurrent relaying (time delay and instantaneous).

- “Ground chain protection” or switch-to-on-fault to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs and protection elements dependent on distance measurement.

- Recognition and trip for open conductor is desirable but not required.

- Overload protection is provided by SCADA analog alarms and dispatcher discretion.

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure.

- Short lines may require special attention, such as dual primary schemes, etc.

- For transmission Facilities with series compensation, dual communication-aided protection should be used.  At least one (1) of the two (2) protective relay systems should be differential type.

- For any transmission line that has dual communication-aided protection systems, at least one (1) of the two (2) protective relay schemes should be of a differential type in any location where an adequate communications infrastructure exists or is planned and there are no mitigating circumstances (e.g. tapped loads).

39BTransmission Station Protection

- 1.	Each zone in a station shall be protected by two (2) independent protective relay systems.  For zones not protected by line protection, at least one (1) of the two (2) protective relay systems shall be a differential type.

- 2.	The protective relay system shall be designed to operate for station faults so that, if ultimate clearing is accomplished by a breaker failure scheme, a widespread disturbance will not result.  The protective relay system shall be designed to operate properly for the anticipated range of currents.

- 3.	Station protection should consist of:

- Bus differential or bus overcurrent protection of all buses

- All transformers protected by transformer differential, transformer overcurrent, or fuses (for small transformers).  Note that ferroresonance is possible for fused transformers above 69 kV.

- Sudden pressure relay protection for transformer main tanks and transformer tap changer compartments.

- For transformers with conservator tanks, gas accumulator relay (also known as a Buchholz relay) protection for the transformer main tanks and transformer tap changer compartments are preferred in addition to sudden pressure relay protection.

40BBreaker Failure Protection

- 1.	Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.

- 2.	The breaker failure protection should be initiated by each of the protection systems that trip that breaker.  It is not necessary to duplicate the breaker failure protection itself.

- 3.	Induction cup, solid state, or microprocessor based current detectors shall be used to determine if a breaker has failed to interrupt.

- 4.	Plunger or clapper type overcurrent relays are not recommended as breaker failure fault detectors.

- 5.	For all newly installed or upgraded relay systems, a cross-tripping means such that each protective relay system can operate both circuit breaker trip coils without compromising the separation of the DC supplies is recommended.

- 6.	Breaker failure schemes shall be designed such that if fault clearing should be accomplished through operation of the breaker failure scheme, an uncontrolled separation and collapse of the ERCOT System will not result.  Breaker failure schemes shall be designed to be selective in time with other protective relay systems and/or particular system requirements.

41BGenerator Protection

- 1.	Generator faults shall be detected by more than one (1) protective relay system.  These may include faults in the generator or generator leads, unit transformer, and unit-connected station service transformer.

- 2.	Generators shall be protected to keep damage to the equipment and subsequent outage time to a minimum.  In view of the special consideration of generator unit protection, the following are some of the conditions that should be detected by the protection systems:

- Unbalanced phase currents

- Loss of excitation

- Over-excitation

- Field ground

- Inadvertent energization (reverse power)

- Uncleared system faults

- Off-frequency

It is recognized that the overall protection of a generator will also involve non-electrical considerations.  These have not been included as part of this criteria.

- 3.	The apparatus shall be protected when the generator is starting up or shutting down as well as running at normal speed; this may require additional relays, as the normal relays may not function satisfactorily at low frequencies.

- 4.	A generator shall not be tripped for a system swing condition except when that particular generator is out of step with the remainder of the system.  This does not apply to protective relay system designed to trip the generator as part of an overall plan to maintain stability of the ERCOT System.

- 5.	The loss of excitation relay shall be set with due regard to the performance of the excitation system.

42BAutomatic Under-Frequency Load Shedding Protection Systems

- Automatic under-frequency Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, Maintenance and Testing Requirements for ERCOT System Facilities, apply to under-frequency Load shedding protection systems as well.

- 1.	Automatic under-frequency Load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the system during major emergencies.

- 2.	The criteria for the operation of these protection systems are detailed in Section 2.9, Requirements for Under-Frequency Relaying.

- 3.	Automatic under-frequency Load shedding protection systems need not be duplicated.

- 4.	Generator and turbine under-frequency protection systems shall be coordinated with Section 2.9.

- 5.	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency Load shedding program.

- 6.	Automatic Load restoration for an under-frequency Load shedding operation is not currently utilized in ERCOT.

43BAutomatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, apply to under-voltage Load shedding protection systems as well.

- 1.	The requirement for under-voltage relaying shall be determined by system studies performed/administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

- Amount of Load to be shed to restore voltage to minimum acceptable level or higher,

- The minimum and maximum time delay allowed before automatically shedding Load,

- The voltage level(s) at which to initiate automatic relay operation, and

- The location(s) for effectively applying under-voltage Load shedding protection systems.

- 2.	Automatic under-voltage Load shedding protection systems need not be duplicated.

- 3.	Analyses shall be performed on under-voltage Load shedding schemes by working groups and/or equipment owners as assigned by ERCOT to demonstrate that they are expected to act before generators trip Off-line due to the protective relay requirements described in Section 3.1.4.6, Protective Relaying and Voltage Ride-Through (VRT) Requirement.  A specific exemption from this analysis requirement may be provided by the ROS.

- 4.	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

- 5.	Automatic Load restoration for an under-voltage Load shedding operation is not currently utilized in ERCOT.

- 6.	The scheme shall be designed to ensure reliable operation and to prevent false tripping.

3B7.3	Document Control

44BChange History

| Issue/Date | Reason for Issue |
| --- | --- |
| Version 0.1 December 7, 2000 | Draft for Review |
| Version 0.2 December 29, 2000 | Insert comments |
| Version 0.3 January 19, 2001 | Insert comments from seminar |
| Version 0.4 February 5, 2001 | Comments from second Working Group |
| Version 1.0 February 28, 2001 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee |
| May 1, 2002 | OGRR103 |
| July 1, 2002 | OGRR104 |
| September 1, 2002 | OGRR107 & OGRR109 |
| December 1, 2002 | Reformatted numbering from Appendix B to Section 7. |
| January 1, 2003 | OGRR121 revised Section 7.2.2.5 for fault recording equipment. |
| March 1, 2003 | Formatted header and page numbering. |
| May 1, 2003 | Moved “Planning” text to Section 5 and updated section numbering. |
| February 1, 2004 | OGRR140 updated Section 7.2.2 |
| May 1, 2004 | OGRR144 updated Section 7.2.5.3 |
| May 1, 2005 | OGRR162 |
| April 1, 2006 | OGRR172 |
| August 1, 2006 | OGRR179 |
| July 1, 2007 | Admin OGRR201 |
| October 1, 2009 | OGRR224 |
| July 1, 2010 | OGRR240 |
| August 1, 2010 | OGRR241, OGRR243 |