## Slide 1: Houston Import Study
Warren Lasher
Manager, Long-Term Planning and Policy

## Slide 2: Houston Import Background
ERCOT’s December 2008 Long Term Study identified potential need for additional import capacity into Houston
North to Houston congestion continues to be experienced in real-time operations
Two Market Participants (CenterPoint Energy and Sharyland Utilities) submitted RPG proposals for two different Tier 1 projects
  Each project received negative stakeholder comments on the relative merits of the individual proposals
ERCOT performed Independent Review of these projects and analyzed approximately 20 other options under a variety of scenarios

## Slide 3: ERCOT Independent Review of Houston Import Project
Analysis focused on economic benefit of additional import capacity into the Houston area
  Import restrictions not considered to be a NERC-criteria reliability need in the timeframe of the study (2014)
  Recent unit mothballing at SR Bertron and Greens Bayou plants not taken into account
Used 2009 Five-Year Transmission Plan economic model for the year 2014 to perform the analysis
Three phase approach:
  Base case – use standard RPG review assumptions to determine which options pass planning criteria
  Alternative scenarios – evaluate each of the options that pass phase 1 under a variety of scenarios to determine “best” option
  Sensitivity scenarios – evaluate preferred option in additional scenarios to determine robustness

## Slide 4: Houston Import Project Options Studied
Option | Cost | Description
1 | $333M | Lufkin-Canal 345-kV double circuit
2 | $222M | Salem-Zenith 345-kV double circuit
3 | $175M | Fayetteville-Zenith 345-kV double circuit
3A | $225M | Fayetteville-Zenith 345-kV double circuit w/ 30% series comp
4 | $173M | Gibbons Creek-Zenith 345-kV double circuit
6 | $189M | Fayetteville-Obrien 345-kV double circuit
6A | $239M | Fayetteville-Obrien 345-kV double circuit w/ 30% series comp
9 | $278M | Gibbons Creek-Salem-Zenith 345-kV double circuit
12 | $306M | Gibbons Creek-Salem/ Fayetteville-Zenith 345-kV double circuit
19 | $62M | Add series comp to existing Hillje-WAP and Hillje-Holman 345-kV
22 | $226M | Fayetteville-Zenith 345-kV double circuit w/ 50% series comp
24 | $300M | Option 19 + Option 22
J1 | $253M | Sandow-Zenith 345-kV double circuit
J1A | $304M | Sandow-Zenith 345-kV double circuit w/ 30% series comp
J2 | $420M | Marion-Holman-Obrien 345-kV double circuit
J3 | $174M | Hillje-Obrien 345-kV double circuit
DC1 | $787M | Brown-Zenith 3000 MW HVDC line
DC2 | $923M | Scurry-Zenith 2000 MW HVDC line
E1 | $379M | Twin Oaks-Salem 345-kV double ckt and Fayetteville-Zenith 345-kV double ckt
E4 | $286M | Twin Oaks-Zenith 345-kV double circuit
E4A | $336M | Twin Oaks-Zenith 345-kV double circuit with 30% series comp
E5 | $328M | Twin Oaks-Salem-Zenith 345-kV double circuit

## Slide 5: Houston Import Project Options Studied
To Brown
Option 1
Option 2
Option 3/ 3A/ 22
Option 4
Option 6/ 6A
Option 9
Option 12
Option 19
Option J1/ J1A
Option J2
Option J3
Option DC1
Option DC2
Option E1
Option E4/ E4A
Option E5
To Scurry

## Slide 6: ERCOT Independent Review Results
Seven options passed the economic planning criteria in the base scenario based on generator revenue savings (consumer benefit test); none passed using production cost savings (societal benefit test)
  Majority of economic projects recommended by ERCOT are due to the production cost savings of the projects – “societal benefit”
  Houston Import project is justified based on generator revenue savings – “consumer benefit”
    Per ERCOT RPG Planning Charter and Procedures Section 3.3
  Study indicates that increasing the import capacity for Houston will result in lower LMPs in the Houston area

## Slide 7: ERCOT Independent Review Results
  STP 3 & 4 scenario was run on 2014 model because a later year model was not available at the time of analysis
Study Results for Option 3 | $M
Cost | 175
Savings Required For Economic Justification | 29.2
Base Case Production Cost Savings | 13.3
Base Case GR Savings | 45.4
CREZ Generation Scenario GR Savings | 87.5
High Coastal Load Scenario GR Savings | 114.0
Low Coastal Load Scenario GR Savings | 55.0
$4 Gas Price Scenario GR Savings | 31.6
$10 Gas Price Scenario GR Savings | 42.3
STP 3&4 Scenario GR Savings | 4.0
Houston Gas Plant Addition Scenario GR Savings | 55.4
Generator Assumptions Update Scenario GR Savings | 50.4
Savings Required for High Transmission Cost Scenario | 37.7
GR = Generator Revenue; Savings are annual | 
Option 3 (Fayetteville-Zenith 345-kV double circuit line) was the only option that met the economic criteria in the base case and all of the alternative scenarios besides the STP 3 & 4 scenario
Phase 1
Phase 2
Phase 3

## Slide 8: Benchmark case – Relative Avg Annual LMPs
DRAFT
Key Assumptions
2014
Existing and IA gen (incl. wind)
2009 5YR Plan XM and CREZ projects included
$7/MMBTU gas
Ignore phase shifter congestion

## Slide 9: Option 3 – Relative Avg Annual LMPs
DRAFT
Key Assumptions
2014
Existing and IA gen (incl. wind)
2009 5YR Plan XM and CREZ projects included
$7/MMBTU gas
Ignore phase shifter congestion

## Slide 10: Conclusions
ERCOT will request the ERCOT BOD endorse the following improvements associated with Option 3:
  Build Fayetteville – Zenith 345 kV double circuit line (approx. 60 miles on a new ROW) so that each circuit Rate B is approximately 2800 MVA
  Loop Fayette Power Project – Salem 345 kV line into Fayetteville 345 kV substation
  Upgrade Fayette Power Project – Fayetteville 345 kV double circuit lines so that the Rate B of each circuit is approximately 1900 MVA
  Expand the Fayetteville Substation with four new line terminations and Zenith Substation with two new line terminations
  Upgrade the Bellaire – Brays – H.O. Clarke Plant 138 kV line terminal equipment so that the circuit Rate B for the two 138 kV sections is 893 MVA and 561 MVA, respectively
Estimated Capital Cost = $175M
2014 Annual Generator Revenue Savings = $45.4M

## Slide 11
Questions?