Comments

| TAC0706060 | Telemetry Standards |
| --- | --- |

| Date | August 10, 2010 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Nayana Phadke |
| E-mail Address | Nayana.Phadke@lcra.org |
| Company | LCRA Transmission Services Corporation |
| Phone Number | 512-356-6419 |
| Cell Number |  |
| Market Segment | Electric Cooperative |

Comments

To the 08/02/2010 NDSWG edits, LCRA Transmission Services Corporation (TSC) submits modifications to

- Reformat the document and provide page and section numbers.

- In the section “Reliability of ICCP associations” we have a concern with the use of “Real-Time” data.  Real time implies a quality of data which is already addressed in the General and Supplemental criteria. Suggest replacing Real time data with “configured data at the scheduled periodicity”

Revised Proposed Language

Telemetry Standards

- Telemetry Status and Analog Measurements Data

Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors. The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator.

Telemetry is not needed at every node of the System to arrive at a good estimate of the System’s state. There are general telemetry performance criterion, such that sufficient numbers and placement of measurements and accuracy of measurements that are available to achieve System observability and an overall good State Estimator performance.

Beyond general telemetry performance criterion there are locations that require a more stringent criterion needed where state estimator results are more important (e.g., locations where reliability, security, and Market impact are of more focused concern).

- Required Telemetry

  - Telemetry of Voltage and Power Flow

Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers to the extent such can be shown to be needed in achieving the TAC-approved SE performance standard.  On monitored non-Load substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”  An N-1 Redundancy exists if the flow remains observable on the loss of any single measurement pair (MW, MVAr) excluding station RTU communication path failures.  In making the determination to request additional telemetry, ERCOT shall consider the economic implications of inaccurate representation of Load Models in LMP results versus the cost to remedy.

QSEs, Resources and TDSPs are required to provide power operation data to ERCOT including, but not limited to:

    - Real time generation data from QSEs;

    - Planned Outage information from Resources;

    - Network data used by any TDSP’s control center, including:

      - Breaker and line switch status of all ERCOT Transmission Grid devices;

      - Line flow MW and MVAR;

      - Breaker, switches connected to all Resources;

      - Transmission Facility Voltages; and

      - Transformer MW, MVAR and TAP.

    - Real time generation and Load acting as a Resource meter data from QSEs;

    - Real time Generation meter splitting signal from QSEs;

    - Planned Transmission Outage information from TDSP;

    - Network transmission data (model and constraints) from TDSP; and

    - Dynamic Schedules from QSEs;

Real Time data will be provided to ERCOT at the same scan rate as the TDSP or QSE obtains the data from telemetry.

  - Continuous Telemetry of the Status of Breakers and Switches

Each TSP and QSE shall provide telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches used to switch any Transmission Element or load modeled by ERCOT.  Each TSP and QSE is not required to install telemetry on individual breakers and switches, where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP or QSE switching operations and TSP or QSE personnel.  Each TSP or QSE shall update the status of any breaker or switch through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute.  If in the sole opinion of ERCOT, the manual updates of the TSP or QSE have been unsuccessful in maintaining the accuracy required to support State Estimator performance to the State Estimator Performance Standard, ERCOT may request that the TSP or QSE install complete telemetry from the breaker or switch to the TSP or QSE, and then to ERCOT.  If the TSP disputes the request for additional telemetry the TSP shall have the appeals process available under the section titled “ERCOT Requests for Telemetry”. In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results versus the cost to remedy.

- General Telemetry Performance Criteria

The following criterion will apply in general to Telemetry provided to ERCOT:

  - The TSP shall maintain the sum of flows into any telemetered bus less than the greater of 5 MW or 5% of the largest line rating at each bus.

  - Each QSE or TDSP shall provide data to ERCOT that meets the following availability:

Ninety two (92%) percent of all telemetry provided to ERCOT must achieve a quarterly availability of eighty (80%) percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with a Valid, Manual, or Calculated quality code at the scheduled periodicity.

TDSP’s shall make reasonable efforts to obtain this data from retail customers associated with new customer-owned substations to meet this standard or obtain agreement from ERCOT that these retail customers have entered into arrangements with ERCOT to provide this data to ERCOT.  If the data cannot be obtained under either of these methods, ERCOT shall report such case to the Independant Market Monitor.

  - Exceptions to the General Telemetry Performance Criterion shall be made for data points not significant in the solution of the State Estimator or required for the reliable operation on the ERCOT Transmission System.  Some examples of these are:

    - Substation with no more than two transmission lines and less than 10 MW of load;

    - Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes;

    - Substations connected radially to the bulk transmission system.

    - Under ERCOT declared emergencies, the metrics will be suspended until normal operations have resumed.

- Supplemental Telemetry Performance Criterion

ERCOT will identify specific MW/MVAR telemetry pairs, not exceeding 10% of the Transmission Elements in ERCOT, and 20 voltage points that are important to reliability, system observability, support of State Estimator performance, or are of a commercial market concern. This important telemetry must meet more stringent criterion for accuracy and availability where specifically addressed. ERCOT will review and publish this list annually. ERCOT will use the following criterion to identify this specific  telemetry:

  - Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

  - Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

  - Loss of a telemetry point that results in the inability of ERCOT to monitor the loading on transmission facilities designated as important to transmission reliability by ERCOT. A list of specific facilities will be published annually.

  - Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available.

  - Telemetry necessary to monitor the voltages on the specific 20 busses  designated by ERCOT and approved by TAC each October.

  - Each QSE or TDSP shall provide data to ERCOT that meets the following availability:

Ninety two (92%) percent of the important telemetry defined by ERCOT must achieve a quarterly availability of ninety (90%) percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with valid, manual, or calculated  quality codes at the scheduled periodicity.

- TDSP/QSE Telemetry Restoration

Telemetered data shall be provided continuously.  Lost data or signals, whether failed or in error, must be restored promptly by the provider of the telemetered data.  It is recognized that some data may be more essential to the state estimator solution.  ERCOT will inform the TDSP or QSE if a data item is essential and needs to be repaired as quickly as possible.  QSE and TDSP repair procedures and records shall be made available to ERCOT upon request.  When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, either a) Calibrate/repair the mis-behaving equipment b) Request an outage to schedule calibration/repair of the mis-behaving equipment c) Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame or d) Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.   Before ERCOT requests review/re-calibration of a problem piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision on the most appropriate action.

- Calibration, Quality Checking and Testing

It is the responsibility of the owner to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in this Appendix, for both the overall system and for individual equipment where detailed herein.  Coordination of outages required for these activities with ERCOT is also the responsibility of the owner.  Each TSP/QSE shall have a plan on file with ERCOT to assure accurate  telemetry of data.   If a TSP/QSE repeatedly fails other telemetry metrics defined in these guides, ERCOT may require a revision of this plan.

- ICCP Links

  - Data Quality Codes

Market Participant’s shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their quality codes into the ERCOT defined quality codes.

Status & analogs telemetered to ERCOT will be identified with the following quality codes:

–         Valid – represents analog or status the TSP or QSE considers valid

- Manual – represents a analog or status entered manually at the market participant (not received from the field electronically)

- Calculated – represents an analog point that the TSP or QSE calculates.

–         Suspect - Represents a analog or status in which the TSP or QSE is unsure of the validity

–         Invalid – Represents a analog or status which the market participant has identified as out of reasonability limits.

- Com_fail – informs ERCOT that due to communications failure, the analog or status provided ERCOT is not current

  - Reliability of ICCP associations

Each participant using ICCP associations must achieve a monthly availability of ninety-eight (98%) percent, excluding approved planned outages.  Availability will be measured based on end-to-end connectivity of the  communications path and the passing of configured data at the scheduled periodicity. This will include establishing a process to coordinate downtime for ICCP associations  and database maintenance. High availability configuration as allowed by the ICCP handbook should be treated as a single association to achieve this availability measure.

Each TSP and QSE shall use fully redundant data communications between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

    - For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s)

### ERCOT Requests for Telemetry

ERCOT is required to protect transmission assets operated at 60 kV or above from damage.  To do this, ERCOT may request that additional MW, MVAR, and voltage telemetry be installed, while attempting to minimize adding equipment to as few locations as practicable.

ERCOT may request additional telemetry when it determines that network observability or the measurement redundancy is not adequate to produce acceptable state estimator results.

Prior to making a request for additional telemetry, ERCOT will provide evidence supporting a congestion or reliability problem requiring additional observability and , define expected improvements in system observablity needed.  If the request is for telemetry additions at more than one location, ERCOT will prioritize the requested additions.

Upon receipt of a request for additional telemetry, the TDSP or QSE will have sixty (60) days to either:

  - Accept ERCOT’s request for additional telemetry, provide the telemetry within 18 months and notify ERCOT of the implementation schedule;

  - Provide an alternative proposal to ERCOT, for implementation within the next 18 months, which meets the requirements described by ERCOT;

  - Propose a normal topology change (change normal status of switch (es)) in the area which would eliminate the security violations which are ERCOT’s concern. (i.e. eliminates the possibility of flow through a networked element and turns the security problem into a planning problem which is un-affected by unit dispatch);

  - If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

  - Indicate that the requested telemetry point is at a location where the TDSP or QSE does not have the authority to install the requested telemetry.  For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; or

  - File a request with the PUCT requesting expedited action for an Order directing that the responsibility for reliability and protection of this specific element or elements of the transmission system be withdrawn from ERCOT and assigned to the requesting TDSP.  ERCOT will then immediately remove the elements from its Real Time Congestion Management system as monitored elements pending the PUCT decision.

If ERCOT has not received acknowledgement that a request has been received within thirty (30) days of its sending, ERCOT will contact the TDSP or QSE for verification of receipt.

Nothing in this section shall limit the TDSP’s appeal process outlined in Nodal Protocol Section 3.10.7.4.

- ERCOT Request for Redundant Telemetry

  - ERCOT will maintain redundancy on measurements to achieve a N-1 observability.measure ERCOT will identify and produce a list of telemetry points in the ERCOT system that are required to maintain the N-1 observability measure. This list will be published annually.  ERCOT will use this list to identify telemetry points whose loss will result in:

    - Inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

    - Inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

    - Inability of ERCOT to monitor loading on transmission facilities designated as important to transmission reliability by ERCOT. A list of these facilities will be published annually.

  - ERCOT may request additional MW, MVAR and voltage telemetry to make these measurements redundant.  In this request, ERCOT will identify these points, and the contingency/overload condition and the unit dispatch which makes this a possible concern. If the request is for telemetry at multiple locations, ERCOT will prioritize the requested additions.

Upon receipt of a request for additional telemetry, a TDSP or QSE has sixty (60) days to:

    - Provide ERCOT with a schedule of equipment installations within the next eighteen (18) months which will provide the proposed telemetry;

    - Propose an alternative solution which will serve the same purpose as the ERCOT identified telemetry additions with a proposed implementation within 18 months;

    - In cases where the request is based on the availability rate of an existing telemetry point, the TDSP or QSE will provide a plan to improve the availability rate of the identified telemetry to an acceptable level, or provide documentation for why this cannot be accomplished;

    - If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

    - Identify and propose a schedule of equipment installations within the next 18 months which would, as a result, change the classification of the transmission element identified by ERCOT; or

    - Indicate that the facility that telemetry is being requested is not owned or covered by an interconnect agreement that allows the requested party to install the additional telemetry.

If ERCOT does not have knowledge that a request has been received within thirty (30) days of its sending, ERCOT will contact the TDSP or QSE for verification of receipt.

Nothing in this section shall limit the TDSP’s appeal process outlined in Nodal Protocol Section 3.10.7.4.